## Consolidated Annual
Hawaiian Electric Annual - Total Amount of Power (MW)
A | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage Power (MW)
Hawaiian Electric Power (MW) | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 1.147 | 23.247 | 23.247 | 24.937 | 24.937 | 27.937 | 27.937 | 27.255 | 27.247 | 26.247 | 26.247 | 65.247 | 316.247
O‘ahu | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 1.006 | 1.006 | 1.014 | 1.006 | 0.006 | 0.006 | 39.006 | 260.006
Maui County | 0 | 0 | 0 | 0 | 0.0016 | 0.016 | 1.141 | 22.141 | 22.141 | 23.831 | 23.831 | 25.831 | 25.831 | 25.141 | 25.141 | 25.141 | 25.141 | 25.141 | 25.141
Hawai‘i Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 31.1
Hawaiian Electric Annual - Total Amount of Energy (MWh)
B | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage - Energy (MWh)
Hawaiian Electric Energy (MWh) | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.54 | 25.438 | 25.438 | 27.167 | 27.167 | 27.75 | 27.12 | 27.12 | 27.082 | 26.832 | 26.832 | 182.832 | 1011.832
O‘ahu | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.274 | 0.274 | 0.306 | 0.274 | 0.024 | 0.024 | 156.024 | 865.024
Maui County | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.516 | 24.916 | 24.916 | 26.645 | 26.645 | 26.978 | 26.978 | 26.31 | 26.31 | 26.31 | 26.31 | 26.31 | 26.31
Hawai‘i Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 120.498

## Energy Annual
Hawaiian Electric Annual Utility & IPPs - Total Amount of Energy (MWh)
A | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage - Energy (MWh)
Hawaiian Electric Total | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.54 | 25.438 | 25.438 | 27.167 | 27.167 | 27.75 | 27.75 | 27.113 | 27.081 | 26.831 | 26.831 | 182.831 | 1011.831
Utility Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.522 | 0.522 | 2.251 | 2.251 | 2.834 | 2.834 | 2.197 | 2.165 | 1.915 | 1.915 | 1.915 | 1.915
Power Purchase Storage (IPP) | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.516 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 180.916 | 1009.916
Oahu Annual Utility & IPPs - Total Amount of Energy (MWh)
B | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage Energy (MWh)
O‘ahu Total | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.274 | 0.274 | 0.306 | 0.274 | 0.02 | 0.02 | 156.02 | 865.02
Utility Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.274 | 0.274 | 0.306 | 0.274 | 0.02 | 0.02 | 0.02 | 0.02
Power Purchase Storage (IPP) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 865
Maui County Annually Utility & IPPs - Total Amount of Energy (MWh)
C | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage Energy (MWh)
Maui County Total | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.516 | 24.916 | 24.916 | 26.645 | 26.645 | 26.978 | 26.978 | 26.313 | 26.313 | 26.313 | 26.313 | 26.313 | 26.313
Utility Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.729 | 1.729 | 2.062 | 2.062 | 1.397 | 1.397 | 1.397 | 1.397 | 1.397 | 1.397
Power Purchase Storage (IPP) | 0 | 0 | 0 | 0 | 0.016 | 0.016 | 0.516 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916 | 24.916
Hawaii Island Annual Utility & IPPs - Total Amount of Energy (MWh)
D | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual | Annual
Energy Storage - Energy (MWh)
Hawai‘i Island Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 120.498
Utility Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498 | 0.498
Power Purchase Storage (IPP) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120

## Storage Type
Energy Storage Type and Technology at Hawaiian Electric in 2011 to 2023 (4) (5)
Storage Type | Storage Technology | 2011 | [5 empty] | 2012 | [5 empty] | 2013 | [5 empty] | 2014 | [5 empty] | 2015 | [5 empty] | 2016 | [5 empty] | 2017 | [5 empty] | 2018 | [5 empty] | 2019 | [5 empty] | 2020 | [5 empty] | 2021 | [5 empty] | 2022 | [5 empty] | 2023
|  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island |  | O‘ahu |  | Maui County |  | Hawai‘i Island
|  | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh | MW | MWh
Chemical | Lithium ion | 0.006 | 0.024 | 0.016 | 0.016 | 0 | 0 | 0.006 | 0.024 | 11.016 | 4.416 | 1.1 | 0.498 | 0.006 | 0.024 | 11.016 | 4.416 | 1.1 | 0.498 | 0.006 | 0.024 | 12.476 | 5.569 | 1.1 | 0.498 | 0.006 | 0.024 | 12.476 | 5.569 | 1.1 | 0.498 | 1.006 | 0.274 | 14.476 | 5.902 | 1.1 | 0.498 | 1.006 | 0.274 | 14.476 | 5.902 | 1.1 | 0.498 | 1.006 | 0.274 | 24.476 | 25.902 | 1.1 | 0.498 | 1.006 | 0.274 | 25.141 | 25.902 | 1.1 | 0.498 | 0.006 | 0.02 | 25.14 | 25.9 | 1.1 | 0.498 | 0.006 | 0.02 | 25.14 | 25.9 | 1.1 | 0.498 | #REF! | 156.02 | 25.14 | 25.9 | 1.1 | 0.498 | #REF! | 865.02 | 25.14 | 26.313 | #REF! | 120.498
| Advanced Lead Acid | 0 | 0 | 1.125 | 0.5 | 0 | 0 | 0 | 0 | 11.125 | 20.5 | 0 | 0 | 0 | 0 | 11.125 | 20.5 | 0 | 0 | 0 | 0 | 11.355 | 21.076 | 0 | 0 | 0 | 0 | 11.355 | 21.076 | 0 | 0 | 0 | 0 | 11.355 | 21.076 | 0 | 0 | 0 | 0 | 11.355 | 21.076 | 0 | 0 | 0 | 0 | 0.665 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0
Thermal | Ice Storage (Air Conditioning) (1) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hot Water (2) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mechanical | Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Compressed Air Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Flywheel (3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note: Prior to 2011 there was one 16 kW / 16 kWh Demonstration project at Maui County installed in 2009.
(1) There are limited ice storage systems for customer air conditioning, which are not utility dispatchable.
(2) Solar Hot Water Heating, Energy Scout and dispatchable hot water heating are not reported in this table. Hot water storage technologies are reported for Demand Response or Solar Hot Water programs.
(3) One 8 kW 32 kWh Flywheel added in 2018 at Hawaiian Electric and removed in 2019
(4) Includes data for IPPs
(5) Amount of Power (MW) and Amount of Energy (MWh)

## Storage Projects
Energy Storage by Projects -- Hawaiian Electric
Project | Location | Ownership | BESS Application(s) | Battery Size and Type | Status
O‘ahu
EV Carport of the Future | Honolulu | Utility | EV charging, PV/grid energy management | 6 kW/20 kWh Lithium-ion | On-line since 2011
PV Distributed Integration BESS | Honolulu | Utility | Power Smoothing, Voltage Response, Frequency Response, Energy Shifting | 1.0 MW/.25MWh Lithium-ion Titanate | Off-line since 2020
FESS Demostration | Honolulu | Utility | PV Smoothing, Flywheel Energy Shifting | 8 kW / 32 kWh Flywheel | Off-line July 2019
Mililani I Solar | Mililani | IPP | Load Shifting | 39 MW / 156 MWh Lithium-ion | On-line August 2022
Waiawa Solar Power LLC | Waiawa | IPP | Load Shifting | 36 MW / 144 MWh Lithium-ion | On-line January 2023
Kapolei Energy Storage | Barber's Point | IPP | Load Shifting, Fast-freq. response | 185 MW / 565 MWh Lithium-ion | On-line December 2023
Maui County
Maui Economic Development Board (MEDB) BESS Demonstration Project | Kihei, Maui | IPP | Ramp rate, peak shaving | 16 kW/16 kWh Lithium iron phosphate | On-line since 2009
Lāna‘i Sustainability Research BESS | Lanai, Maui | IPP | Ramp rate, voltage support, frequency droop response | 1.125 MW/0.5 MWh Advanced lead acid | On-line since 2011 - Currently Off-Line
Kaheawa Wind Power II BESS | Kaheawa, Maui | IPP | Ramp rate, voltage support, contingency reserves (frequency regulation), operating reserves | 10 MW/20 MWh Lithium Ion | On-line since 2012-Recommissioned 4th Quarter 2018
Auwahi Wind BESS | Ulupalakua, Maui | IPP | Ramp rate, voltage Inertial support | 11 MW/4.4 MWh Nano-phosphate lithium-ion | On-line since 2012
Kihei Wastewater Treatment Plant | Kihei, Maui | Utility | Volt-Ampere Reactive ("var") Control | 0.23 MW / 0.576 MWh Advance Lead Acid | Off-line 2018
University of Hawaii Maui Campus - Site 1 | UH Maui Campus | Utility | var Control | 0.5 MW / 0.380 MWh Lithium-ion (2 Batteries) | Off-line 2018
Maui County Wailea Substation BESS | Wailea, Maui | Utility | Peak load reduction, voltage support | 1 MW/1 MWh Nano-phosphate lithium-ion | On-line 2014
Molokai BESS | Moloka‘i | Utility | Frequency Response & Capacity | 2 MW/.333 MWh Nano-Lithium Titanate | On-line June 2016
Hawai‘i Island
Hawaii Island Power Conditioner Project | Kona, Big Island | Utility | Ramp rate, voltage support | 100 kW/248 kWh Lithium-ion (Ni-Co-Al) | On-line since 2012
Hawi BESS | Hawi, Big Island | Utility | Ramp rate, frequency regulation | 1 MW/250 kWh Nano-lithium titanate | On-line since 2012
AES Waikoloa Solar | South Kohala, Big Island | IPP | Load Shifting | 30 MW/120 MWh Litthium ion | On-line since April 2023
The majority of energy storage capacity currently installed on the Companies’ systems is owned and operated by IPPs to meet performance requirements under their power purchase agreements (“PPAs”). For example, IPPs have installed battery energy storage systems (”BESS”) at two wind farms on the island of Maui (Kaheawa Wind Power (“KWP II”) and Auwahi Wind Farm (“Auwahi”)), and one photovoltaic (“PV”) farm on the island of Lana‘i (Lana‘i Sustainability Research (“LSR”)).
Other energy storage systems have been installed by the Companies or have been installed with collaborating partners as demonstration projects, in order to assess performance characteristics and gain operational experience.
The following are energy storage projects under development by the Companies:
(Power and Energy values reflect current estimates and final values and dates may change)
Project Name | Location | Owner | Application | MW | MWh | Type -Chemistry | PUC Status | Est. In Service Date
Ho‘ohana Solar 1 LLC | O‘ahu | IPP | Load shifting | 52 | 208 | lithium-ion | Approved | 2023-08-31
Mililani 1 Solar LLC | O‘ahu | IPP | Load shifting | 39 | 156 | lithium-ion | Approved | 2022-08-11
Waiawa Solar Power LLC | O‘ahu | IPP | Load shifting | 36 | 144 | lithium-ion | Approved | 2023-01-11
AES West Oahu Solar, LLC | O‘ahu | IPP | Load shifting | 12.5 | 50 | lithium-ion | Approved | 2022-09-30
Kapolei Energy Storage | O‘ahu | IPP | Load shifting | 185 | 565 | lithium-ion | Approved | 2022
Kupehau Solar | O‘ahu | IPP | Load shifting | 60 | 240 | lithium-ion | Approved | 2023-07-31
Mahi Solar | O‘ahu | IPP | Load shifting | 120 | 480 | lithium-ion | Approved | 2023
Mountain View Solar | O‘ahu | IPP | Load shifting | 7 | 35 | lithium-ion | Approved | 2023
Waiawa Phase 2 Solar | O‘ahu | IPP | Load shifting | 30 | 240 | lithium-ion | Approved | 2023-10-30
|  |  | Sub-Total | 541.5 | 2118
AES Kuihelani Solar, LLC | Maui | IPP | Load shifting | 60 | 240 | lithium-ion | Approved | 2023-10-31
Paeahu Solar LLC | Maui | IPP | Load shifting | 15 | 60 | lithium-ion | Approved | 2023-04-30
Kamaole Solar | Maui | IPP | Load shifting | 40 | 160 | lithium-ion | Approved | 2023
Pulehu Solar | Maui | IPP | Load shifting | 40 | 160 | lithium-ion | Approved | 2023
|  |  | Sub-Total | 155 | 620
AES Waikoloa Solar, LLC | Hawai‘i | IPP | Load shifting | 30 | 120 | lithium-ion | Approved | 2022-11-30
Hale Kuawehi Solar, LLC | Hawai‘i | IPP | Load shifting | 30 | 120 | lithium-ion | Approved | 2022-12-31
|  |  | Sub-Total | 60 | 240
|  |  | Total | 756.5 | 2978
10/15/2021: Updated In-service Dates for Projects