## Change Log
Version | Description
1 | Base case inputs
2 | Removed Mehana

## Index
Tab | Description (High level)
Capacity Limits | resource - Name of the resource. period - Year being referenced. capacity_limit_mw - Maximum amount of a new resource that can be built in the referenced year (MW).
Conventional DR period Limits | resource - Name of the resource. period - Year being referenced. conventional_dr_availability_hours_per_year - Maximum number of hours a year that the DR resource can be dispatched (hrs/year). daily_capacity_factor - Maximum fraction of the day that a resource can be dispatched (hrs/day)
Day Weights | day_id - Sample day ID number. day_weight - Number of days a year that the sample day represents. Sum of day weights is 365.
Energy Sharing Max to Move With | hydro_resource - Name of the resource. Does not have to be a hydro resource. energy_sharing_group_id - One of the energy sharing groups. max_energy_to_move_around_hours - Max number of hours per year that the resource can operate, assuming the resource is operating at Pmax (hrs)
ERM Params | period - Year being referenced. erm_percentage - ERM requirement (%). erm_peak_load_mw - Peak load (MW).
ERM Resource Group Map | resource - Name of the resource. erm_group - Assigns each resource to a resource group.
ERM Shapes | erm_hour - Hour in an 8760 year being referenced for the ERM calculation. Columns represent the hourly dependable capacity shape of each resource group. The value is multiplied by the capacity of the resource group to determine the contribution towards ERM for each resource group.
ERM Timepoint Params | erm_hour - Hour in an 8760 year being referenced for the ERM calculation. input_load_mw - Unitized net load profile for reference year. This is multiplied by the erm_peak_load_mw and scaled with the erm_percentage to estimate the MW requirement for each hour.
Flexible Params | param - Name of operating constraints. model_component - Resource associated with the constraint. period - Year being referenced. day - Sample day being referenced. hour_of_day_from - Flexible parameter starts at this hour. hour_of_day_to - Flexible parameter ends at this hour. value - User defined input for constraint.
Fuels | fuels - Name of fuel being referenced. tco2_per_mmbtu - Tons of CO2 produced per mmbtu of fuel burned (tco2/mmbtu). can_blend_with_pipeline_biogas - Denotes whether the fuel can be blended with a RPS eligible fuel (T/F).
Min Cumulative New Build | resource - Name of the resource. period - Year being referenced. min_cumulative_build_by_year - Minimum amount of a new resource that must be built in the given year (MW).
Period Discount Factors | period - Year being referenced. discount_factor - Discount factor used to calculate cost. years_in_period - Number of years being considered in the period.
Planned Installed Capacities | resource - Name of the resource. period - Year being referenced. planned_installed_capacity - Capacity of each resource that is planned to be on the system (MW). min_operational_planned_capacity_mw - Minimum capacity of each resource that can't be retired and must remain on the system (MW). planned_capacity_fixed_o_and_m_dollars_per_kw_yr - Generator Fixed O&M cost in Real 2018$ ($/kW/year).
Planned Storage Energy Capacity | storage_resource - Name of storage resource. period - Year being referenced. planned_storage_energy_capacity_mwh - Capacity of each storage resource that is planned to be on the system (MWh). planned_storage_energy_capacity_fixed_o_and_m_dollars_per_kwh_yr - Storage Fixed O&M cost in Real 2018$ ($/kWh/year) .
Renewable Targets | period - Year being referenced. non_modeled_rps_resources_mwh - Amount of renewable energy from a resource that is not being modeled (MWh). pipeline_biogas_available_mmbtu_per_year - Amount of biofuel that can be used (mmbtu/yr). incremental_pipeline_biogas_cost_per_mmbtu - Incremental cost of blending the biofuel with another fuel ($/mmbtu). retail_sales_mwh - Customer sales to be used with RPS target to calculate amount of renewable generation needed (MWh). RPS_as_fractions_of_retail_sales - RPS target as percent of sales (%).
Reserve Resources | resource - Name of the resource. can_provide_lf_reserves - Denotes whether a resource can be used to meet the regulation requirement (1=Yes, 0=No). contributes_to_freq_resp_total - Denotes whether a resource can be used to meet the FFR requirement (1=Yes, 0=No). thermal_freq_response_fraction_of_commitment - Percent of resource that can be used to meet the FFR requirement (%). can_provide_inertia - Denotes wehther a resource can be used to meet the inertia requirement (T/F). inertia_response_multiplier_of_commitment - Inertia multiplier used to calculate amount of MJ a resource can provide (MJ/MW).
Resource Storage Paired | paired_storage_resource - Name of paired storage resource. paired_supply_resource - Name of paired supply resource. enforce_pairing_ratio - Denotes whether to enforce the pairing ratio (T/F) pairing_ratio - Ratio of installed capacity of supply resource to installed capacity of storage resource (MW Supply/MW Storage).
Resource Variable Renewable | resource - Name of the resource curtailable - Denotes whether the variable renewable resource is curtailable (T/F).
Resources | resource - Name of the resource. technology - Name of the technology. The technology is used to aggregate resources to simplify the optimization problem. zone - Area that the resource is located. rps_eligible - Denotes whether the resource contributes to the RPS target (1=Yes, 0=No). can_build_new - Denotes whether the resource can be built/expanded (1=Yes, 0=No). capacity_limited - Denotes if there is a capacity limit on this resource (1=Yes, 0=No). can_retire - Denotes if the resource can be retired (1=Yes, 0=No).
Simulatneous Flow Limits | simultaneous_flow_group - Name of transmission constraint. period - Year being referenced. simultaneous_flow_limit_mw - Transmission limit (MW).
System Params | unserved_energy_penalty - Penalty for unserved energy ($/MWh). overgen_penalty - Penalthy for overgeneration ($/MWh). upward_reserve_violation_penalty - Penalty for upward reserve shortfall ($/MW). downward_reserve_violation_penalty - Penalty for downward reserve shortfall ($/MW). lf_reserve_dispatch_fraction - Timeframe for reserve dispatch (% of hour). var_rnw_available_for_reserves - Percent of variable renewable available for reserves (%) max_var_rnw_reserves - Maximum capacity of variable renewable resources that can count towards reserves (%) require_overbuild - Denotes if resources are allowed to be overbuilt (T/F) enforce_ghg_targets - Denotes if GHG targets are used (T/F) count_storage_losses_as_rps_curtailment - Denotes if storage losses are counted as curtailment (T/F). allow_unserved_energy - Denotes if system can have unserved energy (T/F).
Tech Dispatchable Params | technology - Name of the dispatchable technology. Technology is used to aggregate resources to simplify the optimization problem. min_stable_level_fraction - Minimum stable level of the technology resource as a percent of unit size (%). ramp_rate_fraction - Maximum hourly ramp rate of the technology resource as a percent of unit size (%/hr). min_down_time_hours - Minimum hours that the technology resource must be offline when shutdown (hrs). min_up_time_hours - Minimum hours that the technology resource must be online when started (hrs). unit_size_mw - The size of the technology resource (MW). startup_cost_per_mw - Cost to start up the technology resource ($/MW). shutdown_cost_per_mw - Cost to shut down the technology resource ($/MW). start_fuel_mmbtu_per_mw - Amount of fuel consumed during startup (mmbtu/MW).
Tech Storage Params | storage_technology - Name of the storage technology. Technology is used to aggregate resources to simplify the optimization problem. charging_efficiency - Charging efficiency of the storage technology resource (%). discharging_efficiency - Discharging efficiency of the storage technology resource (%). duration_h - Duration of the storage technology resource (hrs). duration_type - Denotes if the duration being provided is the minimum duration of the storage and the storage can be increased, or if the duration is fixed.
Tech Thermal Params | technology - Name of the thermal technology. Technology is used to aggregate resources to simplify the optimization problem. fuel - Name of the fuel being used by the technology resource. fuel_burn_slope_mmbtu_per_mwh - Heat rate is defined by a linear heat curve a+bx. This is the 'b' term of the equation (mmbtu/MWh) fuel_burn_intercept_mmbtu_per_hr - Heat rate is defined by a linear heat curve a+bx. This is the 'a' term of the equation (mmbtu/hr)
Technologies | technology - Name of the technology. thermal - Denotes if the technology is a thermal resource (1=Yes, 0=No). dispatchable - Denotes if the technology is dispatchable (1=Yes, 0=No). must_run - Denotes if the technology is must-run (1=Yes, 0=No). variable - Denotes if the technology is a variable resource (1=Yes, 0=No). storage - Denotes if the technology is a storage resource (1=Yes, 0=No). hydro - Denotes if the technology is a hydro resource (1=Yes, 0=No). variable_cost_dollars_per_mwh - Technology's variable cost ($/MWh). firm_capacity - Denotes if the technology is a firm resource (1=Yes, 0=No). conventional_dr - Denotes if the technology is a DR resource (1=Yes, 0=No). hydrogen_electrolysis - Denotes if the technology is a hydrogen electrolysis resource (1=Yes, 0=No). electric_vehicle - Denotes if the technology is an electric vehicle resource (1=Yes, 0=No). energy_efficiency - Denotes if the technology is an energy efficient resource (1=Yes, 0=No). flexible_load - Denotes if the technology is a flexible load resource (1=Yes, 0=No). synchronous_condenser - Denotes if the technology is a synchronous condenser resource (1=Yes, 0=No).
Transmission Lines | transmission_line - Name of transmission line. transmission_from - Name of zone that energy flows away. transmission_to - Name of zone that energy flows towards. min_flow - Minimum energy that can flow in the transmission line (MW). max_flow - Maximum energy that can flow in the transmission line (MW).
Zones | zone - Name of zone. include_in_rps_target - Denotes if the zone and its resources are included in the RPS calculation (1=Yes, 0=No). include_in_load_following - Denotes if the zone and its resources are included in the reserve calculation (1=Yes, 0=No). include_in_ghg_target - Denotes if the zone and its resources are included in the GHG calculation (1=Yes, 0=No).
Technologies Calculations | Calculations used on existing thermal generators on the Technologies tab in RESOLVE.

## capacity_limits
Capacity Limits |  |  | Index
resource | period | capacity_limit_mw
Biomass | 2025 | 0
Biomass | 2026 | 0
Biomass | 2027 | 0
Biomass | 2028 | 9999
Biomass | 2029 | 9999
Biomass | 2030 | 9999
Biomass | 2031 | 9999
Biomass | 2032 | 9999
Biomass | 2033 | 9999
Biomass | 2034 | 9999
Biomass | 2040 | 9999
Biomass | 2045 | 9999
Biomass | 2050 | 9999
ICE_New | 2025 | 0
ICE_New | 2026 | 0
ICE_New | 2027 | 0
ICE_New | 2028 | 9999
ICE_New | 2029 | 9999
ICE_New | 2030 | 9999
ICE_New | 2031 | 9999
ICE_New | 2032 | 9999
ICE_New | 2033 | 9999
ICE_New | 2034 | 9999
ICE_New | 2040 | 9999
ICE_New | 2045 | 9999
ICE_New | 2050 | 9999
LM6000_2x1CC_Sync_Cond | 2025 | 0
LM6000_2x1CC_Sync_Cond | 2026 | 0
LM6000_2x1CC_Sync_Cond | 2027 | 0
LM6000_2x1CC_Sync_Cond | 2028 | 9999
LM6000_2x1CC_Sync_Cond | 2029 | 9999
LM6000_2x1CC_Sync_Cond | 2030 | 9999
LM6000_2x1CC_Sync_Cond | 2031 | 9999
LM6000_2x1CC_Sync_Cond | 2032 | 9999
LM6000_2x1CC_Sync_Cond | 2033 | 9999
LM6000_2x1CC_Sync_Cond | 2034 | 9999
LM6000_2x1CC_Sync_Cond | 2040 | 9999
LM6000_2x1CC_Sync_Cond | 2045 | 9999
LM6000_2x1CC_Sync_Cond | 2050 | 9999
Sync_Cond | 2025 | 9999
Sync_Cond | 2026 | 9999
Sync_Cond | 2027 | 9999
Sync_Cond | 2028 | 9999
Sync_Cond | 2029 | 9999
Sync_Cond | 2030 | 9999
Sync_Cond | 2031 | 9999
Sync_Cond | 2032 | 9999
Sync_Cond | 2033 | 9999
Sync_Cond | 2034 | 9999
Sync_Cond | 2040 | 9999
Sync_Cond | 2045 | 9999
Sync_Cond | 2050 | 9999
SC_6000CC_New | 2025 | 0
SC_6000CC_New | 2026 | 0
SC_6000CC_New | 2027 | 0
SC_6000CC_New | 2028 | 9999
SC_6000CC_New | 2029 | 9999
SC_6000CC_New | 2030 | 9999
SC_6000CC_New | 2031 | 9999
SC_6000CC_New | 2032 | 9999
SC_6000CC_New | 2033 | 9999
SC_6000CC_New | 2034 | 9999
SC_6000CC_New | 2040 | 9999
SC_6000CC_New | 2045 | 9999
SC_6000CC_New | 2050 | 9999
Solar_Grid-Scale_Single-Tracking_New | 2025 | 0
Solar_Grid-Scale_Single-Tracking_New | 2026 | 0
Solar_Grid-Scale_Single-Tracking_New | 2027 | 0
Solar_Grid-Scale_Single-Tracking_New | 2028 | 0
Solar_Grid-Scale_Single-Tracking_New | 2029 | 0
Solar_Grid-Scale_Single-Tracking_New | 2030 | 0
Solar_Grid-Scale_Single-Tracking_New | 2031 | 0
Solar_Grid-Scale_Single-Tracking_New | 2032 | 0
Solar_Grid-Scale_Single-Tracking_New | 2033 | 0
Solar_Grid-Scale_Single-Tracking_New | 2034 | 0
Solar_Grid-Scale_Single-Tracking_New | 2040 | 0
Solar_Grid-Scale_Single-Tracking_New | 2045 | 0
Solar_Grid-Scale_Single-Tracking_New | 2050 | 0
Wind_Onshore_New | 2025 | 210
Wind_Onshore_New | 2026 | 210
Wind_Onshore_New | 2027 | 210
Wind_Onshore_New | 2028 | 210
Wind_Onshore_New | 2029 | 210
Wind_Onshore_New | 2030 | 210
Wind_Onshore_New | 2031 | 240
Wind_Onshore_New | 2032 | 240
Wind_Onshore_New | 2033 | 240
Wind_Onshore_New | 2034 | 240
Wind_Onshore_New | 2040 | 309
Wind_Onshore_New | 2045 | 333
Wind_Onshore_New | 2050 | 333
Wind_Offshore_New | 2025 | 0
Wind_Offshore_New | 2026 | 0
Wind_Offshore_New | 2027 | 0
Wind_Offshore_New | 2028 | 0
Wind_Offshore_New | 2029 | 0
Wind_Offshore_New | 2030 | 9999
Wind_Offshore_New | 2031 | 9999
Wind_Offshore_New | 2032 | 9999
Wind_Offshore_New | 2033 | 9999
Wind_Offshore_New | 2034 | 9999
Wind_Offshore_New | 2040 | 9999
Wind_Offshore_New | 2045 | 9999
Wind_Offshore_New | 2050 | 9999
PV_Paired_Grid_4hr_New_Supply | 2025 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2026 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2027 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2028 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2029 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2030 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2031 | 1958.8
PV_Paired_Grid_4hr_New_Supply | 2032 | 1959.8
PV_Paired_Grid_4hr_New_Supply | 2033 | 1964.8
PV_Paired_Grid_4hr_New_Supply | 2034 | 1969.8
PV_Paired_Grid_4hr_New_Supply | 2040 | 1997.4
PV_Paired_Grid_4hr_New_Supply | 2045 | 2386
PV_Paired_Grid_4hr_New_Supply | 2050 | 2557
PV_Paired_Grid_6hr_New_Supply | 2025 | 0
PV_Paired_Grid_6hr_New_Supply | 2026 | 0
PV_Paired_Grid_6hr_New_Supply | 2027 | 0
PV_Paired_Grid_6hr_New_Supply | 2028 | 0
PV_Paired_Grid_6hr_New_Supply | 2029 | 0
PV_Paired_Grid_6hr_New_Supply | 2030 | 0
PV_Paired_Grid_6hr_New_Supply | 2031 | 0
PV_Paired_Grid_6hr_New_Supply | 2032 | 0
PV_Paired_Grid_6hr_New_Supply | 2033 | 0
PV_Paired_Grid_6hr_New_Supply | 2034 | 0
PV_Paired_Grid_6hr_New_Supply | 2040 | 0
PV_Paired_Grid_6hr_New_Supply | 2045 | 0
PV_Paired_Grid_6hr_New_Supply | 2050 | 0
PV_Aggregated_DER_Supply | 2025 | 3278.288
PV_Aggregated_DER_Supply | 2026 | 3258.397
PV_Aggregated_DER_Supply | 2027 | 3238.505
PV_Aggregated_DER_Supply | 2028 | 3217.66
PV_Aggregated_DER_Supply | 2029 | 3196.933
PV_Aggregated_DER_Supply | 2030 | 3176.155
PV_Aggregated_DER_Supply | 2031 | 3155.978
PV_Aggregated_DER_Supply | 2032 | 3136.336
PV_Aggregated_DER_Supply | 2033 | 3117.708
PV_Aggregated_DER_Supply | 2034 | 3099.233
PV_Aggregated_DER_Supply | 2040 | 2997.626
PV_Aggregated_DER_Supply | 2045 | 2922.899
PV_Aggregated_DER_Supply | 2050 | 2860.895
PV_Paired_LowCF_4hr_New_Supply | 2025 | 91
PV_Paired_LowCF_4hr_New_Supply | 2026 | 91
PV_Paired_LowCF_4hr_New_Supply | 2027 | 91
PV_Paired_LowCF_4hr_New_Supply | 2028 | 91
PV_Paired_LowCF_4hr_New_Supply | 2029 | 91
PV_Paired_LowCF_4hr_New_Supply | 2030 | 91
PV_Paired_LowCF_4hr_New_Supply | 2031 | 91
PV_Paired_LowCF_4hr_New_Supply | 2032 | 91
PV_Paired_LowCF_4hr_New_Supply | 2033 | 91
PV_Paired_LowCF_4hr_New_Supply | 2034 | 91
PV_Paired_LowCF_4hr_New_Supply | 2040 | 91
PV_Paired_LowCF_4hr_New_Supply | 2045 | 91
PV_Paired_LowCF_4hr_New_Supply | 2050 | 91
PV_Paired_LowCF_6hr_New_Supply | 2025 | 91
PV_Paired_LowCF_6hr_New_Supply | 2026 | 91
PV_Paired_LowCF_6hr_New_Supply | 2027 | 91
PV_Paired_LowCF_6hr_New_Supply | 2028 | 91
PV_Paired_LowCF_6hr_New_Supply | 2029 | 91
PV_Paired_LowCF_6hr_New_Supply | 2030 | 91
PV_Paired_LowCF_6hr_New_Supply | 2031 | 91
PV_Paired_LowCF_6hr_New_Supply | 2032 | 91
PV_Paired_LowCF_6hr_New_Supply | 2033 | 91
PV_Paired_LowCF_6hr_New_Supply | 2034 | 91
PV_Paired_LowCF_6hr_New_Supply | 2040 | 91
PV_Paired_LowCF_6hr_New_Supply | 2045 | 91
PV_Paired_LowCF_6hr_New_Supply | 2050 | 91
Battery_Grid-Scale_New | 2025 | 9999
Battery_Grid-Scale_New | 2026 | 9999
Battery_Grid-Scale_New | 2027 | 9999
Battery_Grid-Scale_New | 2028 | 9999
Battery_Grid-Scale_New | 2029 | 9999
Battery_Grid-Scale_New | 2030 | 9999
Battery_Grid-Scale_New | 2031 | 9999
Battery_Grid-Scale_New | 2032 | 9999
Battery_Grid-Scale_New | 2033 | 9999
Battery_Grid-Scale_New | 2034 | 9999
Battery_Grid-Scale_New | 2040 | 9999
Battery_Grid-Scale_New | 2045 | 9999
Battery_Grid-Scale_New | 2050 | 9999
PV_Paired_Grid_4hr_New_Battery | 2025 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2026 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2027 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2028 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2029 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2030 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2031 | 1958.8
PV_Paired_Grid_4hr_New_Battery | 2032 | 1959.8
PV_Paired_Grid_4hr_New_Battery | 2033 | 1964.8
PV_Paired_Grid_4hr_New_Battery | 2034 | 1969.8
PV_Paired_Grid_4hr_New_Battery | 2040 | 1997.4
PV_Paired_Grid_4hr_New_Battery | 2045 | 2386
PV_Paired_Grid_4hr_New_Battery | 2050 | 2557
PV_Paired_Grid_6hr_New_Battery | 2025 | 0
PV_Paired_Grid_6hr_New_Battery | 2026 | 0
PV_Paired_Grid_6hr_New_Battery | 2027 | 0
PV_Paired_Grid_6hr_New_Battery | 2028 | 0
PV_Paired_Grid_6hr_New_Battery | 2029 | 0
PV_Paired_Grid_6hr_New_Battery | 2030 | 0
PV_Paired_Grid_6hr_New_Battery | 2031 | 0
PV_Paired_Grid_6hr_New_Battery | 2032 | 0
PV_Paired_Grid_6hr_New_Battery | 2033 | 0
PV_Paired_Grid_6hr_New_Battery | 2034 | 0
PV_Paired_Grid_6hr_New_Battery | 2040 | 0
PV_Paired_Grid_6hr_New_Battery | 2045 | 0
PV_Paired_Grid_6hr_New_Battery | 2050 | 0
PV_Aggregated_DER_Battery | 2025 | 3278.288
PV_Aggregated_DER_Battery | 2026 | 3258.397
PV_Aggregated_DER_Battery | 2027 | 3238.505
PV_Aggregated_DER_Battery | 2028 | 3217.66
PV_Aggregated_DER_Battery | 2029 | 3196.933
PV_Aggregated_DER_Battery | 2030 | 3176.155
PV_Aggregated_DER_Battery | 2031 | 3155.978
PV_Aggregated_DER_Battery | 2032 | 3136.336
PV_Aggregated_DER_Battery | 2033 | 3117.708
PV_Aggregated_DER_Battery | 2034 | 3099.233
PV_Aggregated_DER_Battery | 2040 | 2997.626
PV_Aggregated_DER_Battery | 2045 | 2922.899
PV_Aggregated_DER_Battery | 2050 | 2860.895
PV_Paired_LowCF_4hr_New_Battery | 2025 | 91
PV_Paired_LowCF_4hr_New_Battery | 2026 | 91
PV_Paired_LowCF_4hr_New_Battery | 2027 | 91
PV_Paired_LowCF_4hr_New_Battery | 2028 | 91
PV_Paired_LowCF_4hr_New_Battery | 2029 | 91
PV_Paired_LowCF_4hr_New_Battery | 2030 | 91
PV_Paired_LowCF_4hr_New_Battery | 2031 | 91
PV_Paired_LowCF_4hr_New_Battery | 2032 | 91
PV_Paired_LowCF_4hr_New_Battery | 2033 | 91
PV_Paired_LowCF_4hr_New_Battery | 2034 | 91
PV_Paired_LowCF_4hr_New_Battery | 2040 | 91
PV_Paired_LowCF_4hr_New_Battery | 2045 | 91
PV_Paired_LowCF_4hr_New_Battery | 2050 | 91
PV_Paired_LowCF_6hr_New_Battery | 2025 | 91
PV_Paired_LowCF_6hr_New_Battery | 2026 | 91
PV_Paired_LowCF_6hr_New_Battery | 2027 | 91
PV_Paired_LowCF_6hr_New_Battery | 2028 | 91
PV_Paired_LowCF_6hr_New_Battery | 2029 | 91
PV_Paired_LowCF_6hr_New_Battery | 2030 | 91
PV_Paired_LowCF_6hr_New_Battery | 2031 | 91
PV_Paired_LowCF_6hr_New_Battery | 2032 | 91
PV_Paired_LowCF_6hr_New_Battery | 2033 | 91
PV_Paired_LowCF_6hr_New_Battery | 2034 | 91
PV_Paired_LowCF_6hr_New_Battery | 2040 | 91
PV_Paired_LowCF_6hr_New_Battery | 2045 | 91
PV_Paired_LowCF_6hr_New_Battery | 2050 | 91

## conventional_dr_period_limits
Conventional DR period Limits |  |  |  | Index
resource | period | conventional_dr_availability_hours_per_year | daily_capacity_factor
Load_reduce | 2025 | 416 | 0.16667
Load_reduce | 2026 | 416 | 0.16667
Load_reduce | 2027 | 416 | 0.16667
Load_reduce | 2028 | 416 | 0.16667
Load_reduce | 2029 | 416 | 0.16667
Load_reduce | 2030 | 416 | 0.16667
Load_reduce | 2031 | 416 | 0.16667
Load_reduce | 2032 | 416 | 0.16667
Load_reduce | 2033 | 416 | 0.16667
Load_reduce | 2034 | 416 | 0.16667
Load_reduce | 2040 | 416 | 0.16667
Load_reduce | 2045 | 416 | 0.16667
Load_reduce | 2050 | 416 | 0.16667

## day_weights
Day Weights |  | Index
day_id | day_weight
1 | 26.3268
2 | 20.1325
3 | 19.134
4 | 18.7574
5 | 18.0397
6 | 17.2416
7 | 16.36
8 | 16.3116
9 | 15.9266
10 | 15.8062
11 | 15.7372
12 | 15.2425
13 | 14.913
14 | 14.6681
15 | 13.738
16 | 13.4067
17 | 12.2823
18 | 12.2223
19 | 10.1918
20 | 9.8009
21 | 9.3938
22 | 8.1256
23 | 7.6788
24 | 6.0485
25 | 5.9415
26 | 5.2906
27 | 2.6535
28 | 1.4534
29 | 1.175
30 | 1

## energy_sharing_max_to_move_with
Energy Sharing Max to Move With |  |  | Index
hydro_resource | energy_sharing_group_id | max_energy_to_move_around_hours
Waiau_3-4 | 1 | 700.8

## erm_params
ERM Params |  |  | Index
period | erm_percentage | erm_peak_load_mw
2025 | 0.3 | 1237.4061
2026 | 0.3 | 1216.5893
2027 | 0.3 | 1216.8458
2028 | 0.3 | 1215.5234
2029 | 0.3 | 1222.4143
2030 | 0.3 | 1238.4284
2031 | 0.3 | 1258.042
2032 | 0.3 | 1261.378
2033 | 0.3 | 1274.1575
2034 | 0.3 | 1277.2103
2040 | 0.3 | 1357.3794
2045 | 0.3 | 1505.0002
2050 | 0.3 | 1669.9068

## erm_resource_group_map
ERM Resource Group Map |  | Index
resource | erm_group
AES | firm
Airport_DSG | firm
Biomass | firm
CIP_BioD | firm
CIP_Diesel | firm
Hpoff | firm
ICE_New | firm
Kahe_5-6 | firm
Kala1 | firm
Kala1_Biod | firm
Kala2 | firm
Kala2_Biod | firm
LM6000_2x1CC_Sync_Cond | firm
Schofield | firm
Schofield_Biod | firm
Waiau_3-4 | firm
Waiau_5-6 | firm
Waiau_9-10 | firm
SC_6000CC_New | firm
K14_W78 | firm
Load_reduce | lsdr
Hoohana_Solar_Supply | paired_solar
Mililani_Solar_1_Supply | paired_solar
PV_Barbers_Point_Supply | paired_solar
PV_Kupehau_Supply | paired_solar
PV_Kupono_Supply | paired_solar
PV_Mahi_Supply | paired_solar
PV_Mountain_View_Supply | paired_solar
PV_Paired_Grid_4hr_New_Supply | paired_solar
PV_Paired_Grid_6hr_New_Supply | paired_solar
PV_Paired_LowCF_4hr_New_Supply | paired_solar
PV_Paired_LowCF_6hr_New_Supply | paired_solar
PV_Waiawa_Ph2_Supply | paired_solar
Waiawa_Solar_Supply | paired_solar
West_Oahu_Solar_Supply | paired_solar
Hoohana_Solar_Battery | paired_storage
Mililani_Solar_1_Battery | paired_storage
PV_Barbers_Point_Battery | paired_storage
PV_Kupehau_Battery | paired_storage
PV_Kupono_Battery | paired_storage
PV_Mahi_Battery | paired_storage
PV_Mountain_View_Battery | paired_storage
PV_Paired_Grid_4hr_New_Battery | paired_storage
PV_Paired_Grid_6hr_New_Battery | paired_storage
PV_Paired_LowCF_4hr_New_Battery | paired_storage
PV_Paired_LowCF_6hr_New_Battery | paired_storage
PV_Waiawa_Ph2_Battery | paired_storage
Waiawa_Solar_Battery | paired_storage
West_Oahu_Solar_Battery | paired_storage
Solar_CBRE | solar
Solar_Grid-Scale_Single-Tracking_New | solar
Solar_Planned | solar
Solar_Waianae | solar
Battery_Grid-Scale_New | stand_alone_storage
Battery_Grid-Scale_Planned | stand_alone_storage
Kapolei_Energy_Storage | stand_alone_storage
Wind_NPM | wind
Wind_Offshore_New | wind
Wind_Offshore_Planned | wind
Wind_Onshore_New | wind
Wind_Onshore_Planned | wind
PV_Aggregated_DER_Supply | paired_solar
PV_Aggregated_DER_Battery | paired_storage

## erm_shapes
ERM Shapes | [9 empty] | Index
erm_hour | solar | wind | firm | DGPV | lsdr | stand_alone_storage | paired_solar | paired_wind | paired_storage
1 | 0 | 0.0087473 | 0.96512 | 0 | 0 | 1 | 0 | 0.0087473 | 1
2 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
3 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
4 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
5 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
6 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
7 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
8 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
9 | 0.022261 | 0 | 0.96512 | 0 | 0 | 1 | 0.022261 | 0 | 1
10 | 0.21082 | 0 | 0.96512 | 0 | 0 | 1 | 0.21082 | 0 | 1
11 | 0.36056 | 0 | 0.96512 | 0 | 0 | 1 | 0.36056 | 0 | 1
12 | 0.43102 | 0.0056599 | 0.96512 | 0 | 0 | 1 | 0.43102 | 0.0056599 | 1
13 | 0.37884 | 0.0030331 | 0.96512 | 0 | 0 | 1 | 0.37884 | 0.0030331 | 1
14 | 0.38017 | 0.0096523 | 0.96512 | 0 | 0 | 1 | 0.38017 | 0.0096523 | 1
15 | 0.29555 | 0.023086 | 0.96512 | 0 | 0 | 1 | 0.29555 | 0.023086 | 1
16 | 0.13645 | 0.04272 | 0.96512 | 0 | 0 | 1 | 0.13645 | 0.04272 | 1
17 | 0 | 0.045475 | 0.96512 | 0 | 0 | 1 | 0 | 0.045475 | 1
18 | 0 | 0.030141 | 0.96512 | 0 | 1 | 1 | 0 | 0.030141 | 1
19 | 0 | 0.027691 | 0.96512 | 0 | 1 | 1 | 0 | 0.027691 | 1
20 | 0 | 0.02308 | 0.96512 | 0 | 1 | 1 | 0 | 0.02308 | 1
21 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
22 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
23 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
24 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
25 | 0 | 0.0087473 | 0.96512 | 0 | 0 | 1 | 0 | 0.0087473 | 1
26 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
27 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
28 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
29 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
30 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
31 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
32 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
33 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
34 | 0.13698 | 0 | 0.96512 | 0 | 0 | 1 | 0.13698 | 0 | 1
35 | 0.21227 | 0 | 0.96512 | 0 | 0 | 1 | 0.21227 | 0 | 1
36 | 0.2752 | 0 | 0.96512 | 0 | 0 | 1 | 0.2752 | 0 | 1
37 | 0.22454 | 0.0078128 | 0.96512 | 0 | 0 | 1 | 0.22454 | 0.0078128 | 1
38 | 0.23383 | 0.01544 | 0.96512 | 0 | 0 | 1 | 0.23383 | 0.01544 | 1
39 | 0.17662 | 0.036512 | 0.96512 | 0 | 0 | 1 | 0.17662 | 0.036512 | 1
40 | 0.057582 | 0.045294 | 0.96512 | 0 | 0 | 1 | 0.057582 | 0.045294 | 1
41 | 0 | 0.037795 | 0.96512 | 0 | 0 | 1 | 0 | 0.037795 | 1
42 | 0 | 0.014836 | 0.96512 | 0 | 1 | 1 | 0 | 0.014836 | 1
43 | 0 | 0.010016 | 0.96512 | 0 | 1 | 1 | 0 | 0.010016 | 1
44 | 0 | 0.023646 | 0.96512 | 0 | 1 | 1 | 0 | 0.023646 | 1
45 | 0 | 0.007512 | 0.96512 | 0 | 1 | 1 | 0 | 0.007512 | 1
46 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
47 | 0 | 0.00098148 | 0.96512 | 0 | 0 | 1 | 0 | 0.00098148 | 1
48 | 0 | 0.02112 | 0.96512 | 0 | 0 | 1 | 0 | 0.02112 | 1
49 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
50 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
51 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
52 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
53 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
54 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
55 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
56 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
57 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
58 | 0.10666 | 0 | 0.96512 | 0 | 0 | 1 | 0.10666 | 0 | 1
59 | 0.18543 | 0.013097 | 0.96512 | 0 | 0 | 1 | 0.18543 | 0.013097 | 1
60 | 0.25837 | 0.027799 | 0.96512 | 0 | 0 | 1 | 0.25837 | 0.027799 | 1
61 | 0.25173 | 0.035397 | 0.96512 | 0 | 0 | 1 | 0.25173 | 0.035397 | 1
62 | 0.23523 | 0.037785 | 0.96512 | 0 | 0 | 1 | 0.23523 | 0.037785 | 1
63 | 0.11465 | 0.050523 | 0.96512 | 0 | 0 | 1 | 0.11465 | 0.050523 | 1
64 | 0.039666 | 0.039271 | 0.96512 | 0 | 0 | 1 | 0.039666 | 0.039271 | 1
65 | 0 | 0.033327 | 0.96512 | 0 | 0 | 1 | 0 | 0.033327 | 1
66 | 0 | 0.022241 | 0.96512 | 0 | 1 | 1 | 0 | 0.022241 | 1
67 | 0 | 0.017815 | 0.96512 | 0 | 1 | 1 | 0 | 0.017815 | 1
68 | 0 | 0.024893 | 0.96512 | 0 | 1 | 1 | 0 | 0.024893 | 1
69 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
70 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
71 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
72 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
73 | 0 | 0.0073326 | 0.96512 | 0 | 0 | 1 | 0 | 0.0073326 | 1
74 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
75 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
76 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
77 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
78 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
79 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
80 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
81 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
82 | 0.12229 | 0 | 0.96512 | 0 | 0 | 1 | 0.12229 | 0 | 1
83 | 0.16938 | 0 | 0.96512 | 0 | 0 | 1 | 0.16938 | 0 | 1
84 | 0.20672 | 0 | 0.96512 | 0 | 0 | 1 | 0.20672 | 0 | 1
85 | 0.17022 | 0 | 0.96512 | 0 | 0 | 1 | 0.17022 | 0 | 1
86 | 0.16304 | 0.00050477 | 0.96512 | 0 | 0 | 1 | 0.16304 | 0.00050477 | 1
87 | 0.055689 | 0.016223 | 0.96512 | 0 | 0 | 1 | 0.055689 | 0.016223 | 1
88 | 0.05345 | 0.0016525 | 0.96512 | 0 | 0 | 1 | 0.05345 | 0.0016525 | 1
89 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
90 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
91 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
92 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
93 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
94 | 0 | 0.001368 | 0.96512 | 0 | 0 | 1 | 0 | 0.001368 | 1
95 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
96 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
97 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
98 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
99 | 0 | 0.010785 | 0.96512 | 0 | 0 | 1 | 0 | 0.010785 | 1
100 | 0 | 0.014851 | 0.96512 | 0 | 0 | 1 | 0 | 0.014851 | 1
101 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
102 | 0 | 0.0040402 | 0.96512 | 0 | 0 | 1 | 0 | 0.0040402 | 1
103 | 0 | 0.0053584 | 0.96512 | 0 | 0 | 1 | 0 | 0.0053584 | 1
104 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
105 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
106 | 0.14518 | 0 | 0.96512 | 0 | 0 | 1 | 0.14518 | 0 | 1
107 | 0.20762 | 0.001959 | 0.96512 | 0 | 0 | 1 | 0.20762 | 0.001959 | 1
108 | 0.24743 | 0.013014 | 0.96512 | 0 | 0 | 1 | 0.24743 | 0.013014 | 1
109 | 0.21423 | 0.011234 | 0.96512 | 0 | 0 | 1 | 0.21423 | 0.011234 | 1
110 | 0.18872 | 0.0058278 | 0.96512 | 0 | 0 | 1 | 0.18872 | 0.0058278 | 1
111 | 0.080801 | 0.031355 | 0.96512 | 0 | 0 | 1 | 0.080801 | 0.031355 | 1
112 | 0.086242 | 0.025815 | 0.96512 | 0 | 0 | 1 | 0.086242 | 0.025815 | 1
113 | 0 | 0.0094339 | 0.96512 | 0 | 0 | 1 | 0 | 0.0094339 | 1
114 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
115 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
116 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
117 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
118 | 0 | 0.00082547 | 0.96512 | 0 | 0 | 1 | 0 | 0.00082547 | 1
119 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
120 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
121 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
122 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
123 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
124 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
125 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
126 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
127 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
128 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
129 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
130 | 0.18114 | 0 | 0.96512 | 0 | 0 | 1 | 0.18114 | 0 | 1
131 | 0.24363 | 0 | 0.96512 | 0 | 0 | 1 | 0.24363 | 0 | 1
132 | 0.21919 | 0 | 0.96512 | 0 | 0 | 1 | 0.21919 | 0 | 1
133 | 0.18523 | 0 | 0.96512 | 0 | 0 | 1 | 0.18523 | 0 | 1
134 | 0.18039 | 0 | 0.96512 | 0 | 0 | 1 | 0.18039 | 0 | 1
135 | 0.13627 | 0.021104 | 0.96512 | 0 | 0 | 1 | 0.13627 | 0.021104 | 1
136 | 0.12483 | 0.011751 | 0.96512 | 0 | 0 | 1 | 0.12483 | 0.011751 | 1
137 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
138 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
139 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
140 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
141 | 0 | 0.011984 | 0.96512 | 0 | 1 | 1 | 0 | 0.011984 | 1
142 | 0 | 0.011117 | 0.96512 | 0 | 0 | 1 | 0 | 0.011117 | 1
143 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
144 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
145 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
146 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
147 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
148 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
149 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
150 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
151 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
152 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
153 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
154 | 0.17919 | 0 | 0.96512 | 0 | 0 | 1 | 0.17919 | 0 | 1
155 | 0.24823 | 0 | 0.96512 | 0 | 0 | 1 | 0.24823 | 0 | 1
156 | 0.23585 | 0 | 0.96512 | 0 | 0 | 1 | 0.23585 | 0 | 1
157 | 0.29714 | 0 | 0.96512 | 0 | 0 | 1 | 0.29714 | 0 | 1
158 | 0.28031 | 0 | 0.96512 | 0 | 0 | 1 | 0.28031 | 0 | 1
159 | 0.20923 | 0.030446 | 0.96512 | 0 | 0 | 1 | 0.20923 | 0.030446 | 1
160 | 0.1269 | 0.030762 | 0.96512 | 0 | 0 | 1 | 0.1269 | 0.030762 | 1
161 | 0 | 0.00086921 | 0.96512 | 0 | 0 | 1 | 0 | 0.00086921 | 1
162 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
163 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
164 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
165 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
166 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
167 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
168 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
169 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
170 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
171 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
172 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
173 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
174 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
175 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
176 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
177 | 0.009691 | 0 | 0.96512 | 0 | 0 | 1 | 0.009691 | 0 | 1
178 | 0.19588 | 0 | 0.96512 | 0 | 0 | 1 | 0.19588 | 0 | 1
179 | 0.29557 | 0 | 0.96512 | 0 | 0 | 1 | 0.29557 | 0 | 1
180 | 0.32777 | 0 | 0.96512 | 0 | 0 | 1 | 0.32777 | 0 | 1
181 | 0.44302 | 0 | 0.96512 | 0 | 0 | 1 | 0.44302 | 0 | 1
182 | 0.38648 | 0 | 0.96512 | 0 | 0 | 1 | 0.38648 | 0 | 1
183 | 0.27736 | 0.0082193 | 0.96512 | 0 | 0 | 1 | 0.27736 | 0.0082193 | 1
184 | 0.12801 | 0.0013076 | 0.96512 | 0 | 0 | 1 | 0.12801 | 0.0013076 | 1
185 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
186 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
187 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
188 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
189 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
190 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
191 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
192 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
193 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
194 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
195 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
196 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
197 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
198 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
199 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
200 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
201 | 0.028017 | 0 | 0.96512 | 0 | 0 | 1 | 0.028017 | 0 | 1
202 | 0.19489 | 0 | 0.96512 | 0 | 0 | 1 | 0.19489 | 0 | 1
203 | 0.27916 | 0 | 0.96512 | 0 | 0 | 1 | 0.27916 | 0 | 1
204 | 0.33778 | 0 | 0.96512 | 0 | 0 | 1 | 0.33778 | 0 | 1
205 | 0.43736 | 0 | 0.96512 | 0 | 0 | 1 | 0.43736 | 0 | 1
206 | 0.39887 | 0 | 0.96512 | 0 | 0 | 1 | 0.39887 | 0 | 1
207 | 0.28342 | 0.0048239 | 0.96512 | 0 | 0 | 1 | 0.28342 | 0.0048239 | 1
208 | 0.13017 | 0.015147 | 0.96512 | 0 | 0 | 1 | 0.13017 | 0.015147 | 1
209 | 0.00091317 | 0 | 0.96512 | 0 | 0 | 1 | 0.00091317 | 0 | 1
210 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
211 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
212 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
213 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
214 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
215 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
216 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
217 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
218 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
219 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
220 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
221 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
222 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
223 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
224 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
225 | 0.013693 | 0 | 0.96512 | 0 | 0 | 1 | 0.013693 | 0 | 1
226 | 0.14954 | 0 | 0.96512 | 0 | 0 | 1 | 0.14954 | 0 | 1
227 | 0.22334 | 0 | 0.96512 | 0 | 0 | 1 | 0.22334 | 0 | 1
228 | 0.22759 | 0 | 0.96512 | 0 | 0 | 1 | 0.22759 | 0 | 1
229 | 0.23294 | 0 | 0.96512 | 0 | 0 | 1 | 0.23294 | 0 | 1
230 | 0.21801 | 0 | 0.96512 | 0 | 0 | 1 | 0.21801 | 0 | 1
231 | 0.2543 | 0.001199 | 0.96512 | 0 | 0 | 1 | 0.2543 | 0.001199 | 1
232 | 0.087321 | 0 | 0.96512 | 0 | 0 | 1 | 0.087321 | 0 | 1
233 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
234 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
235 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
236 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
237 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
238 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
239 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
240 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
241 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
242 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
243 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
244 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
245 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
246 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
247 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
248 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
249 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
250 | 0.10981 | 0 | 0.96512 | 0 | 0 | 1 | 0.10981 | 0 | 1
251 | 0.16565 | 0 | 0.96512 | 0 | 0 | 1 | 0.16565 | 0 | 1
252 | 0.12853 | 0 | 0.96512 | 0 | 0 | 1 | 0.12853 | 0 | 1
253 | 0.12448 | 0 | 0.96512 | 0 | 0 | 1 | 0.12448 | 0 | 1
254 | 0.12496 | 0 | 0.96512 | 0 | 0 | 1 | 0.12496 | 0 | 1
255 | 0.16377 | 0 | 0.96512 | 0 | 0 | 1 | 0.16377 | 0 | 1
256 | 0.068225 | 0 | 0.96512 | 0 | 0 | 1 | 0.068225 | 0 | 1
257 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
258 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
259 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
260 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
261 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
262 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
263 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
264 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
265 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
266 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
267 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
268 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
269 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
270 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
271 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
272 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
273 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
274 | 0.1273 | 0 | 0.96512 | 0 | 0 | 1 | 0.1273 | 0 | 1
275 | 0.19056 | 0 | 0.96512 | 0 | 0 | 1 | 0.19056 | 0 | 1
276 | 0.16954 | 0 | 0.96512 | 0 | 0 | 1 | 0.16954 | 0 | 1
277 | 0.17685 | 0 | 0.96512 | 0 | 0 | 1 | 0.17685 | 0 | 1
278 | 0.14149 | 0 | 0.96512 | 0 | 0 | 1 | 0.14149 | 0 | 1
279 | 0.18833 | 0 | 0.96512 | 0 | 0 | 1 | 0.18833 | 0 | 1
280 | 0.0601 | 0 | 0.96512 | 0 | 0 | 1 | 0.0601 | 0 | 1
281 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
282 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
283 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
284 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
285 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
286 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
287 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
288 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
289 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
290 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
291 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
292 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
293 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
294 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
295 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
296 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
297 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
298 | 0.11363 | 0 | 0.96512 | 0 | 0 | 1 | 0.11363 | 0 | 1
299 | 0.20238 | 0 | 0.96512 | 0 | 0 | 1 | 0.20238 | 0 | 1
300 | 0.26212 | 0 | 0.96512 | 0 | 0 | 1 | 0.26212 | 0 | 1
301 | 0.25579 | 0 | 0.96512 | 0 | 0 | 1 | 0.25579 | 0 | 1
302 | 0.21024 | 0 | 0.96512 | 0 | 0 | 1 | 0.21024 | 0 | 1
303 | 0.21661 | 0 | 0.96512 | 0 | 0 | 1 | 0.21661 | 0 | 1
304 | 0.10857 | 0 | 0.96512 | 0 | 0 | 1 | 0.10857 | 0 | 1
305 | 0.00040769 | 0 | 0.96512 | 0 | 0 | 1 | 0.00040769 | 0 | 1
306 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
307 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
308 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
309 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
310 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
311 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
312 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
313 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
314 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
315 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
316 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
317 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
318 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
319 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
320 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
321 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
322 | 0.12677 | 0 | 0.96512 | 0 | 0 | 1 | 0.12677 | 0 | 1
323 | 0.23891 | 0 | 0.96512 | 0 | 0 | 1 | 0.23891 | 0 | 1
324 | 0.32664 | 0 | 0.96512 | 0 | 0 | 1 | 0.32664 | 0 | 1
325 | 0.34776 | 0 | 0.96512 | 0 | 0 | 1 | 0.34776 | 0 | 1
326 | 0.2635 | 0 | 0.96512 | 0 | 0 | 1 | 0.2635 | 0 | 1
327 | 0.26535 | 0 | 0.96512 | 0 | 0 | 1 | 0.26535 | 0 | 1
328 | 0.1353 | 0 | 0.96512 | 0 | 0 | 1 | 0.1353 | 0 | 1
329 | 0.042222 | 0 | 0.96512 | 0 | 0 | 1 | 0.042222 | 0 | 1
330 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
331 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
332 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
333 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
334 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
335 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
336 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
337 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
338 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
339 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
340 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
341 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
342 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
343 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
344 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
345 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
346 | 0.071753 | 0 | 0.88973 | 0 | 0 | 1 | 0.071753 | 0 | 1
347 | 0.19562 | 0 | 0.88973 | 0 | 0 | 1 | 0.19562 | 0 | 1
348 | 0.27561 | 0 | 0.88973 | 0 | 0 | 1 | 0.27561 | 0 | 1
349 | 0.31747 | 0 | 0.88973 | 0 | 0 | 1 | 0.31747 | 0 | 1
350 | 0.27073 | 0 | 0.88973 | 0 | 0 | 1 | 0.27073 | 0 | 1
351 | 0.24299 | 0 | 0.88973 | 0 | 0 | 1 | 0.24299 | 0 | 1
352 | 0.10906 | 0 | 0.88973 | 0 | 0 | 1 | 0.10906 | 0 | 1
353 | 0.022578 | 0 | 0.88973 | 0 | 0 | 1 | 0.022578 | 0 | 1
354 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
355 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
356 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
357 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
358 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
359 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
360 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
361 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
362 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
363 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
364 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
365 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
366 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
367 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
368 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
369 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
370 | 0.080358 | 0 | 0.88973 | 0 | 0 | 1 | 0.080358 | 0 | 1
371 | 0.20764 | 0 | 0.88973 | 0 | 0 | 1 | 0.20764 | 0 | 1
372 | 0.26831 | 0 | 0.88973 | 0 | 0 | 1 | 0.26831 | 0 | 1
373 | 0.3207 | 0 | 0.88973 | 0 | 0 | 1 | 0.3207 | 0 | 1
374 | 0.26056 | 0 | 0.88973 | 0 | 0 | 1 | 0.26056 | 0 | 1
375 | 0.24937 | 0 | 0.88973 | 0 | 0 | 1 | 0.24937 | 0 | 1
376 | 0.13507 | 0 | 0.88973 | 0 | 0 | 1 | 0.13507 | 0 | 1
377 | 0.025541 | 0 | 0.88973 | 0 | 0 | 1 | 0.025541 | 0 | 1
378 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
379 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
380 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
381 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
382 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
383 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
384 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
385 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
386 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
387 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
388 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
389 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
390 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
391 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
392 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
393 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
394 | 0.10739 | 0 | 0.88973 | 0 | 0 | 1 | 0.10739 | 0 | 1
395 | 0.23824 | 0 | 0.88973 | 0 | 0 | 1 | 0.23824 | 0 | 1
396 | 0.28211 | 0 | 0.88973 | 0 | 0 | 1 | 0.28211 | 0 | 1
397 | 0.29786 | 0 | 0.88973 | 0 | 0 | 1 | 0.29786 | 0 | 1
398 | 0.28282 | 0 | 0.88973 | 0 | 0 | 1 | 0.28282 | 0 | 1
399 | 0.259 | 0 | 0.88973 | 0 | 0 | 1 | 0.259 | 0 | 1
400 | 0.15726 | 0 | 0.88973 | 0 | 0 | 1 | 0.15726 | 0 | 1
401 | 0.011217 | 0 | 0.88973 | 0 | 0 | 1 | 0.011217 | 0 | 1
402 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
403 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
404 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
405 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
406 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
407 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
408 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
409 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
410 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
411 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
412 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
413 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
414 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
415 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
416 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
417 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
418 | 0.1315 | 0 | 0.88973 | 0 | 0 | 1 | 0.1315 | 0 | 1
419 | 0.21494 | 0 | 0.88973 | 0 | 0 | 1 | 0.21494 | 0 | 1
420 | 0.22489 | 0 | 0.88973 | 0 | 0 | 1 | 0.22489 | 0 | 1
421 | 0.25148 | 0 | 0.88973 | 0 | 0 | 1 | 0.25148 | 0 | 1
422 | 0.23241 | 0 | 0.88973 | 0 | 0 | 1 | 0.23241 | 0 | 1
423 | 0.20344 | 0 | 0.88973 | 0 | 0 | 1 | 0.20344 | 0 | 1
424 | 0.14058 | 0 | 0.88973 | 0 | 0 | 1 | 0.14058 | 0 | 1
425 | 0.013209 | 0 | 0.88973 | 0 | 0 | 1 | 0.013209 | 0 | 1
426 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
427 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
428 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
429 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
430 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
431 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
432 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
433 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
434 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
435 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
436 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
437 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
438 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
439 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
440 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
441 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
442 | 0.095471 | 0 | 0.88973 | 0 | 0 | 1 | 0.095471 | 0 | 1
443 | 0.17526 | 0 | 0.88973 | 0 | 0 | 1 | 0.17526 | 0 | 1
444 | 0.19644 | 0 | 0.88973 | 0 | 0 | 1 | 0.19644 | 0 | 1
445 | 0.17847 | 0 | 0.88973 | 0 | 0 | 1 | 0.17847 | 0 | 1
446 | 0.13496 | 0 | 0.88973 | 0 | 0 | 1 | 0.13496 | 0 | 1
447 | 0.053963 | 0 | 0.88973 | 0 | 0 | 1 | 0.053963 | 0 | 1
448 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
449 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
450 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
451 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
452 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
453 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
454 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
455 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
456 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
457 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
458 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
459 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
460 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
461 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
462 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
463 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
464 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
465 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
466 | 0.063806 | 0 | 0.88973 | 0 | 0 | 1 | 0.063806 | 0 | 1
467 | 0.12452 | 0 | 0.88973 | 0 | 0 | 1 | 0.12452 | 0 | 1
468 | 0.15433 | 0 | 0.88973 | 0 | 0 | 1 | 0.15433 | 0 | 1
469 | 0.13373 | 0 | 0.88973 | 0 | 0 | 1 | 0.13373 | 0 | 1
470 | 0.083402 | 0 | 0.88973 | 0 | 0 | 1 | 0.083402 | 0 | 1
471 | 0.032305 | 0 | 0.88973 | 0 | 0 | 1 | 0.032305 | 0 | 1
472 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
473 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
474 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
475 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
476 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
477 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
478 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
479 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
480 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
481 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
482 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
483 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
484 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
485 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
486 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
487 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
488 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
489 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
490 | 0.044384 | 0 | 0.88973 | 0 | 0 | 1 | 0.044384 | 0 | 1
491 | 0.12147 | 0 | 0.88973 | 0 | 0 | 1 | 0.12147 | 0 | 1
492 | 0.17511 | 0 | 0.88973 | 0 | 0 | 1 | 0.17511 | 0 | 1
493 | 0.10569 | 0 | 0.88973 | 0 | 0 | 1 | 0.10569 | 0 | 1
494 | 0.035507 | 0 | 0.88973 | 0 | 0 | 1 | 0.035507 | 0 | 1
495 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
496 | 0 | 0.0069206 | 0.88973 | 0 | 0 | 1 | 0 | 0.0069206 | 1
497 | 0 | 0.019866 | 0.88973 | 0 | 0 | 1 | 0 | 0.019866 | 1
498 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
499 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
500 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
501 | 0 | 0.0044661 | 0.88973 | 0 | 1 | 1 | 0 | 0.0044661 | 1
502 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
503 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
504 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
505 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
506 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
507 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
508 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
509 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
510 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
511 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
512 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
513 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
514 | 0.081661 | 0 | 0.88973 | 0 | 0 | 1 | 0.081661 | 0 | 1
515 | 0.19029 | 0 | 0.88973 | 0 | 0 | 1 | 0.19029 | 0 | 1
516 | 0.21211 | 0.025821 | 0.88973 | 0 | 0 | 1 | 0.21211 | 0.025821 | 1
517 | 0.17249 | 0.034938 | 0.88973 | 0 | 0 | 1 | 0.17249 | 0.034938 | 1
518 | 0.1255 | 0.032434 | 0.88973 | 0 | 0 | 1 | 0.1255 | 0.032434 | 1
519 | 0.11476 | 0.027009 | 0.88973 | 0 | 0 | 1 | 0.11476 | 0.027009 | 1
520 | 0.062004 | 0.031839 | 0.88973 | 0 | 0 | 1 | 0.062004 | 0.031839 | 1
521 | 0 | 0.055309 | 0.88973 | 0 | 0 | 1 | 0 | 0.055309 | 1
522 | 0 | 0.022323 | 0.88973 | 0 | 1 | 1 | 0 | 0.022323 | 1
523 | 0 | 0.00027693 | 0.88973 | 0 | 1 | 1 | 0 | 0.00027693 | 1
524 | 0 | 0.0073817 | 0.88973 | 0 | 1 | 1 | 0 | 0.0073817 | 1
525 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
526 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
527 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
528 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
529 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
530 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
531 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
532 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
533 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
534 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
535 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
536 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
537 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
538 | 0.064634 | 0 | 0.88973 | 0 | 0 | 1 | 0.064634 | 0 | 1
539 | 0.12742 | 0 | 0.88973 | 0 | 0 | 1 | 0.12742 | 0 | 1
540 | 0.13846 | 0.015797 | 0.88973 | 0 | 0 | 1 | 0.13846 | 0.015797 | 1
541 | 0.14007 | 0.032341 | 0.88973 | 0 | 0 | 1 | 0.14007 | 0.032341 | 1
542 | 0.13587 | 0.0263 | 0.88973 | 0 | 0 | 1 | 0.13587 | 0.0263 | 1
543 | 0.10755 | 0.029157 | 0.88973 | 0 | 0 | 1 | 0.10755 | 0.029157 | 1
544 | 0.085207 | 0.016034 | 0.88973 | 0 | 0 | 1 | 0.085207 | 0.016034 | 1
545 | 0 | 0.032836 | 0.88973 | 0 | 0 | 1 | 0 | 0.032836 | 1
546 | 0 | 0.0046598 | 0.88973 | 0 | 1 | 1 | 0 | 0.0046598 | 1
547 | 0 | 0.002287 | 0.88973 | 0 | 1 | 1 | 0 | 0.002287 | 1
548 | 0 | 0.00763 | 0.88973 | 0 | 1 | 1 | 0 | 0.00763 | 1
549 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
550 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
551 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
552 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
553 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
554 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
555 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
556 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
557 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
558 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
559 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
560 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
561 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
562 | 0.05915 | 0 | 0.88973 | 0 | 0 | 1 | 0.05915 | 0 | 1
563 | 0.13684 | 0 | 0.88973 | 0 | 0 | 1 | 0.13684 | 0 | 1
564 | 0.14326 | 0.0012029 | 0.88973 | 0 | 0 | 1 | 0.14326 | 0.0012029 | 1
565 | 0.17073 | 0.012804 | 0.88973 | 0 | 0 | 1 | 0.17073 | 0.012804 | 1
566 | 0.19847 | 0 | 0.88973 | 0 | 0 | 1 | 0.19847 | 0 | 1
567 | 0.18154 | 0 | 0.88973 | 0 | 0 | 1 | 0.18154 | 0 | 1
568 | 0.12704 | 0 | 0.88973 | 0 | 0 | 1 | 0.12704 | 0 | 1
569 | 0.00048291 | 0 | 0.88973 | 0 | 0 | 1 | 0.00048291 | 0 | 1
570 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
571 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
572 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
573 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
574 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
575 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
576 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
577 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
578 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
579 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
580 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
581 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
582 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
583 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
584 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
585 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
586 | 0.078446 | 0 | 0.88973 | 0 | 0 | 1 | 0.078446 | 0 | 1
587 | 0.14087 | 0 | 0.88973 | 0 | 0 | 1 | 0.14087 | 0 | 1
588 | 0.15788 | 0 | 0.88973 | 0 | 0 | 1 | 0.15788 | 0 | 1
589 | 0.16804 | 0.0044192 | 0.88973 | 0 | 0 | 1 | 0.16804 | 0.0044192 | 1
590 | 0.19876 | 0 | 0.88973 | 0 | 0 | 1 | 0.19876 | 0 | 1
591 | 0.19043 | 0 | 0.88973 | 0 | 0 | 1 | 0.19043 | 0 | 1
592 | 0.14375 | 0 | 0.88973 | 0 | 0 | 1 | 0.14375 | 0 | 1
593 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
594 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
595 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
596 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
597 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
598 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
599 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
600 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
601 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
602 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
603 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
604 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
605 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
606 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
607 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
608 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
609 | 0.012196 | 0 | 0.88973 | 0 | 0 | 1 | 0.012196 | 0 | 1
610 | 0.13788 | 0 | 0.88973 | 0 | 0 | 1 | 0.13788 | 0 | 1
611 | 0.27884 | 0 | 0.88973 | 0 | 0 | 1 | 0.27884 | 0 | 1
612 | 0.26607 | 0 | 0.88973 | 0 | 0 | 1 | 0.26607 | 0 | 1
613 | 0.22299 | 0 | 0.88973 | 0 | 0 | 1 | 0.22299 | 0 | 1
614 | 0.2113 | 0 | 0.88973 | 0 | 0 | 1 | 0.2113 | 0 | 1
615 | 0.13887 | 0 | 0.88973 | 0 | 0 | 1 | 0.13887 | 0 | 1
616 | 0.038572 | 0 | 0.88973 | 0 | 0 | 1 | 0.038572 | 0 | 1
617 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
618 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
619 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
620 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
621 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
622 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
623 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
624 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
625 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
626 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
627 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
628 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
629 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
630 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
631 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
632 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
633 | 0.012141 | 0 | 0.88973 | 0 | 0 | 1 | 0.012141 | 0 | 1
634 | 0.15 | 0 | 0.88973 | 0 | 0 | 1 | 0.15 | 0 | 1
635 | 0.29229 | 0 | 0.88973 | 0 | 0 | 1 | 0.29229 | 0 | 1
636 | 0.23295 | 0 | 0.88973 | 0 | 0 | 1 | 0.23295 | 0 | 1
637 | 0.20487 | 0 | 0.88973 | 0 | 0 | 1 | 0.20487 | 0 | 1
638 | 0.21353 | 0 | 0.88973 | 0 | 0 | 1 | 0.21353 | 0 | 1
639 | 0.14058 | 0 | 0.88973 | 0 | 0 | 1 | 0.14058 | 0 | 1
640 | 0.045723 | 0 | 0.88973 | 0 | 0 | 1 | 0.045723 | 0 | 1
641 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
642 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
643 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
644 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
645 | 0 | 0 | 0.88973 | 0 | 1 | 1 | 0 | 0 | 1
646 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
647 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
648 | 0 | 0 | 0.88973 | 0 | 0 | 1 | 0 | 0 | 1
649 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
650 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
651 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
652 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
653 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
654 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
655 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
656 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
657 | 0.0017274 | 0 | 0.868 | 0 | 0 | 1 | 0.0017274 | 0 | 1
658 | 0.11223 | 0 | 0.868 | 0 | 0 | 1 | 0.11223 | 0 | 1
659 | 0.26411 | 0 | 0.868 | 0 | 0 | 1 | 0.26411 | 0 | 1
660 | 0.25948 | 0 | 0.868 | 0 | 0 | 1 | 0.25948 | 0 | 1
661 | 0.21068 | 0 | 0.868 | 0 | 0 | 1 | 0.21068 | 0 | 1
662 | 0.26143 | 0 | 0.868 | 0 | 0 | 1 | 0.26143 | 0 | 1
663 | 0.14688 | 0 | 0.868 | 0 | 0 | 1 | 0.14688 | 0 | 1
664 | 0.065661 | 0 | 0.868 | 0 | 0 | 1 | 0.065661 | 0 | 1
665 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
666 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
667 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
668 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
669 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
670 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
671 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
672 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
673 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
674 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
675 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
676 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
677 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
678 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
679 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
680 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
681 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
682 | 0.13221 | 0 | 0.8105 | 0 | 0 | 1 | 0.13221 | 0 | 1
683 | 0.26528 | 0 | 0.8105 | 0 | 0 | 1 | 0.26528 | 0 | 1
684 | 0.27604 | 0 | 0.8105 | 0 | 0 | 1 | 0.27604 | 0 | 1
685 | 0.25366 | 0 | 0.8105 | 0 | 0 | 1 | 0.25366 | 0 | 1
686 | 0.33727 | 0 | 0.8105 | 0 | 0 | 1 | 0.33727 | 0 | 1
687 | 0.31186 | 0 | 0.8105 | 0 | 0 | 1 | 0.31186 | 0 | 1
688 | 0.20493 | 0 | 0.8105 | 0 | 0 | 1 | 0.20493 | 0 | 1
689 | 0.02576 | 0 | 0.8105 | 0 | 0 | 1 | 0.02576 | 0 | 1
690 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
691 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
692 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
693 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
694 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
695 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
696 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
697 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
698 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
699 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
700 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
701 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
702 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
703 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
704 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
705 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
706 | 0.062412 | 0 | 0.8105 | 0 | 0 | 1 | 0.062412 | 0 | 1
707 | 0.1558 | 0 | 0.8105 | 0 | 0 | 1 | 0.1558 | 0 | 1
708 | 0.20828 | 0 | 0.8105 | 0 | 0 | 1 | 0.20828 | 0 | 1
709 | 0.20617 | 0 | 0.8105 | 0 | 0 | 1 | 0.20617 | 0 | 1
710 | 0.26604 | 0 | 0.8105 | 0 | 0 | 1 | 0.26604 | 0 | 1
711 | 0.21365 | 0 | 0.8105 | 0 | 0 | 1 | 0.21365 | 0 | 1
712 | 0.13442 | 0 | 0.8105 | 0 | 0 | 1 | 0.13442 | 0 | 1
713 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
714 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
715 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
716 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
717 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
718 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
719 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
720 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
721 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
722 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
723 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
724 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
725 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
726 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
727 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
728 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
729 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
730 | 0.017501 | 0 | 0.8105 | 0 | 0 | 1 | 0.017501 | 0 | 1
731 | 0.074813 | 0 | 0.8105 | 0 | 0 | 1 | 0.074813 | 0 | 1
732 | 0.085193 | 0 | 0.8105 | 0 | 0 | 1 | 0.085193 | 0 | 1
733 | 0.14537 | 0 | 0.8105 | 0 | 0 | 1 | 0.14537 | 0 | 1
734 | 0.15489 | 0 | 0.8105 | 0 | 0 | 1 | 0.15489 | 0 | 1
735 | 0.17068 | 0 | 0.8105 | 0 | 0 | 1 | 0.17068 | 0 | 1
736 | 0.091608 | 0 | 0.8105 | 0 | 0 | 1 | 0.091608 | 0 | 1
737 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
738 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
739 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
740 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
741 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
742 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
743 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
744 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
745 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
746 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
747 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
748 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
749 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
750 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
751 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
752 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
753 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
754 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
755 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
756 | 0.078589 | 0 | 0.8105 | 0 | 0 | 1 | 0.078589 | 0 | 1
757 | 0.14917 | 0.0016221 | 0.8105 | 0 | 0 | 1 | 0.14917 | 0.0016221 | 1
758 | 0.14283 | 0 | 0.8105 | 0 | 0 | 1 | 0.14283 | 0 | 1
759 | 0.11356 | 0.0052107 | 0.8105 | 0 | 0 | 1 | 0.11356 | 0.0052107 | 1
760 | 0.044074 | 0 | 0.8105 | 0 | 0 | 1 | 0.044074 | 0 | 1
761 | 0 | 0.0063261 | 0.8105 | 0 | 0 | 1 | 0 | 0.0063261 | 1
762 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
763 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
764 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
765 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
766 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
767 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
768 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
769 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
770 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
771 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
772 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
773 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
774 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
775 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
776 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
777 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
778 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
779 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
780 | 0.056387 | 0 | 0.8105 | 0 | 0 | 1 | 0.056387 | 0 | 1
781 | 0.144 | 0 | 0.8105 | 0 | 0 | 1 | 0.144 | 0 | 1
782 | 0.11043 | 0 | 0.8105 | 0 | 0 | 1 | 0.11043 | 0 | 1
783 | 0.035619 | 0 | 0.8105 | 0 | 0 | 1 | 0.035619 | 0 | 1
784 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
785 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
786 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
787 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
788 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
789 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
790 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
791 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
792 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
793 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
794 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
795 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
796 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
797 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
798 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
799 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
800 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
801 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
802 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
803 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
804 | 0.0051918 | 0 | 0.8105 | 0 | 0 | 1 | 0.0051918 | 0 | 1
805 | 0.071815 | 0 | 0.8105 | 0 | 0 | 1 | 0.071815 | 0 | 1
806 | 0.079504 | 0 | 0.8105 | 0 | 0 | 1 | 0.079504 | 0 | 1
807 | 0.034577 | 0 | 0.8105 | 0 | 0 | 1 | 0.034577 | 0 | 1
808 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
809 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
810 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
811 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
812 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
813 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
814 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
815 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
816 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
817 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
818 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
819 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
820 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
821 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
822 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
823 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
824 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
825 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
826 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
827 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
828 | 0.036932 | 0 | 0.8105 | 0 | 0 | 1 | 0.036932 | 0 | 1
829 | 0.071033 | 0 | 0.8105 | 0 | 0 | 1 | 0.071033 | 0 | 1
830 | 0.081531 | 0 | 0.8105 | 0 | 0 | 1 | 0.081531 | 0 | 1
831 | 0.06601 | 0 | 0.8105 | 0 | 0 | 1 | 0.06601 | 0 | 1
832 | 0.0099219 | 0 | 0.8105 | 0 | 0 | 1 | 0.0099219 | 0 | 1
833 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
834 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
835 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
836 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
837 | 0 | 0 | 0.8105 | 0 | 1 | 1 | 0 | 0 | 1
838 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
839 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
840 | 0 | 0 | 0.8105 | 0 | 0 | 1 | 0 | 0 | 1
841 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
842 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
843 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
844 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
845 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
846 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
847 | 0 | 0.0016674 | 0.868 | 0 | 0 | 1 | 0 | 0.0016674 | 1
848 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
849 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
850 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
851 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
852 | 0.0077774 | 0 | 0.868 | 0 | 0 | 1 | 0.0077774 | 0 | 1
853 | 0.062741 | 0 | 0.868 | 0 | 0 | 1 | 0.062741 | 0 | 1
854 | 0.10194 | 0 | 0.868 | 0 | 0 | 1 | 0.10194 | 0 | 1
855 | 0.17939 | 0 | 0.868 | 0 | 0 | 1 | 0.17939 | 0 | 1
856 | 0.09374 | 0 | 0.868 | 0 | 0 | 1 | 0.09374 | 0 | 1
857 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
858 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
859 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
860 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
861 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
862 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
863 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
864 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
865 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
866 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
867 | 0 | 0.0047903 | 0.868 | 0 | 0 | 1 | 0 | 0.0047903 | 1
868 | 0 | 0.026509 | 0.868 | 0 | 0 | 1 | 0 | 0.026509 | 1
869 | 0 | 0.021554 | 0.868 | 0 | 0 | 1 | 0 | 0.021554 | 1
870 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
871 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
872 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
873 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
874 | 0.044235 | 0 | 0.868 | 0 | 0 | 1 | 0.044235 | 0 | 1
875 | 0.072055 | 0 | 0.868 | 0 | 0 | 1 | 0.072055 | 0 | 1
876 | 0.12645 | 0 | 0.868 | 0 | 0 | 1 | 0.12645 | 0 | 1
877 | 0.13948 | 0 | 0.868 | 0 | 0 | 1 | 0.13948 | 0 | 1
878 | 0.18814 | 0.0097006 | 0.868 | 0 | 0 | 1 | 0.18814 | 0.0097006 | 1
879 | 0.20254 | 0 | 0.868 | 0 | 0 | 1 | 0.20254 | 0 | 1
880 | 0.11479 | 0 | 0.868 | 0 | 0 | 1 | 0.11479 | 0 | 1
881 | 0.0068435 | 0 | 0.868 | 0 | 0 | 1 | 0.0068435 | 0 | 1
882 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
883 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
884 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
885 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
886 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
887 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
888 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
889 | 0 | 0.008741 | 0.868 | 0 | 0 | 1 | 0 | 0.008741 | 1
890 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
891 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
892 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
893 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
894 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
895 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
896 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
897 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
898 | 0.060966 | 0 | 0.868 | 0 | 0 | 1 | 0.060966 | 0 | 1
899 | 0.055517 | 0 | 0.868 | 0 | 0 | 1 | 0.055517 | 0 | 1
900 | 0.08151 | 0 | 0.868 | 0 | 0 | 1 | 0.08151 | 0 | 1
901 | 0.13808 | 0 | 0.868 | 0 | 0 | 1 | 0.13808 | 0 | 1
902 | 0.20264 | 0 | 0.868 | 0 | 0 | 1 | 0.20264 | 0 | 1
903 | 0.23045 | 0.0033461 | 0.868 | 0 | 0 | 1 | 0.23045 | 0.0033461 | 1
904 | 0.079495 | 0 | 0.868 | 0 | 0 | 1 | 0.079495 | 0 | 1
905 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
906 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
907 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
908 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
909 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
910 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
911 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
912 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
913 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
914 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
915 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
916 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
917 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
918 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
919 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
920 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
921 | 0.053378 | 0 | 0.868 | 0 | 0 | 1 | 0.053378 | 0 | 1
922 | 0.25094 | 0 | 0.868 | 0 | 0 | 1 | 0.25094 | 0 | 1
923 | 0.27171 | 0 | 0.868 | 0 | 0 | 1 | 0.27171 | 0 | 1
924 | 0.32235 | 0 | 0.868 | 0 | 0 | 1 | 0.32235 | 0 | 1
925 | 0.32141 | 0 | 0.868 | 0 | 0 | 1 | 0.32141 | 0 | 1
926 | 0.39278 | 0 | 0.868 | 0 | 0 | 1 | 0.39278 | 0 | 1
927 | 0.32495 | 0 | 0.868 | 0 | 0 | 1 | 0.32495 | 0 | 1
928 | 0.14381 | 0 | 0.868 | 0 | 0 | 1 | 0.14381 | 0 | 1
929 | 0.027046 | 0 | 0.868 | 0 | 0 | 1 | 0.027046 | 0 | 1
930 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
931 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
932 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
933 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
934 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
935 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
936 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
937 | 0 | 0.00011989 | 0.868 | 0 | 0 | 1 | 0 | 0.00011989 | 1
938 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
939 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
940 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
941 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
942 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
943 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
944 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
945 | 0.025504 | 0 | 0.868 | 0 | 0 | 1 | 0.025504 | 0 | 1
946 | 0.21815 | 0 | 0.868 | 0 | 0 | 1 | 0.21815 | 0 | 1
947 | 0.33324 | 0 | 0.868 | 0 | 0 | 1 | 0.33324 | 0 | 1
948 | 0.41714 | 0 | 0.868 | 0 | 0 | 1 | 0.41714 | 0 | 1
949 | 0.38884 | 0 | 0.868 | 0 | 0 | 1 | 0.38884 | 0 | 1
950 | 0.442 | 0 | 0.868 | 0 | 0 | 1 | 0.442 | 0 | 1
951 | 0.36286 | 0 | 0.868 | 0 | 0 | 1 | 0.36286 | 0 | 1
952 | 0.14824 | 0 | 0.868 | 0 | 0 | 1 | 0.14824 | 0 | 1
953 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
954 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
955 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
956 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
957 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
958 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
959 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
960 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
961 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
962 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
963 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
964 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
965 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
966 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
967 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
968 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
969 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
970 | 0.086615 | 0 | 0.868 | 0 | 0 | 1 | 0.086615 | 0 | 1
971 | 0.1683 | 0 | 0.868 | 0 | 0 | 1 | 0.1683 | 0 | 1
972 | 0.25642 | 0 | 0.868 | 0 | 0 | 1 | 0.25642 | 0 | 1
973 | 0.20168 | 0 | 0.868 | 0 | 0 | 1 | 0.20168 | 0 | 1
974 | 0.24899 | 0 | 0.868 | 0 | 0 | 1 | 0.24899 | 0 | 1
975 | 0.24694 | 0 | 0.868 | 0 | 0 | 1 | 0.24694 | 0 | 1
976 | 0.12258 | 0 | 0.868 | 0 | 0 | 1 | 0.12258 | 0 | 1
977 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
978 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
979 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
980 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
981 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
982 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
983 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
984 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
985 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
986 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
987 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
988 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
989 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
990 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
991 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
992 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
993 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
994 | 0.054948 | 0 | 0.868 | 0 | 0 | 1 | 0.054948 | 0 | 1
995 | 0.14654 | 0 | 0.868 | 0 | 0 | 1 | 0.14654 | 0 | 1
996 | 0.23439 | 0 | 0.868 | 0 | 0 | 1 | 0.23439 | 0 | 1
997 | 0.17365 | 0 | 0.868 | 0 | 0 | 1 | 0.17365 | 0 | 1
998 | 0.25802 | 0 | 0.868 | 0 | 0 | 1 | 0.25802 | 0 | 1
999 | 0.23629 | 0 | 0.868 | 0 | 0 | 1 | 0.23629 | 0 | 1
1000 | 0.13794 | 0 | 0.868 | 0 | 0 | 1 | 0.13794 | 0 | 1
1001 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
1002 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
1003 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
1004 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
1005 | 0 | 0 | 0.868 | 0 | 1 | 1 | 0 | 0 | 1
1006 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
1007 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
1008 | 0 | 0 | 0.868 | 0 | 0 | 1 | 0 | 0 | 1
1009 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1010 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1011 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1012 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1013 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1014 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1015 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1016 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1017 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1018 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1019 | 0.054924 | 0 | 0.81171 | 0 | 0 | 1 | 0.054924 | 0 | 1
1020 | 0.13307 | 0 | 0.81171 | 0 | 0 | 1 | 0.13307 | 0 | 1
1021 | 0.13922 | 0 | 0.81171 | 0 | 0 | 1 | 0.13922 | 0 | 1
1022 | 0.19411 | 0 | 0.81171 | 0 | 0 | 1 | 0.19411 | 0 | 1
1023 | 0.16829 | 0 | 0.81171 | 0 | 0 | 1 | 0.16829 | 0 | 1
1024 | 0.11506 | 0 | 0.81171 | 0 | 0 | 1 | 0.11506 | 0 | 1
1025 | 0.014925 | 0 | 0.81171 | 0 | 0 | 1 | 0.014925 | 0 | 1
1026 | 0 | 0 | 0.81171 | 0 | 1 | 1 | 0 | 0 | 1
1027 | 0 | 0 | 0.81171 | 0 | 1 | 1 | 0 | 0 | 1
1028 | 0 | 0 | 0.81171 | 0 | 1 | 1 | 0 | 0 | 1
1029 | 0 | 0 | 0.81171 | 0 | 1 | 1 | 0 | 0 | 1
1030 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1031 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1032 | 0 | 0 | 0.81171 | 0 | 0 | 1 | 0 | 0 | 1
1033 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1034 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1035 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1036 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1037 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1038 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1039 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1040 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1041 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1042 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1043 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1044 | 0.058781 | 0 | 0.83344 | 0 | 0 | 1 | 0.058781 | 0 | 1
1045 | 0.11934 | 0 | 0.83344 | 0 | 0 | 1 | 0.11934 | 0 | 1
1046 | 0.17221 | 0 | 0.83344 | 0 | 0 | 1 | 0.17221 | 0 | 1
1047 | 0.11605 | 0 | 0.83344 | 0 | 0 | 1 | 0.11605 | 0 | 1
1048 | 0.029838 | 0 | 0.83344 | 0 | 0 | 1 | 0.029838 | 0 | 1
1049 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1050 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1051 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1052 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1053 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1054 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1055 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1056 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1057 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1058 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1059 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1060 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1061 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1062 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1063 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1064 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1065 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1066 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1067 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1068 | 0.044884 | 0 | 0.83344 | 0 | 0 | 1 | 0.044884 | 0 | 1
1069 | 0.1203 | 0.0082177 | 0.83344 | 0 | 0 | 1 | 0.1203 | 0.0082177 | 1
1070 | 0.1646 | 0.022904 | 0.83344 | 0 | 0 | 1 | 0.1646 | 0.022904 | 1
1071 | 0.13464 | 0.016335 | 0.83344 | 0 | 0 | 1 | 0.13464 | 0.016335 | 1
1072 | 0.021029 | 0.03067 | 0.83344 | 0 | 0 | 1 | 0.021029 | 0.03067 | 1
1073 | 0 | 0.028722 | 0.83344 | 0 | 0 | 1 | 0 | 0.028722 | 1
1074 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1075 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1076 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1077 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1078 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1079 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1080 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1081 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1082 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1083 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1084 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1085 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1086 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1087 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1088 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1089 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1090 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1091 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1092 | 0.031021 | 0 | 0.83344 | 0 | 0 | 1 | 0.031021 | 0 | 1
1093 | 0.065681 | 0 | 0.83344 | 0 | 0 | 1 | 0.065681 | 0 | 1
1094 | 0.098594 | 0.0063768 | 0.83344 | 0 | 0 | 1 | 0.098594 | 0.0063768 | 1
1095 | 0.10962 | 0.0016874 | 0.83344 | 0 | 0 | 1 | 0.10962 | 0.0016874 | 1
1096 | 0 | 0.014161 | 0.83344 | 0 | 0 | 1 | 0 | 0.014161 | 1
1097 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1098 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1099 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1100 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1101 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1102 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1103 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1104 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1105 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1106 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1107 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1108 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1109 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1110 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1111 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1112 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1113 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1114 | 0.035427 | 0 | 0.83344 | 0 | 0 | 1 | 0.035427 | 0 | 1
1115 | 0.17128 | 0 | 0.83344 | 0 | 0 | 1 | 0.17128 | 0 | 1
1116 | 0.24291 | 0 | 0.83344 | 0 | 0 | 1 | 0.24291 | 0 | 1
1117 | 0.21977 | 0 | 0.83344 | 0 | 0 | 1 | 0.21977 | 0 | 1
1118 | 0.17628 | 0 | 0.83344 | 0 | 0 | 1 | 0.17628 | 0 | 1
1119 | 0.20353 | 0 | 0.83344 | 0 | 0 | 1 | 0.20353 | 0 | 1
1120 | 0.042525 | 0 | 0.83344 | 0 | 0 | 1 | 0.042525 | 0 | 1
1121 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1122 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1123 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1124 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1125 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1126 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1127 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1128 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1129 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1130 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1131 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1132 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1133 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1134 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1135 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1136 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1137 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1138 | 0.049035 | 0 | 0.83344 | 0 | 0 | 1 | 0.049035 | 0 | 1
1139 | 0.14496 | 0 | 0.83344 | 0 | 0 | 1 | 0.14496 | 0 | 1
1140 | 0.14198 | 0 | 0.83344 | 0 | 0 | 1 | 0.14198 | 0 | 1
1141 | 0.071101 | 0 | 0.83344 | 0 | 0 | 1 | 0.071101 | 0 | 1
1142 | 0.046179 | 0 | 0.83344 | 0 | 0 | 1 | 0.046179 | 0 | 1
1143 | 0.026473 | 0 | 0.83344 | 0 | 0 | 1 | 0.026473 | 0 | 1
1144 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1145 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1146 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1147 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1148 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1149 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1150 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1151 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1152 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1153 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1154 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1155 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1156 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1157 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1158 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1159 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1160 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1161 | 0.00054113 | 0 | 0.83344 | 0 | 0 | 1 | 0.00054113 | 0 | 1
1162 | 0.10264 | 0 | 0.83344 | 0 | 0 | 1 | 0.10264 | 0 | 1
1163 | 0.22482 | 0 | 0.83344 | 0 | 0 | 1 | 0.22482 | 0 | 1
1164 | 0.21035 | 0 | 0.83344 | 0 | 0 | 1 | 0.21035 | 0 | 1
1165 | 0.16177 | 0 | 0.83344 | 0 | 0 | 1 | 0.16177 | 0 | 1
1166 | 0.12734 | 0 | 0.83344 | 0 | 0 | 1 | 0.12734 | 0 | 1
1167 | 0.070825 | 0 | 0.83344 | 0 | 0 | 1 | 0.070825 | 0 | 1
1168 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1169 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1170 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1171 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1172 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1173 | 0 | 0 | 0.83344 | 0 | 1 | 1 | 0 | 0 | 1
1174 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1175 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1176 | 0 | 0 | 0.83344 | 0 | 0 | 1 | 0 | 0 | 1
1177 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1178 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1179 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1180 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1181 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1182 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1183 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1184 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1185 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1186 | 0.076425 | 0 | 0.90883 | 0 | 0 | 1 | 0.076425 | 0 | 1
1187 | 0.19847 | 0 | 0.90883 | 0 | 0 | 1 | 0.19847 | 0 | 1
1188 | 0.12398 | 0 | 0.90883 | 0 | 0 | 1 | 0.12398 | 0 | 1
1189 | 0.10929 | 0 | 0.90883 | 0 | 0 | 1 | 0.10929 | 0 | 1
1190 | 0.13041 | 0 | 0.90883 | 0 | 0 | 1 | 0.13041 | 0 | 1
1191 | 0.038264 | 0 | 0.90883 | 0 | 0 | 1 | 0.038264 | 0 | 1
1192 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1193 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1194 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1195 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1196 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1197 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1198 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1199 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1200 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1201 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1202 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1203 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1204 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1205 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1206 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1207 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1208 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1209 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1210 | 0.04395 | 0 | 0.90883 | 0 | 0 | 1 | 0.04395 | 0 | 1
1211 | 0.19887 | 0 | 0.90883 | 0 | 0 | 1 | 0.19887 | 0 | 1
1212 | 0.21247 | 0 | 0.90883 | 0 | 0 | 1 | 0.21247 | 0 | 1
1213 | 0.30889 | 0 | 0.90883 | 0 | 0 | 1 | 0.30889 | 0 | 1
1214 | 0.27977 | 0 | 0.90883 | 0 | 0 | 1 | 0.27977 | 0 | 1
1215 | 0.18736 | 0 | 0.90883 | 0 | 0 | 1 | 0.18736 | 0 | 1
1216 | 0.11993 | 0 | 0.90883 | 0 | 0 | 1 | 0.11993 | 0 | 1
1217 | 0.036787 | 0 | 0.90883 | 0 | 0 | 1 | 0.036787 | 0 | 1
1218 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1219 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1220 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1221 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1222 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1223 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1224 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1225 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1226 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1227 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1228 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1229 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1230 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1231 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1232 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1233 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1234 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1235 | 0.047487 | 0 | 0.90883 | 0 | 0 | 1 | 0.047487 | 0 | 1
1236 | 0.083841 | 0 | 0.90883 | 0 | 0 | 1 | 0.083841 | 0 | 1
1237 | 0.14691 | 0 | 0.90883 | 0 | 0 | 1 | 0.14691 | 0 | 1
1238 | 0.14389 | 0 | 0.90883 | 0 | 0 | 1 | 0.14389 | 0 | 1
1239 | 0.097803 | 0 | 0.90883 | 0 | 0 | 1 | 0.097803 | 0 | 1
1240 | 0.024688 | 0 | 0.90883 | 0 | 0 | 1 | 0.024688 | 0 | 1
1241 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1242 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1243 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1244 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1245 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1246 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1247 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1248 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1249 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1250 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1251 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1252 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1253 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1254 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1255 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1256 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1257 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1258 | 0.012557 | 0 | 0.90883 | 0 | 0 | 1 | 0.012557 | 0 | 1
1259 | 0.14024 | 0 | 0.90883 | 0 | 0 | 1 | 0.14024 | 0 | 1
1260 | 0.21039 | 0 | 0.90883 | 0 | 0 | 1 | 0.21039 | 0 | 1
1261 | 0.25761 | 0 | 0.90883 | 0 | 0 | 1 | 0.25761 | 0 | 1
1262 | 0.21706 | 0 | 0.90883 | 0 | 0 | 1 | 0.21706 | 0 | 1
1263 | 0.18915 | 0 | 0.90883 | 0 | 0 | 1 | 0.18915 | 0 | 1
1264 | 0.073131 | 0 | 0.90883 | 0 | 0 | 1 | 0.073131 | 0 | 1
1265 | 0.028112 | 0 | 0.90883 | 0 | 0 | 1 | 0.028112 | 0 | 1
1266 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1267 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1268 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1269 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1270 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1271 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1272 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1273 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1274 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1275 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1276 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1277 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1278 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1279 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1280 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1281 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1282 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1283 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1284 | 0.088283 | 0 | 0.90883 | 0 | 0 | 1 | 0.088283 | 0 | 1
1285 | 0.14221 | 0 | 0.90883 | 0 | 0 | 1 | 0.14221 | 0 | 1
1286 | 0.14492 | 0 | 0.90883 | 0 | 0 | 1 | 0.14492 | 0 | 1
1287 | 0.14513 | 0 | 0.90883 | 0 | 0 | 1 | 0.14513 | 0 | 1
1288 | 0.054468 | 0 | 0.90883 | 0 | 0 | 1 | 0.054468 | 0 | 1
1289 | 0.017555 | 0 | 0.90883 | 0 | 0 | 1 | 0.017555 | 0 | 1
1290 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1291 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1292 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1293 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1294 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1295 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1296 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1297 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1298 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1299 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1300 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1301 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1302 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1303 | 0 | 0.0097667 | 0.90883 | 0 | 0 | 1 | 0 | 0.0097667 | 1
1304 | 0 | 0.006488 | 0.90883 | 0 | 0 | 1 | 0 | 0.006488 | 1
1305 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1306 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1307 | 0.037396 | 0 | 0.90883 | 0 | 0 | 1 | 0.037396 | 0 | 1
1308 | 0.19908 | 0 | 0.90883 | 0 | 0 | 1 | 0.19908 | 0 | 1
1309 | 0.2439 | 0.0011222 | 0.90883 | 0 | 0 | 1 | 0.2439 | 0.0011222 | 1
1310 | 0.22452 | 0.015044 | 0.90883 | 0 | 0 | 1 | 0.22452 | 0.015044 | 1
1311 | 0.13575 | 0.022729 | 0.90883 | 0 | 0 | 1 | 0.13575 | 0.022729 | 1
1312 | 0.078984 | 0.01138 | 0.90883 | 0 | 0 | 1 | 0.078984 | 0.01138 | 1
1313 | 0.0063416 | 0.0050802 | 0.90883 | 0 | 0 | 1 | 0.0063416 | 0.0050802 | 1
1314 | 0 | 0.0030974 | 0.90883 | 0 | 1 | 1 | 0 | 0.0030974 | 1
1315 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1316 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1317 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1318 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1319 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1320 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1321 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1322 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1323 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1324 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1325 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1326 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1327 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1328 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1329 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1330 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1331 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1332 | 0.17347 | 0 | 0.90883 | 0 | 0 | 1 | 0.17347 | 0 | 1
1333 | 0.22466 | 0.0005531 | 0.90883 | 0 | 0 | 1 | 0.22466 | 0.0005531 | 1
1334 | 0.17955 | 0.012776 | 0.90883 | 0 | 0 | 1 | 0.17955 | 0.012776 | 1
1335 | 0.079429 | 0.027194 | 0.90883 | 0 | 0 | 1 | 0.079429 | 0.027194 | 1
1336 | 0.0090796 | 0.0075713 | 0.90883 | 0 | 0 | 1 | 0.0090796 | 0.0075713 | 1
1337 | 0 | 0.00094724 | 0.90883 | 0 | 0 | 1 | 0 | 0.00094724 | 1
1338 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1339 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1340 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1341 | 0 | 0 | 0.90883 | 0 | 1 | 1 | 0 | 0 | 1
1342 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1343 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1344 | 0 | 0 | 0.90883 | 0 | 0 | 1 | 0 | 0 | 1
1345 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1346 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1347 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1348 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1349 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1350 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1351 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1352 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1353 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1354 | 0.013776 | 0 | 0.85369 | 0 | 0 | 1 | 0.013776 | 0 | 1
1355 | 0.1129 | 0 | 0.85369 | 0 | 0 | 1 | 0.1129 | 0 | 1
1356 | 0.27021 | 0.0013039 | 0.85369 | 0 | 0 | 1 | 0.27021 | 0.0013039 | 1
1357 | 0.27102 | 0 | 0.85369 | 0 | 0 | 1 | 0.27102 | 0 | 1
1358 | 0.16354 | 0.0014241 | 0.85369 | 0 | 0 | 1 | 0.16354 | 0.0014241 | 1
1359 | 0.063146 | 0.015427 | 0.85369 | 0 | 0 | 1 | 0.063146 | 0.015427 | 1
1360 | 0 | 0.011488 | 0.85369 | 0 | 0 | 1 | 0 | 0.011488 | 1
1361 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1362 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1363 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1364 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1365 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1366 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1367 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1368 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1369 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1370 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1371 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1372 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1373 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1374 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1375 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1376 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1377 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1378 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1379 | 0.024885 | 0 | 0.85369 | 0 | 0 | 1 | 0.024885 | 0 | 1
1380 | 0.10525 | 0 | 0.85369 | 0 | 0 | 1 | 0.10525 | 0 | 1
1381 | 0.10443 | 0 | 0.85369 | 0 | 0 | 1 | 0.10443 | 0 | 1
1382 | 0.042691 | 0 | 0.85369 | 0 | 0 | 1 | 0.042691 | 0 | 1
1383 | 0.015383 | 0.0047952 | 0.85369 | 0 | 0 | 1 | 0.015383 | 0.0047952 | 1
1384 | 0 | 0.0018526 | 0.85369 | 0 | 0 | 1 | 0 | 0.0018526 | 1
1385 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1386 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1387 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1388 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1389 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1390 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1391 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1392 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1393 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1394 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1395 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1396 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1397 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1398 | 0 | 0.01147 | 0.85369 | 0 | 0 | 1 | 0 | 0.01147 | 1
1399 | 0 | 0.043405 | 0.85369 | 0 | 0 | 1 | 0 | 0.043405 | 1
1400 | 0 | 0.034076 | 0.85369 | 0 | 0 | 1 | 0 | 0.034076 | 1
1401 | 0 | 0.01292 | 0.85369 | 0 | 0 | 1 | 0 | 0.01292 | 1
1402 | 0 | 0.033363 | 0.85369 | 0 | 0 | 1 | 0 | 0.033363 | 1
1403 | 0 | 0.033667 | 0.85369 | 0 | 0 | 1 | 0 | 0.033667 | 1
1404 | 0 | 0.043044 | 0.85369 | 0 | 0 | 1 | 0 | 0.043044 | 1
1405 | 0 | 0.045433 | 0.85369 | 0 | 0 | 1 | 0 | 0.045433 | 1
1406 | 0 | 0.044784 | 0.85369 | 0 | 0 | 1 | 0 | 0.044784 | 1
1407 | 0 | 0.040306 | 0.85369 | 0 | 0 | 1 | 0 | 0.040306 | 1
1408 | 0 | 0.027742 | 0.85369 | 0 | 0 | 1 | 0 | 0.027742 | 1
1409 | 0 | 0.012816 | 0.85369 | 0 | 0 | 1 | 0 | 0.012816 | 1
1410 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1411 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1412 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1413 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1414 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1415 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1416 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1417 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1418 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1419 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1420 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1421 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1422 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1423 | 0 | 0.022127 | 0.85369 | 0 | 0 | 1 | 0 | 0.022127 | 1
1424 | 0 | 0.032467 | 0.85369 | 0 | 0 | 1 | 0 | 0.032467 | 1
1425 | 0 | 0.019043 | 0.85369 | 0 | 0 | 1 | 0 | 0.019043 | 1
1426 | 0 | 0.014721 | 0.85369 | 0 | 0 | 1 | 0 | 0.014721 | 1
1427 | 0 | 0.01029 | 0.85369 | 0 | 0 | 1 | 0 | 0.01029 | 1
1428 | 0 | 0.023955 | 0.85369 | 0 | 0 | 1 | 0 | 0.023955 | 1
1429 | 0 | 0.034367 | 0.85369 | 0 | 0 | 1 | 0 | 0.034367 | 1
1430 | 0 | 0.022787 | 0.85369 | 0 | 0 | 1 | 0 | 0.022787 | 1
1431 | 0 | 0.014545 | 0.85369 | 0 | 0 | 1 | 0 | 0.014545 | 1
1432 | 0 | 0.012211 | 0.85369 | 0 | 0 | 1 | 0 | 0.012211 | 1
1433 | 0 | 0.0098628 | 0.85369 | 0 | 0 | 1 | 0 | 0.0098628 | 1
1434 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1435 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1436 | 0 | 0.0055348 | 0.85369 | 0 | 1 | 1 | 0 | 0.0055348 | 1
1437 | 0 | 0.0045349 | 0.85369 | 0 | 1 | 1 | 0 | 0.0045349 | 1
1438 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1439 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1440 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1441 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1442 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1443 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1444 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1445 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1446 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1447 | 0 | 0.035778 | 0.85369 | 0 | 0 | 1 | 0 | 0.035778 | 1
1448 | 0 | 0.047774 | 0.85369 | 0 | 0 | 1 | 0 | 0.047774 | 1
1449 | 0 | 0.028098 | 0.85369 | 0 | 0 | 1 | 0 | 0.028098 | 1
1450 | 0 | 0.027242 | 0.85369 | 0 | 0 | 1 | 0 | 0.027242 | 1
1451 | 0 | 0.030329 | 0.85369 | 0 | 0 | 1 | 0 | 0.030329 | 1
1452 | 0 | 0.05208 | 0.85369 | 0 | 0 | 1 | 0 | 0.05208 | 1
1453 | 0 | 0.051661 | 0.85369 | 0 | 0 | 1 | 0 | 0.051661 | 1
1454 | 0 | 0.046685 | 0.85369 | 0 | 0 | 1 | 0 | 0.046685 | 1
1455 | 0 | 0.03614 | 0.85369 | 0 | 0 | 1 | 0 | 0.03614 | 1
1456 | 0 | 0.034702 | 0.85369 | 0 | 0 | 1 | 0 | 0.034702 | 1
1457 | 0 | 0.013712 | 0.85369 | 0 | 0 | 1 | 0 | 0.013712 | 1
1458 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1459 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1460 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1461 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1462 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1463 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1464 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1465 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1466 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1467 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1468 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1469 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1470 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1471 | 0 | 0.0086249 | 0.85369 | 0 | 0 | 1 | 0 | 0.0086249 | 1
1472 | 0 | 0.021542 | 0.85369 | 0 | 0 | 1 | 0 | 0.021542 | 1
1473 | 0 | 0.020074 | 0.85369 | 0 | 0 | 1 | 0 | 0.020074 | 1
1474 | 0 | 0.0076289 | 0.85369 | 0 | 0 | 1 | 0 | 0.0076289 | 1
1475 | 0.013665 | 0.029103 | 0.85369 | 0 | 0 | 1 | 0.013665 | 0.029103 | 1
1476 | 0.05578 | 0.042033 | 0.85369 | 0 | 0 | 1 | 0.05578 | 0.042033 | 1
1477 | 0.11615 | 0.040915 | 0.85369 | 0 | 0 | 1 | 0.11615 | 0.040915 | 1
1478 | 0.037065 | 0.045493 | 0.85369 | 0 | 0 | 1 | 0.037065 | 0.045493 | 1
1479 | 0.059843 | 0.028656 | 0.85369 | 0 | 0 | 1 | 0.059843 | 0.028656 | 1
1480 | 0 | 0.012853 | 0.85369 | 0 | 0 | 1 | 0 | 0.012853 | 1
1481 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1482 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1483 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1484 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1485 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1486 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1487 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1488 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1489 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1490 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1491 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1492 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1493 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1494 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1495 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1496 | 0 | 0.0019363 | 0.85369 | 0 | 0 | 1 | 0 | 0.0019363 | 1
1497 | 0 | 0.0079707 | 0.85369 | 0 | 0 | 1 | 0 | 0.0079707 | 1
1498 | 0 | 0.0056394 | 0.85369 | 0 | 0 | 1 | 0 | 0.0056394 | 1
1499 | 0.11223 | 0.02003 | 0.85369 | 0 | 0 | 1 | 0.11223 | 0.02003 | 1
1500 | 0.21559 | 0.030683 | 0.85369 | 0 | 0 | 1 | 0.21559 | 0.030683 | 1
1501 | 0.31814 | 0.034294 | 0.85369 | 0 | 0 | 1 | 0.31814 | 0.034294 | 1
1502 | 0.26001 | 0.044059 | 0.85369 | 0 | 0 | 1 | 0.26001 | 0.044059 | 1
1503 | 0.15188 | 0.025115 | 0.85369 | 0 | 0 | 1 | 0.15188 | 0.025115 | 1
1504 | 0.028207 | 0 | 0.85369 | 0 | 0 | 1 | 0.028207 | 0 | 1
1505 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1506 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1507 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1508 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1509 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1510 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1511 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1512 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1513 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1514 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1515 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1516 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1517 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1518 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1519 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1520 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1521 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1522 | 0.081527 | 0 | 0.85369 | 0 | 0 | 1 | 0.081527 | 0 | 1
1523 | 0.22997 | 0 | 0.85369 | 0 | 0 | 1 | 0.22997 | 0 | 1
1524 | 0.33992 | 0.010629 | 0.85369 | 0 | 0 | 1 | 0.33992 | 0.010629 | 1
1525 | 0.43817 | 0.021809 | 0.85369 | 0 | 0 | 1 | 0.43817 | 0.021809 | 1
1526 | 0.41013 | 0.019322 | 0.85369 | 0 | 0 | 1 | 0.41013 | 0.019322 | 1
1527 | 0.33516 | 0.0077514 | 0.85369 | 0 | 0 | 1 | 0.33516 | 0.0077514 | 1
1528 | 0.20046 | 0 | 0.85369 | 0 | 0 | 1 | 0.20046 | 0 | 1
1529 | 0.044844 | 0 | 0.85369 | 0 | 0 | 1 | 0.044844 | 0 | 1
1530 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1531 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1532 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1533 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1534 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1535 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1536 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1537 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1538 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1539 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1540 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1541 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1542 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1543 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1544 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1545 | 0.044096 | 0 | 0.85369 | 0 | 0 | 1 | 0.044096 | 0 | 1
1546 | 0.20593 | 0 | 0.85369 | 0 | 0 | 1 | 0.20593 | 0 | 1
1547 | 0.34813 | 0 | 0.85369 | 0 | 0 | 1 | 0.34813 | 0 | 1
1548 | 0.55615 | 0 | 0.85369 | 0 | 0 | 1 | 0.55615 | 0 | 1
1549 | 0.58879 | 0.0093686 | 0.85369 | 0 | 0 | 1 | 0.58879 | 0.0093686 | 1
1550 | 0.48472 | 0.018795 | 0.85369 | 0 | 0 | 1 | 0.48472 | 0.018795 | 1
1551 | 0.40779 | 0.0098415 | 0.85369 | 0 | 0 | 1 | 0.40779 | 0.0098415 | 1
1552 | 0.27964 | 0 | 0.85369 | 0 | 0 | 1 | 0.27964 | 0 | 1
1553 | 0.080258 | 0 | 0.85369 | 0 | 0 | 1 | 0.080258 | 0 | 1
1554 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1555 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1556 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1557 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1558 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1559 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1560 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1561 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1562 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1563 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1564 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1565 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1566 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1567 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1568 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1569 | 0.048018 | 0 | 0.85369 | 0 | 0 | 1 | 0.048018 | 0 | 1
1570 | 0.1749 | 0 | 0.85369 | 0 | 0 | 1 | 0.1749 | 0 | 1
1571 | 0.31726 | 0 | 0.85369 | 0 | 0 | 1 | 0.31726 | 0 | 1
1572 | 0.55776 | 0.0098762 | 0.85369 | 0 | 0 | 1 | 0.55776 | 0.0098762 | 1
1573 | 0.47222 | 0.02416 | 0.85369 | 0 | 0 | 1 | 0.47222 | 0.02416 | 1
1574 | 0.39054 | 0.030129 | 0.85369 | 0 | 0 | 1 | 0.39054 | 0.030129 | 1
1575 | 0.25124 | 0.033258 | 0.85369 | 0 | 0 | 1 | 0.25124 | 0.033258 | 1
1576 | 0.13833 | 0.022975 | 0.85369 | 0 | 0 | 1 | 0.13833 | 0.022975 | 1
1577 | 0.013546 | 0 | 0.85369 | 0 | 0 | 1 | 0.013546 | 0 | 1
1578 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1579 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1580 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1581 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1582 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1583 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1584 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1585 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1586 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1587 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1588 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1589 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1590 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1591 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1592 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1593 | 0.045697 | 0 | 0.85369 | 0 | 0 | 1 | 0.045697 | 0 | 1
1594 | 0.20296 | 0 | 0.85369 | 0 | 0 | 1 | 0.20296 | 0 | 1
1595 | 0.31769 | 0 | 0.85369 | 0 | 0 | 1 | 0.31769 | 0 | 1
1596 | 0.50222 | 0.020089 | 0.85369 | 0 | 0 | 1 | 0.50222 | 0.020089 | 1
1597 | 0.38129 | 0.036586 | 0.85369 | 0 | 0 | 1 | 0.38129 | 0.036586 | 1
1598 | 0.37047 | 0.050744 | 0.85369 | 0 | 0 | 1 | 0.37047 | 0.050744 | 1
1599 | 0.21132 | 0.05981 | 0.85369 | 0 | 0 | 1 | 0.21132 | 0.05981 | 1
1600 | 0.090211 | 0.043985 | 0.85369 | 0 | 0 | 1 | 0.090211 | 0.043985 | 1
1601 | 0 | 0.014817 | 0.85369 | 0 | 0 | 1 | 0 | 0.014817 | 1
1602 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1603 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1604 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1605 | 0 | 0 | 0.85369 | 0 | 1 | 1 | 0 | 0 | 1
1606 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1607 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1608 | 0 | 0 | 0.85369 | 0 | 0 | 1 | 0 | 0 | 1
1609 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1610 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1611 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1612 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1613 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1614 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1615 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1616 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1617 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1618 | 0.04014 | 0 | 0.96512 | 0 | 0 | 1 | 0.04014 | 0 | 1
1619 | 0.25387 | 0 | 0.96512 | 0 | 0 | 1 | 0.25387 | 0 | 1
1620 | 0.40331 | 0.0056657 | 0.96512 | 0 | 0 | 1 | 0.40331 | 0.0056657 | 1
1621 | 0.1688 | 0.016908 | 0.96512 | 0 | 0 | 1 | 0.1688 | 0.016908 | 1
1622 | 0.10368 | 0.031187 | 0.96512 | 0 | 0 | 1 | 0.10368 | 0.031187 | 1
1623 | 0.091433 | 0.050655 | 0.96512 | 0 | 0 | 1 | 0.091433 | 0.050655 | 1
1624 | 0.059172 | 0.04202 | 0.96512 | 0 | 0 | 1 | 0.059172 | 0.04202 | 1
1625 | 0.0020652 | 0.020605 | 0.96512 | 0 | 0 | 1 | 0.0020652 | 0.020605 | 1
1626 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1627 | 0 | 0.013966 | 0.96512 | 0 | 1 | 1 | 0 | 0.013966 | 1
1628 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1629 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1630 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1631 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1632 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1633 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1634 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1635 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1636 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1637 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1638 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1639 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1640 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1641 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1642 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1643 | 0.11881 | 0 | 0.96512 | 0 | 0 | 1 | 0.11881 | 0 | 1
1644 | 0.21217 | 0 | 0.96512 | 0 | 0 | 1 | 0.21217 | 0 | 1
1645 | 0.056513 | 0 | 0.96512 | 0 | 0 | 1 | 0.056513 | 0 | 1
1646 | 0.031135 | 0 | 0.96512 | 0 | 0 | 1 | 0.031135 | 0 | 1
1647 | 0.051036 | 0.010171 | 0.96512 | 0 | 0 | 1 | 0.051036 | 0.010171 | 1
1648 | 0.056429 | 0 | 0.96512 | 0 | 0 | 1 | 0.056429 | 0 | 1
1649 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1650 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1651 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1652 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1653 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1654 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1655 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1656 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1657 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1658 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1659 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1660 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1661 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1662 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1663 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1664 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1665 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1666 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1667 | 0.12988 | 0 | 0.96512 | 0 | 0 | 1 | 0.12988 | 0 | 1
1668 | 0.1638 | 0 | 0.96512 | 0 | 0 | 1 | 0.1638 | 0 | 1
1669 | 0.080886 | 0 | 0.96512 | 0 | 0 | 1 | 0.080886 | 0 | 1
1670 | 0.052996 | 0 | 0.96512 | 0 | 0 | 1 | 0.052996 | 0 | 1
1671 | 0.075744 | 0 | 0.96512 | 0 | 0 | 1 | 0.075744 | 0 | 1
1672 | 0.081157 | 0 | 0.96512 | 0 | 0 | 1 | 0.081157 | 0 | 1
1673 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1674 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1675 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1676 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1677 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1678 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1679 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1680 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1681 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1682 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1683 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1684 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1685 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1686 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1687 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1688 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1689 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1690 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1691 | 0.10526 | 0 | 0.88206 | 0 | 0 | 1 | 0.10526 | 0 | 1
1692 | 0.12155 | 0 | 0.88206 | 0 | 0 | 1 | 0.12155 | 0 | 1
1693 | 0.13821 | 0.0017053 | 0.88206 | 0 | 0 | 1 | 0.13821 | 0.0017053 | 1
1694 | 0.13682 | 0.020007 | 0.88206 | 0 | 0 | 1 | 0.13682 | 0.020007 | 1
1695 | 0.11313 | 0.014705 | 0.88206 | 0 | 0 | 1 | 0.11313 | 0.014705 | 1
1696 | 0.014514 | 0.016023 | 0.88206 | 0 | 0 | 1 | 0.014514 | 0.016023 | 1
1697 | 0 | 0.020488 | 0.88206 | 0 | 0 | 1 | 0 | 0.020488 | 1
1698 | 0 | 0.012908 | 0.88206 | 0 | 1 | 1 | 0 | 0.012908 | 1
1699 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1700 | 0 | 0.0042257 | 0.88206 | 0 | 1 | 1 | 0 | 0.0042257 | 1
1701 | 0 | 0.0032199 | 0.88206 | 0 | 1 | 1 | 0 | 0.0032199 | 1
1702 | 0 | 0.0022782 | 0.88206 | 0 | 0 | 1 | 0 | 0.0022782 | 1
1703 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1704 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1705 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1706 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1707 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1708 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1709 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1710 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1711 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1712 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1713 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1714 | 0.019538 | 0 | 0.88206 | 0 | 0 | 1 | 0.019538 | 0 | 1
1715 | 0.19385 | 0.0026441 | 0.88206 | 0 | 0 | 1 | 0.19385 | 0.0026441 | 1
1716 | 0.18604 | 0.018182 | 0.88206 | 0 | 0 | 1 | 0.18604 | 0.018182 | 1
1717 | 0.18404 | 0.020583 | 0.88206 | 0 | 0 | 1 | 0.18404 | 0.020583 | 1
1718 | 0.11539 | 0.025791 | 0.88206 | 0 | 0 | 1 | 0.11539 | 0.025791 | 1
1719 | 0.11605 | 0.014575 | 0.88206 | 0 | 0 | 1 | 0.11605 | 0.014575 | 1
1720 | 0 | 0.0059681 | 0.88206 | 0 | 0 | 1 | 0 | 0.0059681 | 1
1721 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1722 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1723 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1724 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1725 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1726 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1727 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1728 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1729 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1730 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1731 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1732 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1733 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1734 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1735 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1736 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1737 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1738 | 0.017286 | 0 | 0.88206 | 0 | 0 | 1 | 0.017286 | 0 | 1
1739 | 0.16707 | 0 | 0.88206 | 0 | 0 | 1 | 0.16707 | 0 | 1
1740 | 0.1835 | 0 | 0.88206 | 0 | 0 | 1 | 0.1835 | 0 | 1
1741 | 0.15657 | 0.0099615 | 0.88206 | 0 | 0 | 1 | 0.15657 | 0.0099615 | 1
1742 | 0.053163 | 0.0054831 | 0.88206 | 0 | 0 | 1 | 0.053163 | 0.0054831 | 1
1743 | 0.018271 | 0 | 0.88206 | 0 | 0 | 1 | 0.018271 | 0 | 1
1744 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1745 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1746 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1747 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1748 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1749 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1750 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1751 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1752 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1753 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1754 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1755 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1756 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1757 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1758 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1759 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1760 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1761 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1762 | 0.087543 | 0 | 0.88206 | 0 | 0 | 1 | 0.087543 | 0 | 1
1763 | 0.20739 | 0 | 0.88206 | 0 | 0 | 1 | 0.20739 | 0 | 1
1764 | 0.24256 | 0 | 0.88206 | 0 | 0 | 1 | 0.24256 | 0 | 1
1765 | 0.16523 | 0 | 0.88206 | 0 | 0 | 1 | 0.16523 | 0 | 1
1766 | 0.10512 | 0 | 0.88206 | 0 | 0 | 1 | 0.10512 | 0 | 1
1767 | 0.054268 | 0 | 0.88206 | 0 | 0 | 1 | 0.054268 | 0 | 1
1768 | 0.060634 | 0 | 0.88206 | 0 | 0 | 1 | 0.060634 | 0 | 1
1769 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1770 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1771 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1772 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1773 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1774 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1775 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1776 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1777 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1778 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1779 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1780 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1781 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1782 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1783 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1784 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1785 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1786 | 0.13151 | 0 | 0.88206 | 0 | 0 | 1 | 0.13151 | 0 | 1
1787 | 0.23951 | 0 | 0.88206 | 0 | 0 | 1 | 0.23951 | 0 | 1
1788 | 0.27099 | 0 | 0.88206 | 0 | 0 | 1 | 0.27099 | 0 | 1
1789 | 0.20752 | 0 | 0.88206 | 0 | 0 | 1 | 0.20752 | 0 | 1
1790 | 0.18717 | 0 | 0.88206 | 0 | 0 | 1 | 0.18717 | 0 | 1
1791 | 0.10562 | 0 | 0.88206 | 0 | 0 | 1 | 0.10562 | 0 | 1
1792 | 0.13484 | 0 | 0.88206 | 0 | 0 | 1 | 0.13484 | 0 | 1
1793 | 0.0065533 | 0 | 0.88206 | 0 | 0 | 1 | 0.0065533 | 0 | 1
1794 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1795 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1796 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1797 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1798 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1799 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1800 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1801 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1802 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1803 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1804 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1805 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1806 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1807 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1808 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1809 | 0.041555 | 0 | 0.88206 | 0 | 0 | 1 | 0.041555 | 0 | 1
1810 | 0.14982 | 0 | 0.88206 | 0 | 0 | 1 | 0.14982 | 0 | 1
1811 | 0.21997 | 0 | 0.88206 | 0 | 0 | 1 | 0.21997 | 0 | 1
1812 | 0.24481 | 0 | 0.88206 | 0 | 0 | 1 | 0.24481 | 0 | 1
1813 | 0.15872 | 0 | 0.88206 | 0 | 0 | 1 | 0.15872 | 0 | 1
1814 | 0.20049 | 0 | 0.88206 | 0 | 0 | 1 | 0.20049 | 0 | 1
1815 | 0.16168 | 0 | 0.88206 | 0 | 0 | 1 | 0.16168 | 0 | 1
1816 | 0.11832 | 0 | 0.88206 | 0 | 0 | 1 | 0.11832 | 0 | 1
1817 | 0.013722 | 0 | 0.88206 | 0 | 0 | 1 | 0.013722 | 0 | 1
1818 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1819 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1820 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1821 | 0 | 0 | 0.88206 | 0 | 1 | 1 | 0 | 0 | 1
1822 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1823 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1824 | 0 | 0 | 0.88206 | 0 | 0 | 1 | 0 | 0 | 1
1825 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1826 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1827 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1828 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1829 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1830 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1831 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1832 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1833 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1834 | 0.088008 | 0 | 0.96512 | 0 | 0 | 1 | 0.088008 | 0 | 1
1835 | 0.1585 | 0.0035263 | 0.96512 | 0 | 0 | 1 | 0.1585 | 0.0035263 | 1
1836 | 0.16271 | 0.014134 | 0.96512 | 0 | 0 | 1 | 0.16271 | 0.014134 | 1
1837 | 0.14939 | 0.015579 | 0.96512 | 0 | 0 | 1 | 0.14939 | 0.015579 | 1
1838 | 0.16445 | 0.019133 | 0.96512 | 0 | 0 | 1 | 0.16445 | 0.019133 | 1
1839 | 0.13826 | 0.022862 | 0.96512 | 0 | 0 | 1 | 0.13826 | 0.022862 | 1
1840 | 0.088019 | 0.029742 | 0.96512 | 0 | 0 | 1 | 0.088019 | 0.029742 | 1
1841 | 0.01119 | 0.011596 | 0.96512 | 0 | 0 | 1 | 0.01119 | 0.011596 | 1
1842 | 0 | 0.0018619 | 0.96512 | 0 | 1 | 1 | 0 | 0.0018619 | 1
1843 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1844 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1845 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1846 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1847 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1848 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1849 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1850 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1851 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1852 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1853 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1854 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1855 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1856 | 0 | 0.031447 | 0.96512 | 0 | 0 | 1 | 0 | 0.031447 | 1
1857 | 0.0026158 | 0.020174 | 0.96512 | 0 | 0 | 1 | 0.0026158 | 0.020174 | 1
1858 | 0.12068 | 0.028547 | 0.96512 | 0 | 0 | 1 | 0.12068 | 0.028547 | 1
1859 | 0.1578 | 0.053288 | 0.96512 | 0 | 0 | 1 | 0.1578 | 0.053288 | 1
1860 | 0.16018 | 0.07567 | 0.96512 | 0 | 0 | 1 | 0.16018 | 0.07567 | 1
1861 | 0.14945 | 0.080214 | 0.96512 | 0 | 0 | 1 | 0.14945 | 0.080214 | 1
1862 | 0.11682 | 0.08704 | 0.96512 | 0 | 0 | 1 | 0.11682 | 0.08704 | 1
1863 | 0.065561 | 0.090101 | 0.96512 | 0 | 0 | 1 | 0.065561 | 0.090101 | 1
1864 | 0 | 0.089636 | 0.96512 | 0 | 0 | 1 | 0 | 0.089636 | 1
1865 | 0 | 0.082407 | 0.96512 | 0 | 0 | 1 | 0 | 0.082407 | 1
1866 | 0 | 0.066642 | 0.96512 | 0 | 1 | 1 | 0 | 0.066642 | 1
1867 | 0 | 0.032722 | 0.96512 | 0 | 1 | 1 | 0 | 0.032722 | 1
1868 | 0 | 0.036427 | 0.96512 | 0 | 1 | 1 | 0 | 0.036427 | 1
1869 | 0 | 0.059056 | 0.96512 | 0 | 1 | 1 | 0 | 0.059056 | 1
1870 | 0 | 0.065862 | 0.96512 | 0 | 0 | 1 | 0 | 0.065862 | 1
1871 | 0 | 0.059082 | 0.96512 | 0 | 0 | 1 | 0 | 0.059082 | 1
1872 | 0 | 0.05317 | 0.96512 | 0 | 0 | 1 | 0 | 0.05317 | 1
1873 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1874 | 0 | 0.035931 | 0.96512 | 0 | 0 | 1 | 0 | 0.035931 | 1
1875 | 0 | 0.024982 | 0.96512 | 0 | 0 | 1 | 0 | 0.024982 | 1
1876 | 0 | 0.040735 | 0.96512 | 0 | 0 | 1 | 0 | 0.040735 | 1
1877 | 0 | 0.03893 | 0.96512 | 0 | 0 | 1 | 0 | 0.03893 | 1
1878 | 0 | 0.04205 | 0.96512 | 0 | 0 | 1 | 0 | 0.04205 | 1
1879 | 0 | 0.016658 | 0.96512 | 0 | 0 | 1 | 0 | 0.016658 | 1
1880 | 0 | 0.059809 | 0.96512 | 0 | 0 | 1 | 0 | 0.059809 | 1
1881 | 0 | 0.058426 | 0.96512 | 0 | 0 | 1 | 0 | 0.058426 | 1
1882 | 0.18908 | 0.074458 | 0.96512 | 0 | 0 | 1 | 0.18908 | 0.074458 | 1
1883 | 0.17743 | 0.11079 | 0.96512 | 0 | 0 | 1 | 0.17743 | 0.11079 | 1
1884 | 0.1982 | 0.12317 | 0.96512 | 0 | 0 | 1 | 0.1982 | 0.12317 | 1
1885 | 0.20561 | 0.1209 | 0.96512 | 0 | 0 | 1 | 0.20561 | 0.1209 | 1
1886 | 0.14694 | 0.1244 | 0.96512 | 0 | 0 | 1 | 0.14694 | 0.1244 | 1
1887 | 0.080351 | 0.12422 | 0.96512 | 0 | 0 | 1 | 0.080351 | 0.12422 | 1
1888 | 0 | 0.12805 | 0.96512 | 0 | 0 | 1 | 0 | 0.12805 | 1
1889 | 0 | 0.13704 | 0.96512 | 0 | 0 | 1 | 0 | 0.13704 | 1
1890 | 0 | 0.13078 | 0.96512 | 0 | 1 | 1 | 0 | 0.13078 | 1
1891 | 0 | 0.096904 | 0.96512 | 0 | 1 | 1 | 0 | 0.096904 | 1
1892 | 0 | 0.089298 | 0.96512 | 0 | 1 | 1 | 0 | 0.089298 | 1
1893 | 0 | 0.1057 | 0.96512 | 0 | 1 | 1 | 0 | 0.1057 | 1
1894 | 0 | 0.11096 | 0.96512 | 0 | 0 | 1 | 0 | 0.11096 | 1
1895 | 0 | 0.09402 | 0.96512 | 0 | 0 | 1 | 0 | 0.09402 | 1
1896 | 0 | 0.086353 | 0.96512 | 0 | 0 | 1 | 0 | 0.086353 | 1
1897 | 0 | 0.053449 | 0.96512 | 0 | 0 | 1 | 0 | 0.053449 | 1
1898 | 0 | 0.066637 | 0.96512 | 0 | 0 | 1 | 0 | 0.066637 | 1
1899 | 0 | 0.048101 | 0.96512 | 0 | 0 | 1 | 0 | 0.048101 | 1
1900 | 0 | 0.047638 | 0.96512 | 0 | 0 | 1 | 0 | 0.047638 | 1
1901 | 0 | 0.055186 | 0.96512 | 0 | 0 | 1 | 0 | 0.055186 | 1
1902 | 0 | 0.059939 | 0.96512 | 0 | 0 | 1 | 0 | 0.059939 | 1
1903 | 0 | 0.021835 | 0.96512 | 0 | 0 | 1 | 0 | 0.021835 | 1
1904 | 0 | 0.048658 | 0.96512 | 0 | 0 | 1 | 0 | 0.048658 | 1
1905 | 0 | 0.041374 | 0.96512 | 0 | 0 | 1 | 0 | 0.041374 | 1
1906 | 0.077417 | 0.051205 | 0.96512 | 0 | 0 | 1 | 0.077417 | 0.051205 | 1
1907 | 0.086422 | 0.084334 | 0.96512 | 0 | 0 | 1 | 0.086422 | 0.084334 | 1
1908 | 0.1436 | 0.098168 | 0.96512 | 0 | 0 | 1 | 0.1436 | 0.098168 | 1
1909 | 0.14894 | 0.096976 | 0.96512 | 0 | 0 | 1 | 0.14894 | 0.096976 | 1
1910 | 0.037627 | 0.10878 | 0.96512 | 0 | 0 | 1 | 0.037627 | 0.10878 | 1
1911 | 0 | 0.099604 | 0.96512 | 0 | 0 | 1 | 0 | 0.099604 | 1
1912 | 0 | 0.065589 | 0.96512 | 0 | 0 | 1 | 0 | 0.065589 | 1
1913 | 0 | 0.066233 | 0.96512 | 0 | 0 | 1 | 0 | 0.066233 | 1
1914 | 0 | 0.065701 | 0.96512 | 0 | 1 | 1 | 0 | 0.065701 | 1
1915 | 0 | 0.046117 | 0.96512 | 0 | 1 | 1 | 0 | 0.046117 | 1
1916 | 0 | 0.040344 | 0.96512 | 0 | 1 | 1 | 0 | 0.040344 | 1
1917 | 0 | 0.051429 | 0.96512 | 0 | 1 | 1 | 0 | 0.051429 | 1
1918 | 0 | 0.051172 | 0.96512 | 0 | 0 | 1 | 0 | 0.051172 | 1
1919 | 0 | 0.056379 | 0.96512 | 0 | 0 | 1 | 0 | 0.056379 | 1
1920 | 0 | 0.050928 | 0.96512 | 0 | 0 | 1 | 0 | 0.050928 | 1
1921 | 0 | 0.066178 | 0.96512 | 0 | 0 | 1 | 0 | 0.066178 | 1
1922 | 0 | 0.047454 | 0.96512 | 0 | 0 | 1 | 0 | 0.047454 | 1
1923 | 0 | 0.031082 | 0.96512 | 0 | 0 | 1 | 0 | 0.031082 | 1
1924 | 0 | 0.027435 | 0.96512 | 0 | 0 | 1 | 0 | 0.027435 | 1
1925 | 0 | 0.028207 | 0.96512 | 0 | 0 | 1 | 0 | 0.028207 | 1
1926 | 0 | 0.013436 | 0.96512 | 0 | 0 | 1 | 0 | 0.013436 | 1
1927 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1928 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1929 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1930 | 0.052292 | 0.0083556 | 0.96512 | 0 | 0 | 1 | 0.052292 | 0.0083556 | 1
1931 | 0.090446 | 0.044027 | 0.96512 | 0 | 0 | 1 | 0.090446 | 0.044027 | 1
1932 | 0.17015 | 0.046211 | 0.96512 | 0 | 0 | 1 | 0.17015 | 0.046211 | 1
1933 | 0.15082 | 0.049788 | 0.96512 | 0 | 0 | 1 | 0.15082 | 0.049788 | 1
1934 | 0.068405 | 0.071764 | 0.96512 | 0 | 0 | 1 | 0.068405 | 0.071764 | 1
1935 | 0 | 0.072487 | 0.96512 | 0 | 0 | 1 | 0 | 0.072487 | 1
1936 | 0 | 0.049367 | 0.96512 | 0 | 0 | 1 | 0 | 0.049367 | 1
1937 | 0 | 0.034807 | 0.96512 | 0 | 0 | 1 | 0 | 0.034807 | 1
1938 | 0 | 0.029005 | 0.96512 | 0 | 1 | 1 | 0 | 0.029005 | 1
1939 | 0 | 0.012064 | 0.96512 | 0 | 1 | 1 | 0 | 0.012064 | 1
1940 | 0 | 0.0023563 | 0.96512 | 0 | 1 | 1 | 0 | 0.0023563 | 1
1941 | 0 | 0.0023781 | 0.96512 | 0 | 1 | 1 | 0 | 0.0023781 | 1
1942 | 0 | 0.0041934 | 0.96512 | 0 | 0 | 1 | 0 | 0.0041934 | 1
1943 | 0 | 0.0056166 | 0.96512 | 0 | 0 | 1 | 0 | 0.0056166 | 1
1944 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1945 | 0 | 0.047508 | 0.96512 | 0 | 0 | 1 | 0 | 0.047508 | 1
1946 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1947 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1948 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1949 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1950 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1951 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1952 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1953 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1954 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1955 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1956 | 0 | 0.0034165 | 0.96512 | 0 | 0 | 1 | 0 | 0.0034165 | 1
1957 | 0 | 0.019466 | 0.96512 | 0 | 0 | 1 | 0 | 0.019466 | 1
1958 | 0 | 0.041158 | 0.96512 | 0 | 0 | 1 | 0 | 0.041158 | 1
1959 | 0 | 0.040777 | 0.96512 | 0 | 0 | 1 | 0 | 0.040777 | 1
1960 | 0 | 0.020064 | 0.96512 | 0 | 0 | 1 | 0 | 0.020064 | 1
1961 | 0 | 0.01793 | 0.96512 | 0 | 0 | 1 | 0 | 0.01793 | 1
1962 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1963 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1964 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1965 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1966 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1967 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1968 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1969 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1970 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1971 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1972 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1973 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1974 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1975 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1976 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1977 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1978 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1979 | 0 | 0.0013072 | 0.96512 | 0 | 0 | 1 | 0 | 0.0013072 | 1
1980 | 0 | 0.0042982 | 0.96512 | 0 | 0 | 1 | 0 | 0.0042982 | 1
1981 | 0 | 0.023865 | 0.96512 | 0 | 0 | 1 | 0 | 0.023865 | 1
1982 | 0.069461 | 0.029482 | 0.96512 | 0 | 0 | 1 | 0.069461 | 0.029482 | 1
1983 | 0.077819 | 0.030268 | 0.96512 | 0 | 0 | 1 | 0.077819 | 0.030268 | 1
1984 | 0.0026582 | 0.025609 | 0.96512 | 0 | 0 | 1 | 0.0026582 | 0.025609 | 1
1985 | 0 | 0.020535 | 0.96512 | 0 | 0 | 1 | 0 | 0.020535 | 1
1986 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1987 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1988 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1989 | 0 | 0 | 0.96512 | 0 | 1 | 1 | 0 | 0 | 1
1990 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1991 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1992 | 0 | 0 | 0.96512 | 0 | 0 | 1 | 0 | 0 | 1
1993 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1994 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1995 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1996 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1997 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1998 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
1999 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2000 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2001 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2002 | 0.021027 | 0 | 0.91445 | 0 | 0 | 1 | 0.021027 | 0 | 1
2003 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2004 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2005 | 0.027385 | 0.014803 | 0.91445 | 0 | 0 | 1 | 0.027385 | 0.014803 | 1
2006 | 0.12082 | 0.01725 | 0.91445 | 0 | 0 | 1 | 0.12082 | 0.01725 | 1
2007 | 0.21628 | 0.017672 | 0.91445 | 0 | 0 | 1 | 0.21628 | 0.017672 | 1
2008 | 0.11857 | 0.0089626 | 0.91445 | 0 | 0 | 1 | 0.11857 | 0.0089626 | 1
2009 | 0.021566 | 0.011891 | 0.91445 | 0 | 0 | 1 | 0.021566 | 0.011891 | 1
2010 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2011 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2012 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2013 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2014 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2015 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2016 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2017 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2018 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2019 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2020 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2021 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2022 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2023 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2024 | 0.0069058 | 0 | 0.91445 | 0 | 0 | 1 | 0.0069058 | 0 | 1
2025 | 0.14278 | 0 | 0.91445 | 0 | 0 | 1 | 0.14278 | 0 | 1
2026 | 0.27231 | 0 | 0.91445 | 0 | 0 | 1 | 0.27231 | 0 | 1
2027 | 0.23206 | 0 | 0.91445 | 0 | 0 | 1 | 0.23206 | 0 | 1
2028 | 0.21794 | 0.0016459 | 0.91445 | 0 | 0 | 1 | 0.21794 | 0.0016459 | 1
2029 | 0.25067 | 0.04835 | 0.91445 | 0 | 0 | 1 | 0.25067 | 0.04835 | 1
2030 | 0.31032 | 0.047333 | 0.91445 | 0 | 0 | 1 | 0.31032 | 0.047333 | 1
2031 | 0.31842 | 0.047804 | 0.91445 | 0 | 0 | 1 | 0.31842 | 0.047804 | 1
2032 | 0.22016 | 0.03035 | 0.91445 | 0 | 0 | 1 | 0.22016 | 0.03035 | 1
2033 | 0.090995 | 0.026866 | 0.91445 | 0 | 0 | 1 | 0.090995 | 0.026866 | 1
2034 | 0 | 0.018006 | 0.91445 | 0 | 1 | 1 | 0 | 0.018006 | 1
2035 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2036 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2037 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2038 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2039 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2040 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2041 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2042 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2043 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2044 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2045 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2046 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2047 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2048 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2049 | 0.11812 | 0 | 0.91445 | 0 | 0 | 1 | 0.11812 | 0 | 1
2050 | 0.246 | 0 | 0.91445 | 0 | 0 | 1 | 0.246 | 0 | 1
2051 | 0.2535 | 0 | 0.91445 | 0 | 0 | 1 | 0.2535 | 0 | 1
2052 | 0.27254 | 0 | 0.91445 | 0 | 0 | 1 | 0.27254 | 0 | 1
2053 | 0.33406 | 0.0080169 | 0.91445 | 0 | 0 | 1 | 0.33406 | 0.0080169 | 1
2054 | 0.40183 | 0.0086797 | 0.91445 | 0 | 0 | 1 | 0.40183 | 0.0086797 | 1
2055 | 0.40389 | 0.011463 | 0.91445 | 0 | 0 | 1 | 0.40389 | 0.011463 | 1
2056 | 0.25446 | 0.0012118 | 0.91445 | 0 | 0 | 1 | 0.25446 | 0.0012118 | 1
2057 | 0.0983 | 0 | 0.91445 | 0 | 0 | 1 | 0.0983 | 0 | 1
2058 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2059 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2060 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2061 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2062 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2063 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2064 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2065 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2066 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2067 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2068 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2069 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2070 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2071 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2072 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2073 | 0.048369 | 0 | 0.91445 | 0 | 0 | 1 | 0.048369 | 0 | 1
2074 | 0.19815 | 0 | 0.91445 | 0 | 0 | 1 | 0.19815 | 0 | 1
2075 | 0.26377 | 0 | 0.91445 | 0 | 0 | 1 | 0.26377 | 0 | 1
2076 | 0.24942 | 0 | 0.91445 | 0 | 0 | 1 | 0.24942 | 0 | 1
2077 | 0.33593 | 0.020867 | 0.91445 | 0 | 0 | 1 | 0.33593 | 0.020867 | 1
2078 | 0.39712 | 0.018773 | 0.91445 | 0 | 0 | 1 | 0.39712 | 0.018773 | 1
2079 | 0.33129 | 0.015241 | 0.91445 | 0 | 0 | 1 | 0.33129 | 0.015241 | 1
2080 | 0.1677 | 0.012102 | 0.91445 | 0 | 0 | 1 | 0.1677 | 0.012102 | 1
2081 | 0.051373 | 0 | 0.91445 | 0 | 0 | 1 | 0.051373 | 0 | 1
2082 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2083 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2084 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2085 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2086 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2087 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2088 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2089 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2090 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2091 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2092 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2093 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2094 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2095 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2096 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2097 | 0.057534 | 0 | 0.91445 | 0 | 0 | 1 | 0.057534 | 0 | 1
2098 | 0.19905 | 0 | 0.91445 | 0 | 0 | 1 | 0.19905 | 0 | 1
2099 | 0.31201 | 9.7251e-05 | 0.91445 | 0 | 0 | 1 | 0.31201 | 9.7251e-05 | 1
2100 | 0.30626 | 0.017011 | 0.91445 | 0 | 0 | 1 | 0.30626 | 0.017011 | 1
2101 | 0.35662 | 0.028939 | 0.91445 | 0 | 0 | 1 | 0.35662 | 0.028939 | 1
2102 | 0.40895 | 0.030374 | 0.91445 | 0 | 0 | 1 | 0.40895 | 0.030374 | 1
2103 | 0.35521 | 0.022956 | 0.91445 | 0 | 0 | 1 | 0.35521 | 0.022956 | 1
2104 | 0.18546 | 0.020475 | 0.91445 | 0 | 0 | 1 | 0.18546 | 0.020475 | 1
2105 | 0.060056 | 0.0042597 | 0.91445 | 0 | 0 | 1 | 0.060056 | 0.0042597 | 1
2106 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2107 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2108 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2109 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2110 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2111 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2112 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2113 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2114 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2115 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2116 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2117 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2118 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2119 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2120 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2121 | 0.083148 | 0 | 0.91445 | 0 | 0 | 1 | 0.083148 | 0 | 1
2122 | 0.19343 | 0 | 0.91445 | 0 | 0 | 1 | 0.19343 | 0 | 1
2123 | 0.24557 | 0 | 0.91445 | 0 | 0 | 1 | 0.24557 | 0 | 1
2124 | 0.1835 | 0.045182 | 0.91445 | 0 | 0 | 1 | 0.1835 | 0.045182 | 1
2125 | 0.15961 | 0.053234 | 0.91445 | 0 | 0 | 1 | 0.15961 | 0.053234 | 1
2126 | 0.26962 | 0.056643 | 0.91445 | 0 | 0 | 1 | 0.26962 | 0.056643 | 1
2127 | 0.29553 | 0.042002 | 0.91445 | 0 | 0 | 1 | 0.29553 | 0.042002 | 1
2128 | 0.17047 | 0.033166 | 0.91445 | 0 | 0 | 1 | 0.17047 | 0.033166 | 1
2129 | 0.040755 | 0.024847 | 0.91445 | 0 | 0 | 1 | 0.040755 | 0.024847 | 1
2130 | 0 | 0.0089059 | 0.91445 | 0 | 1 | 1 | 0 | 0.0089059 | 1
2131 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2132 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2133 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2134 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2135 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2136 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2137 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2138 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2139 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2140 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2141 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2142 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2143 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2144 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2145 | 0.11038 | 0 | 0.91445 | 0 | 0 | 1 | 0.11038 | 0 | 1
2146 | 0.1806 | 0 | 0.91445 | 0 | 0 | 1 | 0.1806 | 0 | 1
2147 | 0.17775 | 0 | 0.91445 | 0 | 0 | 1 | 0.17775 | 0 | 1
2148 | 0.14961 | 0.017336 | 0.91445 | 0 | 0 | 1 | 0.14961 | 0.017336 | 1
2149 | 0.15639 | 0.024114 | 0.91445 | 0 | 0 | 1 | 0.15639 | 0.024114 | 1
2150 | 0.28623 | 0.027337 | 0.91445 | 0 | 0 | 1 | 0.28623 | 0.027337 | 1
2151 | 0.36027 | 0.01694 | 0.91445 | 0 | 0 | 1 | 0.36027 | 0.01694 | 1
2152 | 0.24523 | 0.026081 | 0.91445 | 0 | 0 | 1 | 0.24523 | 0.026081 | 1
2153 | 0.063647 | 0.014419 | 0.91445 | 0 | 0 | 1 | 0.063647 | 0.014419 | 1
2154 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2155 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2156 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2157 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2158 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2159 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2160 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2161 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2162 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2163 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2164 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2165 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2166 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2167 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2168 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2169 | 0.011737 | 0 | 0.91445 | 0 | 0 | 1 | 0.011737 | 0 | 1
2170 | 0.090635 | 0.00099556 | 0.91445 | 0 | 0 | 1 | 0.090635 | 0.00099556 | 1
2171 | 0.044605 | 0 | 0.91445 | 0 | 0 | 1 | 0.044605 | 0 | 1
2172 | 0.042977 | 0.025706 | 0.91445 | 0 | 0 | 1 | 0.042977 | 0.025706 | 1
2173 | 0.058289 | 0.016905 | 0.91445 | 0 | 0 | 1 | 0.058289 | 0.016905 | 1
2174 | 0.12333 | 0.018318 | 0.91445 | 0 | 0 | 1 | 0.12333 | 0.018318 | 1
2175 | 0.13675 | 0.02823 | 0.91445 | 0 | 0 | 1 | 0.13675 | 0.02823 | 1
2176 | 0.09439 | 0.023333 | 0.91445 | 0 | 0 | 1 | 0.09439 | 0.023333 | 1
2177 | 0 | 0.023994 | 0.91445 | 0 | 0 | 1 | 0 | 0.023994 | 1
2178 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2179 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2180 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2181 | 0 | 0 | 0.91445 | 0 | 1 | 1 | 0 | 0 | 1
2182 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2183 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2184 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2185 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2186 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2187 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2188 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2189 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2190 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2191 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2192 | 0 | 0.00015385 | 0.91445 | 0 | 0 | 1 | 0 | 0.00015385 | 1
2193 | 0 | 0.0087908 | 0.91445 | 0 | 0 | 1 | 0 | 0.0087908 | 1
2194 | 0.059305 | 0.030235 | 0.91445 | 0 | 0 | 1 | 0.059305 | 0.030235 | 1
2195 | 0.070082 | 0.032148 | 0.91445 | 0 | 0 | 1 | 0.070082 | 0.032148 | 1
2196 | 0.13136 | 0.048036 | 0.91445 | 0 | 0 | 1 | 0.13136 | 0.048036 | 1
2197 | 0.14102 | 0.048377 | 0.91445 | 0 | 0 | 1 | 0.14102 | 0.048377 | 1
2198 | 0.11348 | 0.053808 | 0.91445 | 0 | 0 | 1 | 0.11348 | 0.053808 | 1
2199 | 0.050754 | 0.073024 | 0.91445 | 0 | 0 | 1 | 0.050754 | 0.073024 | 1
2200 | 0.094867 | 0.070798 | 0.91445 | 0 | 0 | 1 | 0.094867 | 0.070798 | 1
2201 | 0 | 0.061225 | 0.91445 | 0 | 0 | 1 | 0 | 0.061225 | 1
2202 | 0 | 0.025155 | 0.91445 | 0 | 1 | 1 | 0 | 0.025155 | 1
2203 | 0 | 0.01024 | 0.91445 | 0 | 1 | 1 | 0 | 0.01024 | 1
2204 | 0 | 0.018154 | 0.91445 | 0 | 1 | 1 | 0 | 0.018154 | 1
2205 | 0 | 0.030968 | 0.91445 | 0 | 1 | 1 | 0 | 0.030968 | 1
2206 | 0 | 0.014518 | 0.91445 | 0 | 0 | 1 | 0 | 0.014518 | 1
2207 | 0 | 0.011149 | 0.91445 | 0 | 0 | 1 | 0 | 0.011149 | 1
2208 | 0 | 0.0072455 | 0.91445 | 0 | 0 | 1 | 0 | 0.0072455 | 1
2209 | 0 | 0.004628 | 0.91445 | 0 | 0 | 1 | 0 | 0.004628 | 1
2210 | 0 | 0.0055975 | 0.91445 | 0 | 0 | 1 | 0 | 0.0055975 | 1
2211 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2212 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2213 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2214 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2215 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2216 | 0 | 0.020235 | 0.91445 | 0 | 0 | 1 | 0 | 0.020235 | 1
2217 | 0 | 0.053782 | 0.91445 | 0 | 0 | 1 | 0 | 0.053782 | 1
2218 | 0.077006 | 0.079487 | 0.91445 | 0 | 0 | 1 | 0.077006 | 0.079487 | 1
2219 | 0.09679 | 0.088871 | 0.91445 | 0 | 0 | 1 | 0.09679 | 0.088871 | 1
2220 | 0.14532 | 0.096141 | 0.91445 | 0 | 0 | 1 | 0.14532 | 0.096141 | 1
2221 | 0.10627 | 0.067337 | 0.91445 | 0 | 0 | 1 | 0.10627 | 0.067337 | 1
2222 | 0.094164 | 0.081285 | 0.91445 | 0 | 0 | 1 | 0.094164 | 0.081285 | 1
2223 | 0.019673 | 0.0947 | 0.91445 | 0 | 0 | 1 | 0.019673 | 0.0947 | 1
2224 | 0.055036 | 0.072562 | 0.91445 | 0 | 0 | 1 | 0.055036 | 0.072562 | 1
2225 | 0 | 0.051575 | 0.91445 | 0 | 0 | 1 | 0 | 0.051575 | 1
2226 | 0 | 0.02835 | 0.91445 | 0 | 1 | 1 | 0 | 0.02835 | 1
2227 | 0 | 0.014716 | 0.91445 | 0 | 1 | 1 | 0 | 0.014716 | 1
2228 | 0 | 0.028013 | 0.91445 | 0 | 1 | 1 | 0 | 0.028013 | 1
2229 | 0 | 0.041628 | 0.91445 | 0 | 1 | 1 | 0 | 0.041628 | 1
2230 | 0 | 0.01626 | 0.91445 | 0 | 0 | 1 | 0 | 0.01626 | 1
2231 | 0 | 0.0039753 | 0.91445 | 0 | 0 | 1 | 0 | 0.0039753 | 1
2232 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2233 | 0 | 0.025211 | 0.91445 | 0 | 0 | 1 | 0 | 0.025211 | 1
2234 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2235 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2236 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2237 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2238 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2239 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2240 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2241 | 0.013475 | 0.0015239 | 0.91445 | 0 | 0 | 1 | 0.013475 | 0.0015239 | 1
2242 | 0.12139 | 0.013201 | 0.91445 | 0 | 0 | 1 | 0.12139 | 0.013201 | 1
2243 | 0.18161 | 0.032472 | 0.91445 | 0 | 0 | 1 | 0.18161 | 0.032472 | 1
2244 | 0.21262 | 0.044717 | 0.91445 | 0 | 0 | 1 | 0.21262 | 0.044717 | 1
2245 | 0.23353 | 0.025565 | 0.91445 | 0 | 0 | 1 | 0.23353 | 0.025565 | 1
2246 | 0.25721 | 0.045456 | 0.91445 | 0 | 0 | 1 | 0.25721 | 0.045456 | 1
2247 | 0.1687 | 0.070492 | 0.91445 | 0 | 0 | 1 | 0.1687 | 0.070492 | 1
2248 | 0.14142 | 0.083037 | 0.91445 | 0 | 0 | 1 | 0.14142 | 0.083037 | 1
2249 | 0 | 0.047759 | 0.91445 | 0 | 0 | 1 | 0 | 0.047759 | 1
2250 | 0 | 0.030424 | 0.91445 | 0 | 1 | 1 | 0 | 0.030424 | 1
2251 | 0 | 0.0076542 | 0.91445 | 0 | 1 | 1 | 0 | 0.0076542 | 1
2252 | 0 | 0.027579 | 0.91445 | 0 | 1 | 1 | 0 | 0.027579 | 1
2253 | 0 | 0.030893 | 0.91445 | 0 | 1 | 1 | 0 | 0.030893 | 1
2254 | 0 | 0.014278 | 0.91445 | 0 | 0 | 1 | 0 | 0.014278 | 1
2255 | 0 | 0.0091631 | 0.91445 | 0 | 0 | 1 | 0 | 0.0091631 | 1
2256 | 0 | 0.011841 | 0.91445 | 0 | 0 | 1 | 0 | 0.011841 | 1
2257 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2258 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2259 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2260 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2261 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2262 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2263 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2264 | 0 | 0 | 0.91445 | 0 | 0 | 1 | 0 | 0 | 1
2265 | 0.075363 | 0.0143 | 0.91445 | 0 | 0 | 1 | 0.075363 | 0.0143 | 1
2266 | 0.21657 | 0.024633 | 0.91445 | 0 | 0 | 1 | 0.21657 | 0.024633 | 1
2267 | 0.2418 | 0.034193 | 0.91445 | 0 | 0 | 1 | 0.2418 | 0.034193 | 1
2268 | 0.33347 | 0.044533 | 0.91445 | 0 | 0 | 1 | 0.33347 | 0.044533 | 1
2269 | 0.34629 | 0.016616 | 0.91445 | 0 | 0 | 1 | 0.34629 | 0.016616 | 1
2270 | 0.35891 | 0.038447 | 0.91445 | 0 | 0 | 1 | 0.35891 | 0.038447 | 1
2271 | 0.31176 | 0.09202 | 0.91445 | 0 | 0 | 1 | 0.31176 | 0.09202 | 1
2272 | 0.19492 | 0.11163 | 0.91445 | 0 | 0 | 1 | 0.19492 | 0.11163 | 1
2273 | 0.024239 | 0.0503 | 0.91445 | 0 | 0 | 1 | 0.024239 | 0.0503 | 1
2274 | 0 | 0.039631 | 0.91445 | 0 | 1 | 1 | 0 | 0.039631 | 1
2275 | 0 | 0.0081266 | 0.91445 | 0 | 1 | 1 | 0 | 0.0081266 | 1
2276 | 0 | 0.036936 | 0.91445 | 0 | 1 | 1 | 0 | 0.036936 | 1
2277 | 0 | 0.037586 | 0.91445 | 0 | 1 | 1 | 0 | 0.037586 | 1
2278 | 0 | 0.030567 | 0.91445 | 0 | 0 | 1 | 0 | 0.030567 | 1
2279 | 0 | 0.02611 | 0.91445 | 0 | 0 | 1 | 0 | 0.02611 | 1
2280 | 0 | 0.041659 | 0.91445 | 0 | 0 | 1 | 0 | 0.041659 | 1
2281 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2282 | 0 | 0.00034779 | 1 | 0 | 0 | 1 | 0 | 0.00034779 | 1
2283 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2284 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2285 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2286 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2287 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2288 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2289 | 0.0044136 | 0 | 1 | 0 | 0 | 1 | 0.0044136 | 0 | 1
2290 | 0.1173 | 0.010315 | 1 | 0 | 0 | 1 | 0.1173 | 0.010315 | 1
2291 | 0.15052 | 0.032072 | 1 | 0 | 0 | 1 | 0.15052 | 0.032072 | 1
2292 | 0.27714 | 0.051129 | 1 | 0 | 0 | 1 | 0.27714 | 0.051129 | 1
2293 | 0.32134 | 0.054573 | 1 | 0 | 0 | 1 | 0.32134 | 0.054573 | 1
2294 | 0.22597 | 0.066256 | 1 | 0 | 0 | 1 | 0.22597 | 0.066256 | 1
2295 | 0.14143 | 0.11282 | 1 | 0 | 0 | 1 | 0.14143 | 0.11282 | 1
2296 | 0.062671 | 0.11366 | 1 | 0 | 0 | 1 | 0.062671 | 0.11366 | 1
2297 | 0 | 0.066027 | 1 | 0 | 0 | 1 | 0 | 0.066027 | 1
2298 | 0 | 0.048269 | 1 | 0 | 1 | 1 | 0 | 0.048269 | 1
2299 | 0 | 0.013112 | 1 | 0 | 1 | 1 | 0 | 0.013112 | 1
2300 | 0 | 0.032139 | 1 | 0 | 1 | 1 | 0 | 0.032139 | 1
2301 | 0 | 0.042326 | 1 | 0 | 1 | 1 | 0 | 0.042326 | 1
2302 | 0 | 0.036607 | 1 | 0 | 0 | 1 | 0 | 0.036607 | 1
2303 | 0 | 0.034756 | 1 | 0 | 0 | 1 | 0 | 0.034756 | 1
2304 | 0 | 0.067401 | 1 | 0 | 0 | 1 | 0 | 0.067401 | 1
2305 | 0 | 0.024174 | 1 | 0 | 0 | 1 | 0 | 0.024174 | 1
2306 | 0 | 0.024528 | 1 | 0 | 0 | 1 | 0 | 0.024528 | 1
2307 | 0 | 0.014943 | 1 | 0 | 0 | 1 | 0 | 0.014943 | 1
2308 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2309 | 0 | 0.0038825 | 1 | 0 | 0 | 1 | 0 | 0.0038825 | 1
2310 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2311 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
2312 | 0 | 0.00027731 | 1 | 0 | 0 | 1 | 0 | 0.00027731 | 1
2313 | 0 | 0.022318 | 1 | 0 | 0 | 1 | 0 | 0.022318 | 1
2314 | 0.083208 | 0.049089 | 1 | 0 | 0 | 1 | 0.083208 | 0.049089 | 1
2315 | 0.15716 | 0.077388 | 1 | 0 | 0 | 1 | 0.15716 | 0.077388 | 1
2316 | 0.23401 | 0.10947 | 1 | 0 | 0 | 1 | 0.23401 | 0.10947 | 1
2317 | 0.19185 | 0.13074 | 1 | 0 | 0 | 1 | 0.19185 | 0.13074 | 1
2318 | 0.17585 | 0.13258 | 1 | 0 | 0 | 1 | 0.17585 | 0.13258 | 1
2319 | 0.13903 | 0.14425 | 1 | 0 | 0 | 1 | 0.13903 | 0.14425 | 1
2320 | 0.024931 | 0.1292 | 1 | 0 | 0 | 1 | 0.024931 | 0.1292 | 1
2321 | 0 | 0.087361 | 1 | 0 | 0 | 1 | 0 | 0.087361 | 1
2322 | 0 | 0.057997 | 1 | 0 | 1 | 1 | 0 | 0.057997 | 1
2323 | 0 | 0.021859 | 1 | 0 | 1 | 1 | 0 | 0.021859 | 1
2324 | 0 | 0.036151 | 1 | 0 | 1 | 1 | 0 | 0.036151 | 1
2325 | 0 | 0.047472 | 1 | 0 | 1 | 1 | 0 | 0.047472 | 1
2326 | 0 | 0.05745 | 1 | 0 | 0 | 1 | 0 | 0.05745 | 1
2327 | 0 | 0.045597 | 1 | 0 | 0 | 1 | 0 | 0.045597 | 1
2328 | 0 | 0.081581 | 1 | 0 | 0 | 1 | 0 | 0.081581 | 1
2329 | 0 | 0.045076 | 1 | 0 | 0 | 1 | 0 | 0.045076 | 1
2330 | 0 | 0.040531 | 1 | 0 | 0 | 1 | 0 | 0.040531 | 1
2331 | 0 | 0.02657 | 1 | 0 | 0 | 1 | 0 | 0.02657 | 1
2332 | 0 | 0.016459 | 1 | 0 | 0 | 1 | 0 | 0.016459 | 1
2333 | 0 | 0.021924 | 1 | 0 | 0 | 1 | 0 | 0.021924 | 1
2334 | 0 | 0.0062606 | 1 | 0 | 0 | 1 | 0 | 0.0062606 | 1
2335 | 0 | 0.0073499 | 1 | 0 | 0 | 1 | 0 | 0.0073499 | 1
2336 | 0 | 0.033988 | 1 | 0 | 0 | 1 | 0 | 0.033988 | 1
2337 | 0 | 0.049925 | 1 | 0 | 0 | 1 | 0 | 0.049925 | 1
2338 | 0.075052 | 0.082653 | 1 | 0 | 0 | 1 | 0.075052 | 0.082653 | 1
2339 | 0.21384 | 0.11358 | 1 | 0 | 0 | 1 | 0.21384 | 0.11358 | 1
2340 | 0.20444 | 0.13938 | 1 | 0 | 0 | 1 | 0.20444 | 0.13938 | 1
2341 | 0.2006 | 0.16145 | 1 | 0 | 0 | 1 | 0.2006 | 0.16145 | 1
2342 | 0.17828 | 0.13976 | 1 | 0 | 0 | 1 | 0.17828 | 0.13976 | 1
2343 | 0.14849 | 0.11749 | 1 | 0 | 0 | 1 | 0.14849 | 0.11749 | 1
2344 | 0 | 0.09533 | 1 | 0 | 0 | 1 | 0 | 0.09533 | 1
2345 | 0 | 0.096387 | 1 | 0 | 0 | 1 | 0 | 0.096387 | 1
2346 | 0 | 0.066431 | 1 | 0 | 1 | 1 | 0 | 0.066431 | 1
2347 | 0 | 0.017331 | 1 | 0 | 1 | 1 | 0 | 0.017331 | 1
2348 | 0 | 0.0064971 | 1 | 0 | 1 | 1 | 0 | 0.0064971 | 1
2349 | 0 | 0.031785 | 1 | 0 | 1 | 1 | 0 | 0.031785 | 1
2350 | 0 | 0.049015 | 1 | 0 | 0 | 1 | 0 | 0.049015 | 1
2351 | 0 | 0.036911 | 1 | 0 | 0 | 1 | 0 | 0.036911 | 1
2352 | 0 | 0.064367 | 1 | 0 | 0 | 1 | 0 | 0.064367 | 1
2353 | 0 | 0.064015 | 0.90985 | 0 | 0 | 1 | 0 | 0.064015 | 1
2354 | 0 | 0.0043596 | 0.90985 | 0 | 0 | 1 | 0 | 0.0043596 | 1
2355 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2356 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2357 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2358 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2359 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2360 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2361 | 0.059168 | 0.021839 | 0.90985 | 0 | 0 | 1 | 0.059168 | 0.021839 | 1
2362 | 0.19077 | 0.047364 | 0.90985 | 0 | 0 | 1 | 0.19077 | 0.047364 | 1
2363 | 0.33398 | 0.065406 | 0.90985 | 0 | 0 | 1 | 0.33398 | 0.065406 | 1
2364 | 0.27227 | 0.092165 | 0.90985 | 0 | 0 | 1 | 0.27227 | 0.092165 | 1
2365 | 0.19669 | 0.13254 | 0.90985 | 0 | 0 | 1 | 0.19669 | 0.13254 | 1
2366 | 0.29183 | 0.13046 | 0.90985 | 0 | 0 | 1 | 0.29183 | 0.13046 | 1
2367 | 0.22225 | 0.12438 | 0.90985 | 0 | 0 | 1 | 0.22225 | 0.12438 | 1
2368 | 0.022837 | 0.12066 | 0.90985 | 0 | 0 | 1 | 0.022837 | 0.12066 | 1
2369 | 0.0075137 | 0.12481 | 0.90985 | 0 | 0 | 1 | 0.0075137 | 0.12481 | 1
2370 | 0 | 0.099706 | 0.90985 | 0 | 1 | 1 | 0 | 0.099706 | 1
2371 | 0 | 0.054794 | 0.90985 | 0 | 1 | 1 | 0 | 0.054794 | 1
2372 | 0 | 0.051816 | 0.90985 | 0 | 1 | 1 | 0 | 0.051816 | 1
2373 | 0 | 0.055121 | 0.90985 | 0 | 1 | 1 | 0 | 0.055121 | 1
2374 | 0 | 0.10627 | 0.90985 | 0 | 0 | 1 | 0 | 0.10627 | 1
2375 | 0 | 0.09519 | 0.90985 | 0 | 0 | 1 | 0 | 0.09519 | 1
2376 | 0 | 0.095778 | 0.90985 | 0 | 0 | 1 | 0 | 0.095778 | 1
2377 | 0 | 0.0355 | 0.90985 | 0 | 0 | 1 | 0 | 0.0355 | 1
2378 | 0 | 0.015288 | 0.90985 | 0 | 0 | 1 | 0 | 0.015288 | 1
2379 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2380 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2381 | 0 | 0 | 0.90985 | 0 | 0 | 1 | 0 | 0 | 1
2382 | 0 | 0.004626 | 0.90985 | 0 | 0 | 1 | 0 | 0.004626 | 1
2383 | 0 | 0.014385 | 0.90985 | 0 | 0 | 1 | 0 | 0.014385 | 1
2384 | 0.0017091 | 0.030197 | 0.90985 | 0 | 0 | 1 | 0.0017091 | 0.030197 | 1
2385 | 0.14667 | 0.042644 | 0.90985 | 0 | 0 | 1 | 0.14667 | 0.042644 | 1
2386 | 0.28582 | 0.065504 | 0.90985 | 0 | 0 | 1 | 0.28582 | 0.065504 | 1
2387 | 0.35114 | 0.091689 | 0.90985 | 0 | 0 | 1 | 0.35114 | 0.091689 | 1
2388 | 0.36425 | 0.10671 | 0.90985 | 0 | 0 | 1 | 0.36425 | 0.10671 | 1
2389 | 0.32322 | 0.14315 | 0.90985 | 0 | 0 | 1 | 0.32322 | 0.14315 | 1
2390 | 0.34199 | 0.13775 | 0.90985 | 0 | 0 | 1 | 0.34199 | 0.13775 | 1
2391 | 0.20128 | 0.12124 | 0.90985 | 0 | 0 | 1 | 0.20128 | 0.12124 | 1
2392 | 0.094535 | 0.12606 | 0.90985 | 0 | 0 | 1 | 0.094535 | 0.12606 | 1
2393 | 0.024961 | 0.15245 | 0.90985 | 0 | 0 | 1 | 0.024961 | 0.15245 | 1
2394 | 0 | 0.14978 | 0.90985 | 0 | 1 | 1 | 0 | 0.14978 | 1
2395 | 0 | 0.1159 | 0.90985 | 0 | 1 | 1 | 0 | 0.1159 | 1
2396 | 0 | 0.0845 | 0.90985 | 0 | 1 | 1 | 0 | 0.0845 | 1
2397 | 0 | 0.062917 | 0.90985 | 0 | 1 | 1 | 0 | 0.062917 | 1
2398 | 0 | 0.10183 | 0.90985 | 0 | 0 | 1 | 0 | 0.10183 | 1
2399 | 0 | 0.089255 | 0.90985 | 0 | 0 | 1 | 0 | 0.089255 | 1
2400 | 0 | 0.070832 | 0.90985 | 0 | 0 | 1 | 0 | 0.070832 | 1
2401 | 0 | 0.0663 | 0.90985 | 0 | 0 | 1 | 0 | 0.0663 | 1
2402 | 0 | 0.010523 | 0.90985 | 0 | 0 | 1 | 0 | 0.010523 | 1
2403 | 0 | 0.0032781 | 0.90985 | 0 | 0 | 1 | 0 | 0.0032781 | 1
2404 | 0 | 0.0045142 | 0.90985 | 0 | 0 | 1 | 0 | 0.0045142 | 1
2405 | 0 | 0.0067279 | 0.90985 | 0 | 0 | 1 | 0 | 0.0067279 | 1
2406 | 0 | 0.022007 | 0.90985 | 0 | 0 | 1 | 0 | 0.022007 | 1
2407 | 0 | 0.030775 | 0.90985 | 0 | 0 | 1 | 0 | 0.030775 | 1
2408 | 0 | 0.034641 | 0.90985 | 0 | 0 | 1 | 0 | 0.034641 | 1
2409 | 0.098678 | 0.048215 | 0.90985 | 0 | 0 | 1 | 0.098678 | 0.048215 | 1
2410 | 0.26865 | 0.078368 | 0.90985 | 0 | 0 | 1 | 0.26865 | 0.078368 | 1
2411 | 0.27838 | 0.097618 | 0.90985 | 0 | 0 | 1 | 0.27838 | 0.097618 | 1
2412 | 0.29738 | 0.1148 | 0.90985 | 0 | 0 | 1 | 0.29738 | 0.1148 | 1
2413 | 0.24548 | 0.15139 | 0.90985 | 0 | 0 | 1 | 0.24548 | 0.15139 | 1
2414 | 0.34476 | 0.16335 | 0.90985 | 0 | 0 | 1 | 0.34476 | 0.16335 | 1
2415 | 0.17577 | 0.15514 | 0.90985 | 0 | 0 | 1 | 0.17577 | 0.15514 | 1
2416 | 0.13418 | 0.15363 | 0.90985 | 0 | 0 | 1 | 0.13418 | 0.15363 | 1
2417 | 0 | 0.16755 | 0.90985 | 0 | 0 | 1 | 0 | 0.16755 | 1
2418 | 0 | 0.15801 | 0.90985 | 0 | 1 | 1 | 0 | 0.15801 | 1
2419 | 0 | 0.12747 | 0.90985 | 0 | 1 | 1 | 0 | 0.12747 | 1
2420 | 0 | 0.12412 | 0.90985 | 0 | 1 | 1 | 0 | 0.12412 | 1
2421 | 0 | 0.095267 | 0.90985 | 0 | 1 | 1 | 0 | 0.095267 | 1
2422 | 0 | 0.11724 | 0.90985 | 0 | 0 | 1 | 0 | 0.11724 | 1
2423 | 0 | 0.088174 | 0.90985 | 0 | 0 | 1 | 0 | 0.088174 | 1
2424 | 0 | 0.053163 | 0.90985 | 0 | 0 | 1 | 0 | 0.053163 | 1
2425 | 0 | 0.063662 | 0.90985 | 0 | 0 | 1 | 0 | 0.063662 | 1
2426 | 0 | 0.018148 | 0.90985 | 0 | 0 | 1 | 0 | 0.018148 | 1
2427 | 0 | 0.016202 | 0.90985 | 0 | 0 | 1 | 0 | 0.016202 | 1
2428 | 0 | 0.010028 | 0.90985 | 0 | 0 | 1 | 0 | 0.010028 | 1
2429 | 0 | 0.027418 | 0.90985 | 0 | 0 | 1 | 0 | 0.027418 | 1
2430 | 0 | 0.044732 | 0.90985 | 0 | 0 | 1 | 0 | 0.044732 | 1
2431 | 0 | 0.064489 | 0.90985 | 0 | 0 | 1 | 0 | 0.064489 | 1
2432 | 0 | 0.084046 | 0.90985 | 0 | 0 | 1 | 0 | 0.084046 | 1
2433 | 0.09473 | 0.10227 | 0.90985 | 0 | 0 | 1 | 0.09473 | 0.10227 | 1
2434 | 0.27002 | 0.14961 | 0.90985 | 0 | 0 | 1 | 0.27002 | 0.14961 | 1
2435 | 0.3129 | 0.15748 | 0.90985 | 0 | 0 | 1 | 0.3129 | 0.15748 | 1
2436 | 0.29959 | 0.17742 | 0.90985 | 0 | 0 | 1 | 0.29959 | 0.17742 | 1
2437 | 0.32627 | 0.18513 | 0.90985 | 0 | 0 | 1 | 0.32627 | 0.18513 | 1
2438 | 0.33326 | 0.18635 | 0.90985 | 0 | 0 | 1 | 0.33326 | 0.18635 | 1
2439 | 0.21061 | 0.18491 | 0.90985 | 0 | 0 | 1 | 0.21061 | 0.18491 | 1
2440 | 0.14181 | 0.15938 | 0.90985 | 0 | 0 | 1 | 0.14181 | 0.15938 | 1
2441 | 0 | 0.17304 | 0.90985 | 0 | 0 | 1 | 0 | 0.17304 | 1
2442 | 0 | 0.15364 | 0.90985 | 0 | 1 | 1 | 0 | 0.15364 | 1
2443 | 0 | 0.12604 | 0.90985 | 0 | 1 | 1 | 0 | 0.12604 | 1
2444 | 0 | 0.11373 | 0.90985 | 0 | 1 | 1 | 0 | 0.11373 | 1
2445 | 0 | 0.07783 | 0.90985 | 0 | 1 | 1 | 0 | 0.07783 | 1
2446 | 0 | 0.070559 | 0.90985 | 0 | 0 | 1 | 0 | 0.070559 | 1
2447 | 0 | 0.064778 | 0.90985 | 0 | 0 | 1 | 0 | 0.064778 | 1
2448 | 0 | 0.059422 | 0.90985 | 0 | 0 | 1 | 0 | 0.059422 | 1
2449 | 0 | 0.051183 | 0.90985 | 0 | 0 | 1 | 0 | 0.051183 | 1
2450 | 0 | 0.033974 | 0.90985 | 0 | 0 | 1 | 0 | 0.033974 | 1
2451 | 0 | 0.028596 | 0.90985 | 0 | 0 | 1 | 0 | 0.028596 | 1
2452 | 0 | 0.026094 | 0.90985 | 0 | 0 | 1 | 0 | 0.026094 | 1
2453 | 0 | 0.04299 | 0.90985 | 0 | 0 | 1 | 0 | 0.04299 | 1
2454 | 0 | 0.065207 | 0.90985 | 0 | 0 | 1 | 0 | 0.065207 | 1
2455 | 0 | 0.084821 | 0.90985 | 0 | 0 | 1 | 0 | 0.084821 | 1
2456 | 0 | 0.097958 | 0.90985 | 0 | 0 | 1 | 0 | 0.097958 | 1
2457 | 0.052023 | 0.11579 | 0.90985 | 0 | 0 | 1 | 0.052023 | 0.11579 | 1
2458 | 0.26997 | 0.15946 | 0.90985 | 0 | 0 | 1 | 0.26997 | 0.15946 | 1
2459 | 0.31163 | 0.17265 | 0.90985 | 0 | 0 | 1 | 0.31163 | 0.17265 | 1
2460 | 0.24298 | 0.18661 | 0.90985 | 0 | 0 | 1 | 0.24298 | 0.18661 | 1
2461 | 0.14222 | 0.19105 | 0.90985 | 0 | 0 | 1 | 0.14222 | 0.19105 | 1
2462 | 0.17986 | 0.20715 | 0.90985 | 0 | 0 | 1 | 0.17986 | 0.20715 | 1
2463 | 0.18105 | 0.21865 | 0.90985 | 0 | 0 | 1 | 0.18105 | 0.21865 | 1
2464 | 0.046102 | 0.18028 | 0.90985 | 0 | 0 | 1 | 0.046102 | 0.18028 | 1
2465 | 0 | 0.17881 | 0.90985 | 0 | 0 | 1 | 0 | 0.17881 | 1
2466 | 0 | 0.15563 | 0.90985 | 0 | 1 | 1 | 0 | 0.15563 | 1
2467 | 0 | 0.11389 | 0.90985 | 0 | 1 | 1 | 0 | 0.11389 | 1
2468 | 0 | 0.12279 | 0.90985 | 0 | 1 | 1 | 0 | 0.12279 | 1
2469 | 0 | 0.11844 | 0.90985 | 0 | 1 | 1 | 0 | 0.11844 | 1
2470 | 0 | 0.11483 | 0.90985 | 0 | 0 | 1 | 0 | 0.11483 | 1
2471 | 0 | 0.13354 | 0.90985 | 0 | 0 | 1 | 0 | 0.13354 | 1
2472 | 0 | 0.12713 | 0.90985 | 0 | 0 | 1 | 0 | 0.12713 | 1
2473 | 0 | 0.074609 | 0.90985 | 0 | 0 | 1 | 0 | 0.074609 | 1
2474 | 0 | 0.076532 | 0.90985 | 0 | 0 | 1 | 0 | 0.076532 | 1
2475 | 0 | 0.044773 | 0.90985 | 0 | 0 | 1 | 0 | 0.044773 | 1
2476 | 0 | 0.043595 | 0.90985 | 0 | 0 | 1 | 0 | 0.043595 | 1
2477 | 0 | 0.032812 | 0.90985 | 0 | 0 | 1 | 0 | 0.032812 | 1
2478 | 0 | 0.036052 | 0.90985 | 0 | 0 | 1 | 0 | 0.036052 | 1
2479 | 0 | 0.075436 | 0.90985 | 0 | 0 | 1 | 0 | 0.075436 | 1
2480 | 0 | 0.096883 | 0.90985 | 0 | 0 | 1 | 0 | 0.096883 | 1
2481 | 0.074245 | 0.10081 | 0.90985 | 0 | 0 | 1 | 0.074245 | 0.10081 | 1
2482 | 0.27929 | 0.15492 | 0.90985 | 0 | 0 | 1 | 0.27929 | 0.15492 | 1
2483 | 0.31771 | 0.1718 | 0.90985 | 0 | 0 | 1 | 0.31771 | 0.1718 | 1
2484 | 0.27763 | 0.19217 | 0.90985 | 0 | 0 | 1 | 0.27763 | 0.19217 | 1
2485 | 0.1674 | 0.20461 | 0.90985 | 0 | 0 | 1 | 0.1674 | 0.20461 | 1
2486 | 0.21296 | 0.21427 | 0.90985 | 0 | 0 | 1 | 0.21296 | 0.21427 | 1
2487 | 0.17939 | 0.20631 | 0.90985 | 0 | 0 | 1 | 0.17939 | 0.20631 | 1
2488 | 0.043389 | 0.18587 | 0.90985 | 0 | 0 | 1 | 0.043389 | 0.18587 | 1
2489 | 0 | 0.17333 | 0.90985 | 0 | 0 | 1 | 0 | 0.17333 | 1
2490 | 0 | 0.16043 | 0.90985 | 0 | 1 | 1 | 0 | 0.16043 | 1
2491 | 0 | 0.13795 | 0.90985 | 0 | 1 | 1 | 0 | 0.13795 | 1
2492 | 0 | 0.13473 | 0.90985 | 0 | 1 | 1 | 0 | 0.13473 | 1
2493 | 0 | 0.10723 | 0.90985 | 0 | 1 | 1 | 0 | 0.10723 | 1
2494 | 0 | 0.10221 | 0.90985 | 0 | 0 | 1 | 0 | 0.10221 | 1
2495 | 0 | 0.14451 | 0.90985 | 0 | 0 | 1 | 0 | 0.14451 | 1
2496 | 0 | 0.14641 | 0.90985 | 0 | 0 | 1 | 0 | 0.14641 | 1
2497 | 0 | 0.11655 | 0.96684 | 0 | 0 | 1 | 0 | 0.11655 | 1
2498 | 0 | 0.075785 | 0.96684 | 0 | 0 | 1 | 0 | 0.075785 | 1
2499 | 0 | 0.038143 | 0.96684 | 0 | 0 | 1 | 0 | 0.038143 | 1
2500 | 0 | 0.042516 | 0.96684 | 0 | 0 | 1 | 0 | 0.042516 | 1
2501 | 0 | 0.019778 | 0.96684 | 0 | 0 | 1 | 0 | 0.019778 | 1
2502 | 0 | 0.0077073 | 0.96684 | 0 | 0 | 1 | 0 | 0.0077073 | 1
2503 | 0 | 0.036761 | 0.96684 | 0 | 0 | 1 | 0 | 0.036761 | 1
2504 | 0 | 0.037756 | 0.96684 | 0 | 0 | 1 | 0 | 0.037756 | 1
2505 | 0.070743 | 0.037732 | 0.96684 | 0 | 0 | 1 | 0.070743 | 0.037732 | 1
2506 | 0.25256 | 0.07298 | 0.96684 | 0 | 0 | 1 | 0.25256 | 0.07298 | 1
2507 | 0.20115 | 0.10517 | 0.96684 | 0 | 0 | 1 | 0.20115 | 0.10517 | 1
2508 | 0.21628 | 0.12402 | 0.96684 | 0 | 0 | 1 | 0.21628 | 0.12402 | 1
2509 | 0.134 | 0.14235 | 0.96684 | 0 | 0 | 1 | 0.134 | 0.14235 | 1
2510 | 0.16095 | 0.15116 | 0.96684 | 0 | 0 | 1 | 0.16095 | 0.15116 | 1
2511 | 0.16781 | 0.14361 | 0.96684 | 0 | 0 | 1 | 0.16781 | 0.14361 | 1
2512 | 0.071537 | 0.15498 | 0.96684 | 0 | 0 | 1 | 0.071537 | 0.15498 | 1
2513 | 0 | 0.15239 | 0.96684 | 0 | 0 | 1 | 0 | 0.15239 | 1
2514 | 0 | 0.14648 | 0.96684 | 0 | 1 | 1 | 0 | 0.14648 | 1
2515 | 0 | 0.1163 | 0.96684 | 0 | 1 | 1 | 0 | 0.1163 | 1
2516 | 0 | 0.10527 | 0.96684 | 0 | 1 | 1 | 0 | 0.10527 | 1
2517 | 0 | 0.11924 | 0.96684 | 0 | 1 | 1 | 0 | 0.11924 | 1
2518 | 0 | 0.13088 | 0.96684 | 0 | 0 | 1 | 0 | 0.13088 | 1
2519 | 0 | 0.15402 | 0.96684 | 0 | 0 | 1 | 0 | 0.15402 | 1
2520 | 0 | 0.13406 | 0.96684 | 0 | 0 | 1 | 0 | 0.13406 | 1
2521 | 0 | 0.1254 | 0.96684 | 0 | 0 | 1 | 0 | 0.1254 | 1
2522 | 0 | 0.087458 | 0.96684 | 0 | 0 | 1 | 0 | 0.087458 | 1
2523 | 0 | 0.056885 | 0.96684 | 0 | 0 | 1 | 0 | 0.056885 | 1
2524 | 0 | 0.04894 | 0.96684 | 0 | 0 | 1 | 0 | 0.04894 | 1
2525 | 0 | 0.023882 | 0.96684 | 0 | 0 | 1 | 0 | 0.023882 | 1
2526 | 0 | 0.015982 | 0.96684 | 0 | 0 | 1 | 0 | 0.015982 | 1
2527 | 0 | 0.054905 | 0.96684 | 0 | 0 | 1 | 0 | 0.054905 | 1
2528 | 0 | 0.068242 | 0.96684 | 0 | 0 | 1 | 0 | 0.068242 | 1
2529 | 0.060846 | 0.05683 | 0.96684 | 0 | 0 | 1 | 0.060846 | 0.05683 | 1
2530 | 0.17739 | 0.093415 | 0.96684 | 0 | 0 | 1 | 0.17739 | 0.093415 | 1
2531 | 0.17188 | 0.12131 | 0.96684 | 0 | 0 | 1 | 0.17188 | 0.12131 | 1
2532 | 0.23669 | 0.15855 | 0.96684 | 0 | 0 | 1 | 0.23669 | 0.15855 | 1
2533 | 0.26238 | 0.18336 | 0.96684 | 0 | 0 | 1 | 0.26238 | 0.18336 | 1
2534 | 0.25661 | 0.19364 | 0.96684 | 0 | 0 | 1 | 0.25661 | 0.19364 | 1
2535 | 0.19533 | 0.17474 | 0.96684 | 0 | 0 | 1 | 0.19533 | 0.17474 | 1
2536 | 0.11595 | 0.18479 | 0.96684 | 0 | 0 | 1 | 0.11595 | 0.18479 | 1
2537 | 0.010514 | 0.17479 | 0.96684 | 0 | 0 | 1 | 0.010514 | 0.17479 | 1
2538 | 0 | 0.15878 | 0.96684 | 0 | 1 | 1 | 0 | 0.15878 | 1
2539 | 0 | 0.14353 | 0.96684 | 0 | 1 | 1 | 0 | 0.14353 | 1
2540 | 0 | 0.14732 | 0.96684 | 0 | 1 | 1 | 0 | 0.14732 | 1
2541 | 0 | 0.15379 | 0.96684 | 0 | 1 | 1 | 0 | 0.15379 | 1
2542 | 0 | 0.1595 | 0.96684 | 0 | 0 | 1 | 0 | 0.1595 | 1
2543 | 0 | 0.19169 | 0.96684 | 0 | 0 | 1 | 0 | 0.19169 | 1
2544 | 0 | 0.17827 | 0.96684 | 0 | 0 | 1 | 0 | 0.17827 | 1
2545 | 0 | 0.1132 | 0.91049 | 0 | 0 | 1 | 0 | 0.1132 | 1
2546 | 0 | 0.11991 | 0.91049 | 0 | 0 | 1 | 0 | 0.11991 | 1
2547 | 0 | 0.11284 | 0.91049 | 0 | 0 | 1 | 0 | 0.11284 | 1
2548 | 0 | 0.076137 | 0.91049 | 0 | 0 | 1 | 0 | 0.076137 | 1
2549 | 0 | 0.054341 | 0.91049 | 0 | 0 | 1 | 0 | 0.054341 | 1
2550 | 0 | 0.061872 | 0.91049 | 0 | 0 | 1 | 0 | 0.061872 | 1
2551 | 0 | 0.097007 | 0.91049 | 0 | 0 | 1 | 0 | 0.097007 | 1
2552 | 0 | 0.11738 | 0.91049 | 0 | 0 | 1 | 0 | 0.11738 | 1
2553 | 0.051209 | 0.10241 | 0.91049 | 0 | 0 | 1 | 0.051209 | 0.10241 | 1
2554 | 0.18802 | 0.14131 | 0.91049 | 0 | 0 | 1 | 0.18802 | 0.14131 | 1
2555 | 0.18725 | 0.1696 | 0.91049 | 0 | 0 | 1 | 0.18725 | 0.1696 | 1
2556 | 0.24517 | 0.20334 | 0.91049 | 0 | 0 | 1 | 0.24517 | 0.20334 | 1
2557 | 0.30074 | 0.22562 | 0.91049 | 0 | 0 | 1 | 0.30074 | 0.22562 | 1
2558 | 0.22736 | 0.2411 | 0.91049 | 0 | 0 | 1 | 0.22736 | 0.2411 | 1
2559 | 0.19954 | 0.22962 | 0.91049 | 0 | 0 | 1 | 0.19954 | 0.22962 | 1
2560 | 0.10829 | 0.2299 | 0.91049 | 0 | 0 | 1 | 0.10829 | 0.2299 | 1
2561 | 0.013694 | 0.21586 | 0.91049 | 0 | 0 | 1 | 0.013694 | 0.21586 | 1
2562 | 0 | 0.20003 | 0.91049 | 0 | 1 | 1 | 0 | 0.20003 | 1
2563 | 0 | 0.17293 | 0.91049 | 0 | 1 | 1 | 0 | 0.17293 | 1
2564 | 0 | 0.15635 | 0.91049 | 0 | 1 | 1 | 0 | 0.15635 | 1
2565 | 0 | 0.16429 | 0.91049 | 0 | 1 | 1 | 0 | 0.16429 | 1
2566 | 0 | 0.18404 | 0.91049 | 0 | 0 | 1 | 0 | 0.18404 | 1
2567 | 0 | 0.18872 | 0.91049 | 0 | 0 | 1 | 0 | 0.18872 | 1
2568 | 0 | 0.17367 | 0.91049 | 0 | 0 | 1 | 0 | 0.17367 | 1
2569 | 0 | 0.13955 | 0.91049 | 0 | 0 | 1 | 0 | 0.13955 | 1
2570 | 0 | 0.12051 | 0.91049 | 0 | 0 | 1 | 0 | 0.12051 | 1
2571 | 0 | 0.1377 | 0.91049 | 0 | 0 | 1 | 0 | 0.1377 | 1
2572 | 0 | 0.076636 | 0.91049 | 0 | 0 | 1 | 0 | 0.076636 | 1
2573 | 0 | 0.059227 | 0.91049 | 0 | 0 | 1 | 0 | 0.059227 | 1
2574 | 0 | 0.061817 | 0.91049 | 0 | 0 | 1 | 0 | 0.061817 | 1
2575 | 0 | 0.095127 | 0.91049 | 0 | 0 | 1 | 0 | 0.095127 | 1
2576 | 0 | 0.14872 | 0.91049 | 0 | 0 | 1 | 0 | 0.14872 | 1
2577 | 0.010733 | 0.15314 | 0.91049 | 0 | 0 | 1 | 0.010733 | 0.15314 | 1
2578 | 0.14562 | 0.19193 | 0.91049 | 0 | 0 | 1 | 0.14562 | 0.19193 | 1
2579 | 0.21342 | 0.21771 | 0.91049 | 0 | 0 | 1 | 0.21342 | 0.21771 | 1
2580 | 0.25026 | 0.23657 | 0.91049 | 0 | 0 | 1 | 0.25026 | 0.23657 | 1
2581 | 0.29857 | 0.25782 | 0.91049 | 0 | 0 | 1 | 0.29857 | 0.25782 | 1
2582 | 0.26847 | 0.27669 | 0.91049 | 0 | 0 | 1 | 0.26847 | 0.27669 | 1
2583 | 0.1937 | 0.26701 | 0.91049 | 0 | 0 | 1 | 0.1937 | 0.26701 | 1
2584 | 0.1128 | 0.24655 | 0.91049 | 0 | 0 | 1 | 0.1128 | 0.24655 | 1
2585 | 0.0050736 | 0.21002 | 0.91049 | 0 | 0 | 1 | 0.0050736 | 0.21002 | 1
2586 | 0 | 0.21978 | 0.91049 | 0 | 1 | 1 | 0 | 0.21978 | 1
2587 | 0 | 0.19096 | 0.91049 | 0 | 1 | 1 | 0 | 0.19096 | 1
2588 | 0 | 0.17971 | 0.91049 | 0 | 1 | 1 | 0 | 0.17971 | 1
2589 | 0 | 0.16685 | 0.91049 | 0 | 1 | 1 | 0 | 0.16685 | 1
2590 | 0 | 0.18035 | 0.91049 | 0 | 0 | 1 | 0 | 0.18035 | 1
2591 | 0 | 0.17234 | 0.91049 | 0 | 0 | 1 | 0 | 0.17234 | 1
2592 | 0 | 0.16192 | 0.91049 | 0 | 0 | 1 | 0 | 0.16192 | 1
2593 | 0 | 0.14073 | 0.91049 | 0 | 0 | 1 | 0 | 0.14073 | 1
2594 | 0 | 0.11027 | 0.91049 | 0 | 0 | 1 | 0 | 0.11027 | 1
2595 | 0 | 0.14127 | 0.91049 | 0 | 0 | 1 | 0 | 0.14127 | 1
2596 | 0 | 0.080378 | 0.91049 | 0 | 0 | 1 | 0 | 0.080378 | 1
2597 | 0 | 0.052685 | 0.91049 | 0 | 0 | 1 | 0 | 0.052685 | 1
2598 | 0 | 0.052355 | 0.91049 | 0 | 0 | 1 | 0 | 0.052355 | 1
2599 | 0 | 0.066986 | 0.91049 | 0 | 0 | 1 | 0 | 0.066986 | 1
2600 | 0 | 0.11038 | 0.91049 | 0 | 0 | 1 | 0 | 0.11038 | 1
2601 | 0.0095824 | 0.1146 | 0.91049 | 0 | 0 | 1 | 0.0095824 | 0.1146 | 1
2602 | 0.11112 | 0.14849 | 0.91049 | 0 | 0 | 1 | 0.11112 | 0.14849 | 1
2603 | 0.21694 | 0.16427 | 0.91049 | 0 | 0 | 1 | 0.21694 | 0.16427 | 1
2604 | 0.2744 | 0.17071 | 0.91049 | 0 | 0 | 1 | 0.2744 | 0.17071 | 1
2605 | 0.3273 | 0.19197 | 0.91049 | 0 | 0 | 1 | 0.3273 | 0.19197 | 1
2606 | 0.29527 | 0.19786 | 0.91049 | 0 | 0 | 1 | 0.29527 | 0.19786 | 1
2607 | 0.22886 | 0.20075 | 0.91049 | 0 | 0 | 1 | 0.22886 | 0.20075 | 1
2608 | 0.099209 | 0.18383 | 0.91049 | 0 | 0 | 1 | 0.099209 | 0.18383 | 1
2609 | 0 | 0.16948 | 0.91049 | 0 | 0 | 1 | 0 | 0.16948 | 1
2610 | 0 | 0.19916 | 0.91049 | 0 | 1 | 1 | 0 | 0.19916 | 1
2611 | 0 | 0.17663 | 0.91049 | 0 | 1 | 1 | 0 | 0.17663 | 1
2612 | 0 | 0.16257 | 0.91049 | 0 | 1 | 1 | 0 | 0.16257 | 1
2613 | 0 | 0.14321 | 0.91049 | 0 | 1 | 1 | 0 | 0.14321 | 1
2614 | 0 | 0.15287 | 0.91049 | 0 | 0 | 1 | 0 | 0.15287 | 1
2615 | 0 | 0.12156 | 0.91049 | 0 | 0 | 1 | 0 | 0.12156 | 1
2616 | 0 | 0.096349 | 0.91049 | 0 | 0 | 1 | 0 | 0.096349 | 1
2617 | 0 | 0.11834 | 0.91049 | 0 | 0 | 1 | 0 | 0.11834 | 1
2618 | 0 | 0.071861 | 0.91049 | 0 | 0 | 1 | 0 | 0.071861 | 1
2619 | 0 | 0.091257 | 0.91049 | 0 | 0 | 1 | 0 | 0.091257 | 1
2620 | 0 | 0.072341 | 0.91049 | 0 | 0 | 1 | 0 | 0.072341 | 1
2621 | 0 | 0.050156 | 0.91049 | 0 | 0 | 1 | 0 | 0.050156 | 1
2622 | 0 | 0.048205 | 0.91049 | 0 | 0 | 1 | 0 | 0.048205 | 1
2623 | 0 | 0.055295 | 0.91049 | 0 | 0 | 1 | 0 | 0.055295 | 1
2624 | 0 | 0.088005 | 0.91049 | 0 | 0 | 1 | 0 | 0.088005 | 1
2625 | 0.005249 | 0.10621 | 0.91049 | 0 | 0 | 1 | 0.005249 | 0.10621 | 1
2626 | 0.094965 | 0.10859 | 0.91049 | 0 | 0 | 1 | 0.094965 | 0.10859 | 1
2627 | 0.17381 | 0.10787 | 0.91049 | 0 | 0 | 1 | 0.17381 | 0.10787 | 1
2628 | 0.27337 | 0.11941 | 0.91049 | 0 | 0 | 1 | 0.27337 | 0.11941 | 1
2629 | 0.29907 | 0.15302 | 0.91049 | 0 | 0 | 1 | 0.29907 | 0.15302 | 1
2630 | 0.23784 | 0.15108 | 0.91049 | 0 | 0 | 1 | 0.23784 | 0.15108 | 1
2631 | 0.16097 | 0.16896 | 0.91049 | 0 | 0 | 1 | 0.16097 | 0.16896 | 1
2632 | 0.028439 | 0.17068 | 0.91049 | 0 | 0 | 1 | 0.028439 | 0.17068 | 1
2633 | 0 | 0.1711 | 0.91049 | 0 | 0 | 1 | 0 | 0.1711 | 1
2634 | 0 | 0.19297 | 0.91049 | 0 | 1 | 1 | 0 | 0.19297 | 1
2635 | 0 | 0.16918 | 0.91049 | 0 | 1 | 1 | 0 | 0.16918 | 1
2636 | 0 | 0.18232 | 0.91049 | 0 | 1 | 1 | 0 | 0.18232 | 1
2637 | 0 | 0.16316 | 0.91049 | 0 | 1 | 1 | 0 | 0.16316 | 1
2638 | 0 | 0.16839 | 0.91049 | 0 | 0 | 1 | 0 | 0.16839 | 1
2639 | 0 | 0.15343 | 0.91049 | 0 | 0 | 1 | 0 | 0.15343 | 1
2640 | 0 | 0.13916 | 0.91049 | 0 | 0 | 1 | 0 | 0.13916 | 1
2641 | 0 | 0.072419 | 0.91049 | 0 | 0 | 1 | 0 | 0.072419 | 1
2642 | 0 | 0.094506 | 0.91049 | 0 | 0 | 1 | 0 | 0.094506 | 1
2643 | 0 | 0.084306 | 0.91049 | 0 | 0 | 1 | 0 | 0.084306 | 1
2644 | 0 | 0.078697 | 0.91049 | 0 | 0 | 1 | 0 | 0.078697 | 1
2645 | 0 | 0.067331 | 0.91049 | 0 | 0 | 1 | 0 | 0.067331 | 1
2646 | 0 | 0.072546 | 0.91049 | 0 | 0 | 1 | 0 | 0.072546 | 1
2647 | 0 | 0.069756 | 0.91049 | 0 | 0 | 1 | 0 | 0.069756 | 1
2648 | 0 | 0.078634 | 0.91049 | 0 | 0 | 1 | 0 | 0.078634 | 1
2649 | 0.026858 | 0.10731 | 0.91049 | 0 | 0 | 1 | 0.026858 | 0.10731 | 1
2650 | 0.1148 | 0.13328 | 0.91049 | 0 | 0 | 1 | 0.1148 | 0.13328 | 1
2651 | 0.20234 | 0.12166 | 0.91049 | 0 | 0 | 1 | 0.20234 | 0.12166 | 1
2652 | 0.30912 | 0.15 | 0.91049 | 0 | 0 | 1 | 0.30912 | 0.15 | 1
2653 | 0.32245 | 0.16685 | 0.91049 | 0 | 0 | 1 | 0.32245 | 0.16685 | 1
2654 | 0.20958 | 0.16565 | 0.91049 | 0 | 0 | 1 | 0.20958 | 0.16565 | 1
2655 | 0.19088 | 0.17478 | 0.91049 | 0 | 0 | 1 | 0.19088 | 0.17478 | 1
2656 | 0.0088931 | 0.15142 | 0.91049 | 0 | 0 | 1 | 0.0088931 | 0.15142 | 1
2657 | 0 | 0.16154 | 0.91049 | 0 | 0 | 1 | 0 | 0.16154 | 1
2658 | 0 | 0.18439 | 0.91049 | 0 | 1 | 1 | 0 | 0.18439 | 1
2659 | 0 | 0.18171 | 0.91049 | 0 | 1 | 1 | 0 | 0.18171 | 1
2660 | 0 | 0.19757 | 0.91049 | 0 | 1 | 1 | 0 | 0.19757 | 1
2661 | 0 | 0.17011 | 0.91049 | 0 | 1 | 1 | 0 | 0.17011 | 1
2662 | 0 | 0.16863 | 0.91049 | 0 | 0 | 1 | 0 | 0.16863 | 1
2663 | 0 | 0.15747 | 0.91049 | 0 | 0 | 1 | 0 | 0.15747 | 1
2664 | 0 | 0.15042 | 0.91049 | 0 | 0 | 1 | 0 | 0.15042 | 1
2665 | 0 | 0.10348 | 0.91049 | 0 | 0 | 1 | 0 | 0.10348 | 1
2666 | 0 | 0.078595 | 0.91049 | 0 | 0 | 1 | 0 | 0.078595 | 1
2667 | 0 | 0.064601 | 0.91049 | 0 | 0 | 1 | 0 | 0.064601 | 1
2668 | 0 | 0.060875 | 0.91049 | 0 | 0 | 1 | 0 | 0.060875 | 1
2669 | 0 | 0.069953 | 0.91049 | 0 | 0 | 1 | 0 | 0.069953 | 1
2670 | 0 | 0.0513 | 0.91049 | 0 | 0 | 1 | 0 | 0.0513 | 1
2671 | 0 | 0.036693 | 0.91049 | 0 | 0 | 1 | 0 | 0.036693 | 1
2672 | 0 | 0.04362 | 0.91049 | 0 | 0 | 1 | 0 | 0.04362 | 1
2673 | 0.061361 | 0.0736 | 0.91049 | 0 | 0 | 1 | 0.061361 | 0.0736 | 1
2674 | 0.19974 | 0.10304 | 0.91049 | 0 | 0 | 1 | 0.19974 | 0.10304 | 1
2675 | 0.24849 | 0.10716 | 0.91049 | 0 | 0 | 1 | 0.24849 | 0.10716 | 1
2676 | 0.33792 | 0.13574 | 0.91049 | 0 | 0 | 1 | 0.33792 | 0.13574 | 1
2677 | 0.32615 | 0.14037 | 0.91049 | 0 | 0 | 1 | 0.32615 | 0.14037 | 1
2678 | 0.17034 | 0.14095 | 0.91049 | 0 | 0 | 1 | 0.17034 | 0.14095 | 1
2679 | 0.11481 | 0.1455 | 0.91049 | 0 | 0 | 1 | 0.11481 | 0.1455 | 1
2680 | 0.040364 | 0.094257 | 0.91049 | 0 | 0 | 1 | 0.040364 | 0.094257 | 1
2681 | 0 | 0.12938 | 0.91049 | 0 | 0 | 1 | 0 | 0.12938 | 1
2682 | 0 | 0.17299 | 0.91049 | 0 | 1 | 1 | 0 | 0.17299 | 1
2683 | 0 | 0.15473 | 0.91049 | 0 | 1 | 1 | 0 | 0.15473 | 1
2684 | 0 | 0.14643 | 0.91049 | 0 | 1 | 1 | 0 | 0.14643 | 1
2685 | 0 | 0.14564 | 0.91049 | 0 | 1 | 1 | 0 | 0.14564 | 1
2686 | 0 | 0.14877 | 0.91049 | 0 | 0 | 1 | 0 | 0.14877 | 1
2687 | 0 | 0.1395 | 0.91049 | 0 | 0 | 1 | 0 | 0.1395 | 1
2688 | 0 | 0.14539 | 0.91049 | 0 | 0 | 1 | 0 | 0.14539 | 1
2689 | 0 | 0.12718 | 0.91049 | 0 | 0 | 1 | 0 | 0.12718 | 1
2690 | 0 | 0.096092 | 0.91049 | 0 | 0 | 1 | 0 | 0.096092 | 1
2691 | 0 | 0.077116 | 0.91049 | 0 | 0 | 1 | 0 | 0.077116 | 1
2692 | 0 | 0.052532 | 0.91049 | 0 | 0 | 1 | 0 | 0.052532 | 1
2693 | 0 | 0.081008 | 0.91049 | 0 | 0 | 1 | 0 | 0.081008 | 1
2694 | 0 | 0.049669 | 0.91049 | 0 | 0 | 1 | 0 | 0.049669 | 1
2695 | 0 | 0.034056 | 0.91049 | 0 | 0 | 1 | 0 | 0.034056 | 1
2696 | 0 | 0.032085 | 0.91049 | 0 | 0 | 1 | 0 | 0.032085 | 1
2697 | 0.071533 | 0.056032 | 0.91049 | 0 | 0 | 1 | 0.071533 | 0.056032 | 1
2698 | 0.17732 | 0.11029 | 0.91049 | 0 | 0 | 1 | 0.17732 | 0.11029 | 1
2699 | 0.25234 | 0.13202 | 0.91049 | 0 | 0 | 1 | 0.25234 | 0.13202 | 1
2700 | 0.31505 | 0.13061 | 0.91049 | 0 | 0 | 1 | 0.31505 | 0.13061 | 1
2701 | 0.35024 | 0.11714 | 0.91049 | 0 | 0 | 1 | 0.35024 | 0.11714 | 1
2702 | 0.25568 | 0.12428 | 0.91049 | 0 | 0 | 1 | 0.25568 | 0.12428 | 1
2703 | 0.15757 | 0.10747 | 0.91049 | 0 | 0 | 1 | 0.15757 | 0.10747 | 1
2704 | 0.099686 | 0.043863 | 0.91049 | 0 | 0 | 1 | 0.099686 | 0.043863 | 1
2705 | 0 | 0.071395 | 0.91049 | 0 | 0 | 1 | 0 | 0.071395 | 1
2706 | 0 | 0.10617 | 0.91049 | 0 | 1 | 1 | 0 | 0.10617 | 1
2707 | 0 | 0.096678 | 0.91049 | 0 | 1 | 1 | 0 | 0.096678 | 1
2708 | 0 | 0.057276 | 0.91049 | 0 | 1 | 1 | 0 | 0.057276 | 1
2709 | 0 | 0.078138 | 0.91049 | 0 | 1 | 1 | 0 | 0.078138 | 1
2710 | 0 | 0.10809 | 0.91049 | 0 | 0 | 1 | 0 | 0.10809 | 1
2711 | 0 | 0.084666 | 0.91049 | 0 | 0 | 1 | 0 | 0.084666 | 1
2712 | 0 | 0.075522 | 0.91049 | 0 | 0 | 1 | 0 | 0.075522 | 1
2713 | 0 | 0.13226 | 0.91049 | 0 | 0 | 1 | 0 | 0.13226 | 1
2714 | 0 | 0.06504 | 0.91049 | 0 | 0 | 1 | 0 | 0.06504 | 1
2715 | 0 | 0.081522 | 0.91049 | 0 | 0 | 1 | 0 | 0.081522 | 1
2716 | 0 | 0.047847 | 0.91049 | 0 | 0 | 1 | 0 | 0.047847 | 1
2717 | 0 | 0.066076 | 0.91049 | 0 | 0 | 1 | 0 | 0.066076 | 1
2718 | 0 | 0.049602 | 0.91049 | 0 | 0 | 1 | 0 | 0.049602 | 1
2719 | 0 | 0.023753 | 0.91049 | 0 | 0 | 1 | 0 | 0.023753 | 1
2720 | 0 | 0.024981 | 0.91049 | 0 | 0 | 1 | 0 | 0.024981 | 1
2721 | 0.10016 | 0.044162 | 0.91049 | 0 | 0 | 1 | 0.10016 | 0.044162 | 1
2722 | 0.21232 | 0.087568 | 0.91049 | 0 | 0 | 1 | 0.21232 | 0.087568 | 1
2723 | 0.25583 | 0.11378 | 0.91049 | 0 | 0 | 1 | 0.25583 | 0.11378 | 1
2724 | 0.31281 | 0.11832 | 0.91049 | 0 | 0 | 1 | 0.31281 | 0.11832 | 1
2725 | 0.34038 | 0.1285 | 0.91049 | 0 | 0 | 1 | 0.34038 | 0.1285 | 1
2726 | 0.30573 | 0.11324 | 0.91049 | 0 | 0 | 1 | 0.30573 | 0.11324 | 1
2727 | 0.15392 | 0.089885 | 0.91049 | 0 | 0 | 1 | 0.15392 | 0.089885 | 1
2728 | 0.12837 | 0.052206 | 0.91049 | 0 | 0 | 1 | 0.12837 | 0.052206 | 1
2729 | 0 | 0.067518 | 0.91049 | 0 | 0 | 1 | 0 | 0.067518 | 1
2730 | 0 | 0.064773 | 0.91049 | 0 | 1 | 1 | 0 | 0.064773 | 1
2731 | 0 | 0.053145 | 0.91049 | 0 | 1 | 1 | 0 | 0.053145 | 1
2732 | 0 | 0.02516 | 0.91049 | 0 | 1 | 1 | 0 | 0.02516 | 1
2733 | 0 | 0.058217 | 0.91049 | 0 | 1 | 1 | 0 | 0.058217 | 1
2734 | 0 | 0.083169 | 0.91049 | 0 | 0 | 1 | 0 | 0.083169 | 1
2735 | 0 | 0.071001 | 0.91049 | 0 | 0 | 1 | 0 | 0.071001 | 1
2736 | 0 | 0.067296 | 0.91049 | 0 | 0 | 1 | 0 | 0.067296 | 1
2737 | 0 | 0.081 | 0.91049 | 0 | 0 | 1 | 0 | 0.081 | 1
2738 | 0 | 0.051 | 0.91049 | 0 | 0 | 1 | 0 | 0.051 | 1
2739 | 0 | 0.056084 | 0.91049 | 0 | 0 | 1 | 0 | 0.056084 | 1
2740 | 0 | 0.054505 | 0.91049 | 0 | 0 | 1 | 0 | 0.054505 | 1
2741 | 0 | 0.06664 | 0.91049 | 0 | 0 | 1 | 0 | 0.06664 | 1
2742 | 0 | 0.043813 | 0.91049 | 0 | 0 | 1 | 0 | 0.043813 | 1
2743 | 0 | 0.035506 | 0.91049 | 0 | 0 | 1 | 0 | 0.035506 | 1
2744 | 0 | 0.031729 | 0.91049 | 0 | 0 | 1 | 0 | 0.031729 | 1
2745 | 0.16488 | 0.018594 | 0.91049 | 0 | 0 | 1 | 0.16488 | 0.018594 | 1
2746 | 0.27955 | 0.069227 | 0.91049 | 0 | 0 | 1 | 0.27955 | 0.069227 | 1
2747 | 0.30248 | 0.084671 | 0.91049 | 0 | 0 | 1 | 0.30248 | 0.084671 | 1
2748 | 0.32076 | 0.092451 | 0.91049 | 0 | 0 | 1 | 0.32076 | 0.092451 | 1
2749 | 0.36103 | 0.11657 | 0.91049 | 0 | 0 | 1 | 0.36103 | 0.11657 | 1
2750 | 0.36671 | 0.10949 | 0.91049 | 0 | 0 | 1 | 0.36671 | 0.10949 | 1
2751 | 0.20871 | 0.087643 | 0.91049 | 0 | 0 | 1 | 0.20871 | 0.087643 | 1
2752 | 0.10877 | 0.074377 | 0.91049 | 0 | 0 | 1 | 0.10877 | 0.074377 | 1
2753 | 0 | 0.037371 | 0.91049 | 0 | 0 | 1 | 0 | 0.037371 | 1
2754 | 0 | 0.040173 | 0.91049 | 0 | 1 | 1 | 0 | 0.040173 | 1
2755 | 0 | 0.027865 | 0.91049 | 0 | 1 | 1 | 0 | 0.027865 | 1
2756 | 0 | 0.0058334 | 0.91049 | 0 | 1 | 1 | 0 | 0.0058334 | 1
2757 | 0 | 0.039731 | 0.91049 | 0 | 1 | 1 | 0 | 0.039731 | 1
2758 | 0 | 0.053096 | 0.91049 | 0 | 0 | 1 | 0 | 0.053096 | 1
2759 | 0 | 0.041603 | 0.91049 | 0 | 0 | 1 | 0 | 0.041603 | 1
2760 | 0 | 0.035701 | 0.91049 | 0 | 0 | 1 | 0 | 0.035701 | 1
2761 | 0 | 0.062249 | 0.91049 | 0 | 0 | 1 | 0 | 0.062249 | 1
2762 | 0 | 0.036296 | 0.91049 | 0 | 0 | 1 | 0 | 0.036296 | 1
2763 | 0 | 0.028587 | 0.91049 | 0 | 0 | 1 | 0 | 0.028587 | 1
2764 | 0 | 0.036872 | 0.91049 | 0 | 0 | 1 | 0 | 0.036872 | 1
2765 | 0 | 0.033734 | 0.91049 | 0 | 0 | 1 | 0 | 0.033734 | 1
2766 | 0 | 0.019638 | 0.91049 | 0 | 0 | 1 | 0 | 0.019638 | 1
2767 | 0 | 0.010523 | 0.91049 | 0 | 0 | 1 | 0 | 0.010523 | 1
2768 | 0 | 0.014491 | 0.91049 | 0 | 0 | 1 | 0 | 0.014491 | 1
2769 | 0.089638 | 0.00060335 | 0.91049 | 0 | 0 | 1 | 0.089638 | 0.00060335 | 1
2770 | 0.2873 | 0.029322 | 0.91049 | 0 | 0 | 1 | 0.2873 | 0.029322 | 1
2771 | 0.34171 | 0.036003 | 0.91049 | 0 | 0 | 1 | 0.34171 | 0.036003 | 1
2772 | 0.36138 | 0.064046 | 0.91049 | 0 | 0 | 1 | 0.36138 | 0.064046 | 1
2773 | 0.30411 | 0.096006 | 0.91049 | 0 | 0 | 1 | 0.30411 | 0.096006 | 1
2774 | 0.25906 | 0.079838 | 0.91049 | 0 | 0 | 1 | 0.25906 | 0.079838 | 1
2775 | 0.1166 | 0.072306 | 0.91049 | 0 | 0 | 1 | 0.1166 | 0.072306 | 1
2776 | 0.012479 | 0.064677 | 0.91049 | 0 | 0 | 1 | 0.012479 | 0.064677 | 1
2777 | 0 | 0.027381 | 0.91049 | 0 | 0 | 1 | 0 | 0.027381 | 1
2778 | 0 | 0.033968 | 0.91049 | 0 | 1 | 1 | 0 | 0.033968 | 1
2779 | 0 | 0.018051 | 0.91049 | 0 | 1 | 1 | 0 | 0.018051 | 1
2780 | 0 | 0.0017948 | 0.91049 | 0 | 1 | 1 | 0 | 0.0017948 | 1
2781 | 0 | 0.012733 | 0.91049 | 0 | 1 | 1 | 0 | 0.012733 | 1
2782 | 0 | 0.014576 | 0.91049 | 0 | 0 | 1 | 0 | 0.014576 | 1
2783 | 0 | 0.024413 | 0.91049 | 0 | 0 | 1 | 0 | 0.024413 | 1
2784 | 0 | 0.018509 | 0.91049 | 0 | 0 | 1 | 0 | 0.018509 | 1
2785 | 0 | 0.042372 | 0.91049 | 0 | 0 | 1 | 0 | 0.042372 | 1
2786 | 0 | 0.01839 | 0.91049 | 0 | 0 | 1 | 0 | 0.01839 | 1
2787 | 0 | 0.0059995 | 0.91049 | 0 | 0 | 1 | 0 | 0.0059995 | 1
2788 | 0 | 0.019282 | 0.91049 | 0 | 0 | 1 | 0 | 0.019282 | 1
2789 | 0 | 0.013887 | 0.91049 | 0 | 0 | 1 | 0 | 0.013887 | 1
2790 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2791 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2792 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2793 | 0.028859 | 0 | 0.91049 | 0 | 0 | 1 | 0.028859 | 0 | 1
2794 | 0.18782 | 0 | 0.91049 | 0 | 0 | 1 | 0.18782 | 0 | 1
2795 | 0.192 | 0 | 0.91049 | 0 | 0 | 1 | 0.192 | 0 | 1
2796 | 0.28136 | 0.0086378 | 0.91049 | 0 | 0 | 1 | 0.28136 | 0.0086378 | 1
2797 | 0.23627 | 0.031366 | 0.91049 | 0 | 0 | 1 | 0.23627 | 0.031366 | 1
2798 | 0.15804 | 0.041747 | 0.91049 | 0 | 0 | 1 | 0.15804 | 0.041747 | 1
2799 | 0.04836 | 0.035914 | 0.91049 | 0 | 0 | 1 | 0.04836 | 0.035914 | 1
2800 | 0 | 0.03004 | 0.91049 | 0 | 0 | 1 | 0 | 0.03004 | 1
2801 | 0 | 0.0011692 | 0.91049 | 0 | 0 | 1 | 0 | 0.0011692 | 1
2802 | 0 | 0.015105 | 0.91049 | 0 | 1 | 1 | 0 | 0.015105 | 1
2803 | 0 | 0 | 0.91049 | 0 | 1 | 1 | 0 | 0 | 1
2804 | 0 | 0 | 0.91049 | 0 | 1 | 1 | 0 | 0 | 1
2805 | 0 | 0 | 0.91049 | 0 | 1 | 1 | 0 | 0 | 1
2806 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2807 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2808 | 0 | 0 | 0.91049 | 0 | 0 | 1 | 0 | 0 | 1
2809 | 0 | 0.010099 | 0.85414 | 0 | 0 | 1 | 0 | 0.010099 | 1
2810 | 0 | 0.0019092 | 0.85414 | 0 | 0 | 1 | 0 | 0.0019092 | 1
2811 | 0 | 0.020073 | 0.85414 | 0 | 0 | 1 | 0 | 0.020073 | 1
2812 | 0 | 0.027742 | 0.85414 | 0 | 0 | 1 | 0 | 0.027742 | 1
2813 | 0 | 0.0074877 | 0.85414 | 0 | 0 | 1 | 0 | 0.0074877 | 1
2814 | 0 | 0.00065602 | 0.85414 | 0 | 0 | 1 | 0 | 0.00065602 | 1
2815 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2816 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2817 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2818 | 0.10868 | 0 | 0.85414 | 0 | 0 | 1 | 0.10868 | 0 | 1
2819 | 0.092644 | 0 | 0.85414 | 0 | 0 | 1 | 0.092644 | 0 | 1
2820 | 0.17044 | 0.0046857 | 0.85414 | 0 | 0 | 1 | 0.17044 | 0.0046857 | 1
2821 | 0.10428 | 0.022424 | 0.85414 | 0 | 0 | 1 | 0.10428 | 0.022424 | 1
2822 | 0 | 0.020878 | 0.85414 | 0 | 0 | 1 | 0 | 0.020878 | 1
2823 | 0 | 0.017321 | 0.85414 | 0 | 0 | 1 | 0 | 0.017321 | 1
2824 | 0 | 0.0027524 | 0.85414 | 0 | 0 | 1 | 0 | 0.0027524 | 1
2825 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2826 | 0 | 0 | 0.85414 | 0 | 1 | 1 | 0 | 0 | 1
2827 | 0 | 0 | 0.85414 | 0 | 1 | 1 | 0 | 0 | 1
2828 | 0 | 0 | 0.85414 | 0 | 1 | 1 | 0 | 0 | 1
2829 | 0 | 0 | 0.85414 | 0 | 1 | 1 | 0 | 0 | 1
2830 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2831 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2832 | 0 | 0 | 0.85414 | 0 | 0 | 1 | 0 | 0 | 1
2833 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2834 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2835 | 0 | 0.0052825 | 0.8388 | 0 | 0 | 1 | 0 | 0.0052825 | 1
2836 | 0 | 0.006297 | 0.8388 | 0 | 0 | 1 | 0 | 0.006297 | 1
2837 | 0 | 0.015291 | 0.8388 | 0 | 0 | 1 | 0 | 0.015291 | 1
2838 | 0 | 0.013258 | 0.8388 | 0 | 0 | 1 | 0 | 0.013258 | 1
2839 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2840 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2841 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2842 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2843 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2844 | 0.045611 | 0 | 0.8388 | 0 | 0 | 1 | 0.045611 | 0 | 1
2845 | 0.040389 | 0 | 0.8388 | 0 | 0 | 1 | 0.040389 | 0 | 1
2846 | 0 | 0.010344 | 0.8388 | 0 | 0 | 1 | 0 | 0.010344 | 1
2847 | 0 | 0.018994 | 0.8388 | 0 | 0 | 1 | 0 | 0.018994 | 1
2848 | 0 | 0.013675 | 0.8388 | 0 | 0 | 1 | 0 | 0.013675 | 1
2849 | 0 | 0.0054328 | 0.8388 | 0 | 0 | 1 | 0 | 0.0054328 | 1
2850 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2851 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2852 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2853 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2854 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2855 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2856 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2857 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2858 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2859 | 0 | 0.0062869 | 0.8388 | 0 | 0 | 1 | 0 | 0.0062869 | 1
2860 | 0 | 0.0068232 | 0.8388 | 0 | 0 | 1 | 0 | 0.0068232 | 1
2861 | 0 | 0.024531 | 0.8388 | 0 | 0 | 1 | 0 | 0.024531 | 1
2862 | 0 | 0.031235 | 0.8388 | 0 | 0 | 1 | 0 | 0.031235 | 1
2863 | 0 | 0.019734 | 0.8388 | 0 | 0 | 1 | 0 | 0.019734 | 1
2864 | 0 | 0.00084673 | 0.8388 | 0 | 0 | 1 | 0 | 0.00084673 | 1
2865 | 0 | 0.00037948 | 0.8388 | 0 | 0 | 1 | 0 | 0.00037948 | 1
2866 | 0.042539 | 0.017908 | 0.8388 | 0 | 0 | 1 | 0.042539 | 0.017908 | 1
2867 | 0.055626 | 0.044267 | 0.8388 | 0 | 0 | 1 | 0.055626 | 0.044267 | 1
2868 | 0.12012 | 0.032296 | 0.8388 | 0 | 0 | 1 | 0.12012 | 0.032296 | 1
2869 | 0.11948 | 0.031966 | 0.8388 | 0 | 0 | 1 | 0.11948 | 0.031966 | 1
2870 | 0.016232 | 0.037041 | 0.8388 | 0 | 0 | 1 | 0.016232 | 0.037041 | 1
2871 | 0.032984 | 0.042923 | 0.8388 | 0 | 0 | 1 | 0.032984 | 0.042923 | 1
2872 | 0 | 0.0408 | 0.8388 | 0 | 0 | 1 | 0 | 0.0408 | 1
2873 | 0 | 0.042352 | 0.8388 | 0 | 0 | 1 | 0 | 0.042352 | 1
2874 | 0 | 0.026051 | 0.8388 | 0 | 1 | 1 | 0 | 0.026051 | 1
2875 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2876 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2877 | 0 | 0.00073693 | 0.8388 | 0 | 1 | 1 | 0 | 0.00073693 | 1
2878 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2879 | 0 | 0.0089363 | 0.8388 | 0 | 0 | 1 | 0 | 0.0089363 | 1
2880 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2881 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2882 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2883 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2884 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2885 | 0 | 0.00086621 | 0.8388 | 0 | 0 | 1 | 0 | 0.00086621 | 1
2886 | 0 | 0.0095404 | 0.8388 | 0 | 0 | 1 | 0 | 0.0095404 | 1
2887 | 0 | 0.0093846 | 0.8388 | 0 | 0 | 1 | 0 | 0.0093846 | 1
2888 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2889 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2890 | 0 | 0.017163 | 0.8388 | 0 | 0 | 1 | 0 | 0.017163 | 1
2891 | 0.023067 | 0.055578 | 0.8388 | 0 | 0 | 1 | 0.023067 | 0.055578 | 1
2892 | 0.10104 | 0.052894 | 0.8388 | 0 | 0 | 1 | 0.10104 | 0.052894 | 1
2893 | 0.13633 | 0.046037 | 0.8388 | 0 | 0 | 1 | 0.13633 | 0.046037 | 1
2894 | 0.15078 | 0.04463 | 0.8388 | 0 | 0 | 1 | 0.15078 | 0.04463 | 1
2895 | 0.13596 | 0.047294 | 0.8388 | 0 | 0 | 1 | 0.13596 | 0.047294 | 1
2896 | 0.056015 | 0.062489 | 0.8388 | 0 | 0 | 1 | 0.056015 | 0.062489 | 1
2897 | 0 | 0.064273 | 0.8388 | 0 | 0 | 1 | 0 | 0.064273 | 1
2898 | 0 | 0.056724 | 0.8388 | 0 | 1 | 1 | 0 | 0.056724 | 1
2899 | 0 | 0.02753 | 0.8388 | 0 | 1 | 1 | 0 | 0.02753 | 1
2900 | 0 | 0.00027586 | 0.8388 | 0 | 1 | 1 | 0 | 0.00027586 | 1
2901 | 0 | 0.0077279 | 0.8388 | 0 | 1 | 1 | 0 | 0.0077279 | 1
2902 | 0 | 0.0092196 | 0.8388 | 0 | 0 | 1 | 0 | 0.0092196 | 1
2903 | 0 | 0.012352 | 0.8388 | 0 | 0 | 1 | 0 | 0.012352 | 1
2904 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2905 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2906 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2907 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2908 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2909 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2910 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2911 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2912 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2913 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2914 | 0.032257 | 0.0074035 | 0.8388 | 0 | 0 | 1 | 0.032257 | 0.0074035 | 1
2915 | 0.088923 | 0.042035 | 0.8388 | 0 | 0 | 1 | 0.088923 | 0.042035 | 1
2916 | 0.18657 | 0.067106 | 0.8388 | 0 | 0 | 1 | 0.18657 | 0.067106 | 1
2917 | 0.17453 | 0.062234 | 0.8388 | 0 | 0 | 1 | 0.17453 | 0.062234 | 1
2918 | 0.21741 | 0.032659 | 0.8388 | 0 | 0 | 1 | 0.21741 | 0.032659 | 1
2919 | 0.13442 | 0.024168 | 0.8388 | 0 | 0 | 1 | 0.13442 | 0.024168 | 1
2920 | 0.021322 | 0.031303 | 0.8388 | 0 | 0 | 1 | 0.021322 | 0.031303 | 1
2921 | 0 | 0.045026 | 0.8388 | 0 | 0 | 1 | 0 | 0.045026 | 1
2922 | 0 | 0.040028 | 0.8388 | 0 | 1 | 1 | 0 | 0.040028 | 1
2923 | 0 | 0.023388 | 0.8388 | 0 | 1 | 1 | 0 | 0.023388 | 1
2924 | 0 | 0.0010667 | 0.8388 | 0 | 1 | 1 | 0 | 0.0010667 | 1
2925 | 0 | 0.0001289 | 0.8388 | 0 | 1 | 1 | 0 | 0.0001289 | 1
2926 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2927 | 0 | 0.010189 | 0.8388 | 0 | 0 | 1 | 0 | 0.010189 | 1
2928 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2929 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2930 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2931 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2932 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2933 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2934 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2935 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2936 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2937 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2938 | 0.027695 | 0 | 0.8388 | 0 | 0 | 1 | 0.027695 | 0 | 1
2939 | 0.10885 | 0.015579 | 0.8388 | 0 | 0 | 1 | 0.10885 | 0.015579 | 1
2940 | 0.15869 | 0.047732 | 0.8388 | 0 | 0 | 1 | 0.15869 | 0.047732 | 1
2941 | 0.17674 | 0.047047 | 0.8388 | 0 | 0 | 1 | 0.17674 | 0.047047 | 1
2942 | 0.18864 | 0.033834 | 0.8388 | 0 | 0 | 1 | 0.18864 | 0.033834 | 1
2943 | 0.12813 | 0.021846 | 0.8388 | 0 | 0 | 1 | 0.12813 | 0.021846 | 1
2944 | 0.042571 | 0.017747 | 0.8388 | 0 | 0 | 1 | 0.042571 | 0.017747 | 1
2945 | 0 | 0.021733 | 0.8388 | 0 | 0 | 1 | 0 | 0.021733 | 1
2946 | 0 | 0.00010774 | 0.8388 | 0 | 1 | 1 | 0 | 0.00010774 | 1
2947 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2948 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2949 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2950 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2951 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2952 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2953 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2954 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2955 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2956 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2957 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2958 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2959 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2960 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2961 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2962 | 0.12165 | 0 | 0.8388 | 0 | 0 | 1 | 0.12165 | 0 | 1
2963 | 0.20214 | 0 | 0.8388 | 0 | 0 | 1 | 0.20214 | 0 | 1
2964 | 0.25786 | 0.021588 | 0.8388 | 0 | 0 | 1 | 0.25786 | 0.021588 | 1
2965 | 0.24128 | 0.02795 | 0.8388 | 0 | 0 | 1 | 0.24128 | 0.02795 | 1
2966 | 0.23358 | 0.023569 | 0.8388 | 0 | 0 | 1 | 0.23358 | 0.023569 | 1
2967 | 0.19722 | 0.0042597 | 0.8388 | 0 | 0 | 1 | 0.19722 | 0.0042597 | 1
2968 | 0.060185 | 0 | 0.8388 | 0 | 0 | 1 | 0.060185 | 0 | 1
2969 | 0 | 0.0040306 | 0.8388 | 0 | 0 | 1 | 0 | 0.0040306 | 1
2970 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2971 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2972 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2973 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2974 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2975 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2976 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2977 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2978 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2979 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2980 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2981 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2982 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2983 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2984 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2985 | 0.054173 | 0 | 0.8388 | 0 | 0 | 1 | 0.054173 | 0 | 1
2986 | 0.20705 | 0 | 0.8388 | 0 | 0 | 1 | 0.20705 | 0 | 1
2987 | 0.33197 | 0.0030865 | 0.8388 | 0 | 0 | 1 | 0.33197 | 0.0030865 | 1
2988 | 0.30515 | 0.042264 | 0.8388 | 0 | 0 | 1 | 0.30515 | 0.042264 | 1
2989 | 0.32482 | 0.060805 | 0.8388 | 0 | 0 | 1 | 0.32482 | 0.060805 | 1
2990 | 0.25317 | 0.081796 | 0.8388 | 0 | 0 | 1 | 0.25317 | 0.081796 | 1
2991 | 0.19549 | 0.064276 | 0.8388 | 0 | 0 | 1 | 0.19549 | 0.064276 | 1
2992 | 0.12366 | 0.046444 | 0.8388 | 0 | 0 | 1 | 0.12366 | 0.046444 | 1
2993 | 0.010434 | 0.042423 | 0.8388 | 0 | 0 | 1 | 0.010434 | 0.042423 | 1
2994 | 0 | 0.011802 | 0.8388 | 0 | 1 | 1 | 0 | 0.011802 | 1
2995 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2996 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2997 | 0 | 0 | 0.8388 | 0 | 1 | 1 | 0 | 0 | 1
2998 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
2999 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
3000 | 0 | 0 | 0.8388 | 0 | 0 | 1 | 0 | 0 | 1
3001 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3002 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3003 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3004 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3005 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3006 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3007 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3008 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3009 | 0.083664 | 0 | 0.95151 | 0 | 0 | 1 | 0.083664 | 0 | 1
3010 | 0.2052 | 0.014802 | 0.95151 | 0 | 0 | 1 | 0.2052 | 0.014802 | 1
3011 | 0.37244 | 0.0038216 | 0.95151 | 0 | 0 | 1 | 0.37244 | 0.0038216 | 1
3012 | 0.39962 | 0.036149 | 0.95151 | 0 | 0 | 1 | 0.39962 | 0.036149 | 1
3013 | 0.35655 | 0.050665 | 0.95151 | 0 | 0 | 1 | 0.35655 | 0.050665 | 1
3014 | 0.29979 | 0.069639 | 0.95151 | 0 | 0 | 1 | 0.29979 | 0.069639 | 1
3015 | 0.24665 | 0.061655 | 0.95151 | 0 | 0 | 1 | 0.24665 | 0.061655 | 1
3016 | 0.13558 | 0.055754 | 0.95151 | 0 | 0 | 1 | 0.13558 | 0.055754 | 1
3017 | 0.0017743 | 0.07216 | 0.95151 | 0 | 0 | 1 | 0.0017743 | 0.07216 | 1
3018 | 0 | 0.048987 | 0.95151 | 0 | 1 | 1 | 0 | 0.048987 | 1
3019 | 0 | 0.020631 | 0.95151 | 0 | 1 | 1 | 0 | 0.020631 | 1
3020 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3021 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3022 | 0 | 0.0032465 | 0.95151 | 0 | 0 | 1 | 0 | 0.0032465 | 1
3023 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3024 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3025 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3026 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3027 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3028 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3029 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3030 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3031 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3032 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3033 | 0.1123 | 0 | 0.95151 | 0 | 0 | 1 | 0.1123 | 0 | 1
3034 | 0.20801 | 0.012469 | 0.95151 | 0 | 0 | 1 | 0.20801 | 0.012469 | 1
3035 | 0.30734 | 0.02238 | 0.95151 | 0 | 0 | 1 | 0.30734 | 0.02238 | 1
3036 | 0.34306 | 0.038379 | 0.95151 | 0 | 0 | 1 | 0.34306 | 0.038379 | 1
3037 | 0.29396 | 0.047001 | 0.95151 | 0 | 0 | 1 | 0.29396 | 0.047001 | 1
3038 | 0.21019 | 0.070296 | 0.95151 | 0 | 0 | 1 | 0.21019 | 0.070296 | 1
3039 | 0.16491 | 0.080466 | 0.95151 | 0 | 0 | 1 | 0.16491 | 0.080466 | 1
3040 | 0.067056 | 0.075276 | 0.95151 | 0 | 0 | 1 | 0.067056 | 0.075276 | 1
3041 | 0 | 0.070141 | 0.95151 | 0 | 0 | 1 | 0 | 0.070141 | 1
3042 | 0 | 0.047932 | 0.95151 | 0 | 1 | 1 | 0 | 0.047932 | 1
3043 | 0 | 0.02277 | 0.95151 | 0 | 1 | 1 | 0 | 0.02277 | 1
3044 | 0 | 0.0046316 | 0.95151 | 0 | 1 | 1 | 0 | 0.0046316 | 1
3045 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3046 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3047 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3048 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3049 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3050 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3051 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3052 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3053 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3054 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3055 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3056 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3057 | 0.067788 | 0.0012336 | 0.95151 | 0 | 0 | 1 | 0.067788 | 0.0012336 | 1
3058 | 0.15769 | 0.0036725 | 0.95151 | 0 | 0 | 1 | 0.15769 | 0.0036725 | 1
3059 | 0.22933 | 0.01926 | 0.95151 | 0 | 0 | 1 | 0.22933 | 0.01926 | 1
3060 | 0.25722 | 0.028741 | 0.95151 | 0 | 0 | 1 | 0.25722 | 0.028741 | 1
3061 | 0.22334 | 0.023727 | 0.95151 | 0 | 0 | 1 | 0.22334 | 0.023727 | 1
3062 | 0.14642 | 0.028041 | 0.95151 | 0 | 0 | 1 | 0.14642 | 0.028041 | 1
3063 | 0.093238 | 0.034115 | 0.95151 | 0 | 0 | 1 | 0.093238 | 0.034115 | 1
3064 | 0 | 0.035266 | 0.95151 | 0 | 0 | 1 | 0 | 0.035266 | 1
3065 | 0 | 0.041571 | 0.95151 | 0 | 0 | 1 | 0 | 0.041571 | 1
3066 | 0 | 0.033638 | 0.95151 | 0 | 1 | 1 | 0 | 0.033638 | 1
3067 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3068 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3069 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3070 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3071 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3072 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3073 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3074 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3075 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3076 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3077 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3078 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3079 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3080 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3081 | 0.070231 | 0 | 0.95151 | 0 | 0 | 1 | 0.070231 | 0 | 1
3082 | 0.15155 | 0 | 0.95151 | 0 | 0 | 1 | 0.15155 | 0 | 1
3083 | 0.192 | 0.018721 | 0.95151 | 0 | 0 | 1 | 0.192 | 0.018721 | 1
3084 | 0.18723 | 0.026341 | 0.95151 | 0 | 0 | 1 | 0.18723 | 0.026341 | 1
3085 | 0.16569 | 0.033884 | 0.95151 | 0 | 0 | 1 | 0.16569 | 0.033884 | 1
3086 | 0.108 | 0.038207 | 0.95151 | 0 | 0 | 1 | 0.108 | 0.038207 | 1
3087 | 0.02992 | 0.042122 | 0.95151 | 0 | 0 | 1 | 0.02992 | 0.042122 | 1
3088 | 0 | 0.032336 | 0.95151 | 0 | 0 | 1 | 0 | 0.032336 | 1
3089 | 0 | 0.022565 | 0.95151 | 0 | 0 | 1 | 0 | 0.022565 | 1
3090 | 0 | 0.020996 | 0.95151 | 0 | 1 | 1 | 0 | 0.020996 | 1
3091 | 0 | 0.00025677 | 0.95151 | 0 | 1 | 1 | 0 | 0.00025677 | 1
3092 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3093 | 0 | 0 | 0.95151 | 0 | 1 | 1 | 0 | 0 | 1
3094 | 0 | 0.0024506 | 0.95151 | 0 | 0 | 1 | 0 | 0.0024506 | 1
3095 | 0 | 0.0097311 | 0.95151 | 0 | 0 | 1 | 0 | 0.0097311 | 1
3096 | 0 | 0.023686 | 0.95151 | 0 | 0 | 1 | 0 | 0.023686 | 1
3097 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3098 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3099 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3100 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3101 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3102 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3103 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3104 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3105 | 0.071881 | 0 | 0.95151 | 0 | 0 | 1 | 0.071881 | 0 | 1
3106 | 0.179 | 0 | 0.95151 | 0 | 0 | 1 | 0.179 | 0 | 1
3107 | 0.195 | 0.02987 | 0.95151 | 0 | 0 | 1 | 0.195 | 0.02987 | 1
3108 | 0.14263 | 0.043982 | 0.95151 | 0 | 0 | 1 | 0.14263 | 0.043982 | 1
3109 | 0.10234 | 0.054049 | 0.95151 | 0 | 0 | 1 | 0.10234 | 0.054049 | 1
3110 | 0.072244 | 0.047219 | 0.95151 | 0 | 0 | 1 | 0.072244 | 0.047219 | 1
3111 | 0.0066701 | 0.052004 | 0.95151 | 0 | 0 | 1 | 0.0066701 | 0.052004 | 1
3112 | 0 | 0.044231 | 0.95151 | 0 | 0 | 1 | 0 | 0.044231 | 1
3113 | 0 | 0.034385 | 0.95151 | 0 | 0 | 1 | 0 | 0.034385 | 1
3114 | 0 | 0.056541 | 0.95151 | 0 | 1 | 1 | 0 | 0.056541 | 1
3115 | 0 | 0.048795 | 0.95151 | 0 | 1 | 1 | 0 | 0.048795 | 1
3116 | 0 | 0.047923 | 0.95151 | 0 | 1 | 1 | 0 | 0.047923 | 1
3117 | 0 | 0.048611 | 0.95151 | 0 | 1 | 1 | 0 | 0.048611 | 1
3118 | 0 | 0.054764 | 0.95151 | 0 | 0 | 1 | 0 | 0.054764 | 1
3119 | 0 | 0.058984 | 0.95151 | 0 | 0 | 1 | 0 | 0.058984 | 1
3120 | 0 | 0.052488 | 0.95151 | 0 | 0 | 1 | 0 | 0.052488 | 1
3121 | 0 | 0.0094559 | 0.95151 | 0 | 0 | 1 | 0 | 0.0094559 | 1
3122 | 0 | 0.013223 | 0.95151 | 0 | 0 | 1 | 0 | 0.013223 | 1
3123 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3124 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3125 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3126 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3127 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3128 | 0 | 0 | 0.95151 | 0 | 0 | 1 | 0 | 0 | 1
3129 | 0.1416 | 0 | 0.95151 | 0 | 0 | 1 | 0.1416 | 0 | 1
3130 | 0.2602 | 0.047235 | 0.95151 | 0 | 0 | 1 | 0.2602 | 0.047235 | 1
3131 | 0.25457 | 0.084835 | 0.95151 | 0 | 0 | 1 | 0.25457 | 0.084835 | 1
3132 | 0.2497 | 0.10247 | 0.95151 | 0 | 0 | 1 | 0.2497 | 0.10247 | 1
3133 | 0.18954 | 0.11249 | 0.95151 | 0 | 0 | 1 | 0.18954 | 0.11249 | 1
3134 | 0.17967 | 0.098297 | 0.95151 | 0 | 0 | 1 | 0.17967 | 0.098297 | 1
3135 | 0.10795 | 0.10042 | 0.95151 | 0 | 0 | 1 | 0.10795 | 0.10042 | 1
3136 | 0.074952 | 0.087971 | 0.95151 | 0 | 0 | 1 | 0.074952 | 0.087971 | 1
3137 | 0 | 0.065026 | 0.95151 | 0 | 0 | 1 | 0 | 0.065026 | 1
3138 | 0 | 0.069885 | 0.95151 | 0 | 1 | 1 | 0 | 0.069885 | 1
3139 | 0 | 0.071586 | 0.95151 | 0 | 1 | 1 | 0 | 0.071586 | 1
3140 | 0 | 0.071842 | 0.95151 | 0 | 1 | 1 | 0 | 0.071842 | 1
3141 | 0 | 0.060325 | 0.95151 | 0 | 1 | 1 | 0 | 0.060325 | 1
3142 | 0 | 0.063962 | 0.95151 | 0 | 0 | 1 | 0 | 0.063962 | 1
3143 | 0 | 0.04803 | 0.95151 | 0 | 0 | 1 | 0 | 0.04803 | 1
3144 | 0 | 0.039598 | 0.95151 | 0 | 0 | 1 | 0 | 0.039598 | 1
3145 | 0 | 0.035902 | 0.95151 | 0 | 0 | 1 | 0 | 0.035902 | 1
3146 | 0 | 0.022273 | 0.95151 | 0 | 0 | 1 | 0 | 0.022273 | 1
3147 | 0 | 0.015934 | 0.95151 | 0 | 0 | 1 | 0 | 0.015934 | 1
3148 | 0 | 0.010891 | 0.95151 | 0 | 0 | 1 | 0 | 0.010891 | 1
3149 | 0 | 0.014045 | 0.95151 | 0 | 0 | 1 | 0 | 0.014045 | 1
3150 | 0 | 0.0014109 | 0.95151 | 0 | 0 | 1 | 0 | 0.0014109 | 1
3151 | 0 | 0.018926 | 0.95151 | 0 | 0 | 1 | 0 | 0.018926 | 1
3152 | 0 | 0.014237 | 0.95151 | 0 | 0 | 1 | 0 | 0.014237 | 1
3153 | 0.15824 | 0.02968 | 0.95151 | 0 | 0 | 1 | 0.15824 | 0.02968 | 1
3154 | 0.29017 | 0.073771 | 0.95151 | 0 | 0 | 1 | 0.29017 | 0.073771 | 1
3155 | 0.30274 | 0.11235 | 0.95151 | 0 | 0 | 1 | 0.30274 | 0.11235 | 1
3156 | 0.33346 | 0.14041 | 0.95151 | 0 | 0 | 1 | 0.33346 | 0.14041 | 1
3157 | 0.2436 | 0.13724 | 0.95151 | 0 | 0 | 1 | 0.2436 | 0.13724 | 1
3158 | 0.20864 | 0.11809 | 0.95151 | 0 | 0 | 1 | 0.20864 | 0.11809 | 1
3159 | 0.20477 | 0.12919 | 0.95151 | 0 | 0 | 1 | 0.20477 | 0.12919 | 1
3160 | 0.22029 | 0.12549 | 0.95151 | 0 | 0 | 1 | 0.22029 | 0.12549 | 1
3161 | 0.026965 | 0.097749 | 0.95151 | 0 | 0 | 1 | 0.026965 | 0.097749 | 1
3162 | 0 | 0.098714 | 0.95151 | 0 | 1 | 1 | 0 | 0.098714 | 1
3163 | 0 | 0.098674 | 0.95151 | 0 | 1 | 1 | 0 | 0.098674 | 1
3164 | 0 | 0.10363 | 0.95151 | 0 | 1 | 1 | 0 | 0.10363 | 1
3165 | 0 | 0.078886 | 0.95151 | 0 | 1 | 1 | 0 | 0.078886 | 1
3166 | 0 | 0.066958 | 0.95151 | 0 | 0 | 1 | 0 | 0.066958 | 1
3167 | 0 | 0.05577 | 0.95151 | 0 | 0 | 1 | 0 | 0.05577 | 1
3168 | 0 | 0.039177 | 0.95151 | 0 | 0 | 1 | 0 | 0.039177 | 1
3169 | 0 | 0.037511 | 0.88078 | 0 | 0 | 1 | 0 | 0.037511 | 1
3170 | 0 | 0.031662 | 0.88078 | 0 | 0 | 1 | 0 | 0.031662 | 1
3171 | 0 | 0.022473 | 0.88078 | 0 | 0 | 1 | 0 | 0.022473 | 1
3172 | 0 | 0.016679 | 0.88078 | 0 | 0 | 1 | 0 | 0.016679 | 1
3173 | 0 | 0.023032 | 0.88078 | 0 | 0 | 1 | 0 | 0.023032 | 1
3174 | 0 | 0.011526 | 0.88078 | 0 | 0 | 1 | 0 | 0.011526 | 1
3175 | 0 | 0.036945 | 0.88078 | 0 | 0 | 1 | 0 | 0.036945 | 1
3176 | 0 | 0.05954 | 0.88078 | 0 | 0 | 1 | 0 | 0.05954 | 1
3177 | 0.13668 | 0.084934 | 0.88078 | 0 | 0 | 1 | 0.13668 | 0.084934 | 1
3178 | 0.2957 | 0.11161 | 0.88078 | 0 | 0 | 1 | 0.2957 | 0.11161 | 1
3179 | 0.40525 | 0.13368 | 0.88078 | 0 | 0 | 1 | 0.40525 | 0.13368 | 1
3180 | 0.45421 | 0.1755 | 0.88078 | 0 | 0 | 1 | 0.45421 | 0.1755 | 1
3181 | 0.43513 | 0.19824 | 0.88078 | 0 | 0 | 1 | 0.43513 | 0.19824 | 1
3182 | 0.41399 | 0.17568 | 0.88078 | 0 | 0 | 1 | 0.41399 | 0.17568 | 1
3183 | 0.28619 | 0.17383 | 0.88078 | 0 | 0 | 1 | 0.28619 | 0.17383 | 1
3184 | 0.23477 | 0.15815 | 0.88078 | 0 | 0 | 1 | 0.23477 | 0.15815 | 1
3185 | 0.089434 | 0.12465 | 0.88078 | 0 | 0 | 1 | 0.089434 | 0.12465 | 1
3186 | 0 | 0.11406 | 0.88078 | 0 | 1 | 1 | 0 | 0.11406 | 1
3187 | 0 | 0.097536 | 0.88078 | 0 | 1 | 1 | 0 | 0.097536 | 1
3188 | 0 | 0.065367 | 0.88078 | 0 | 1 | 1 | 0 | 0.065367 | 1
3189 | 0 | 0.046601 | 0.88078 | 0 | 1 | 1 | 0 | 0.046601 | 1
3190 | 0 | 0.047552 | 0.88078 | 0 | 0 | 1 | 0 | 0.047552 | 1
3191 | 0 | 0.041702 | 0.88078 | 0 | 0 | 1 | 0 | 0.041702 | 1
3192 | 0 | 0.015501 | 0.88078 | 0 | 0 | 1 | 0 | 0.015501 | 1
3193 | 0 | 0.035304 | 0.88078 | 0 | 0 | 1 | 0 | 0.035304 | 1
3194 | 0 | 0.0083835 | 0.88078 | 0 | 0 | 1 | 0 | 0.0083835 | 1
3195 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3196 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3197 | 0 | 0.010563 | 0.88078 | 0 | 0 | 1 | 0 | 0.010563 | 1
3198 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3199 | 0 | 0.014218 | 0.88078 | 0 | 0 | 1 | 0 | 0.014218 | 1
3200 | 0 | 0.029889 | 0.88078 | 0 | 0 | 1 | 0 | 0.029889 | 1
3201 | 0.093642 | 0.032191 | 0.88078 | 0 | 0 | 1 | 0.093642 | 0.032191 | 1
3202 | 0.25839 | 0.046972 | 0.88078 | 0 | 0 | 1 | 0.25839 | 0.046972 | 1
3203 | 0.43741 | 0.059133 | 0.88078 | 0 | 0 | 1 | 0.43741 | 0.059133 | 1
3204 | 0.4244 | 0.10998 | 0.88078 | 0 | 0 | 1 | 0.4244 | 0.10998 | 1
3205 | 0.3863 | 0.14199 | 0.88078 | 0 | 0 | 1 | 0.3863 | 0.14199 | 1
3206 | 0.41388 | 0.11979 | 0.88078 | 0 | 0 | 1 | 0.41388 | 0.11979 | 1
3207 | 0.30492 | 0.12875 | 0.88078 | 0 | 0 | 1 | 0.30492 | 0.12875 | 1
3208 | 0.20532 | 0.12764 | 0.88078 | 0 | 0 | 1 | 0.20532 | 0.12764 | 1
3209 | 0.08165 | 0.10099 | 0.88078 | 0 | 0 | 1 | 0.08165 | 0.10099 | 1
3210 | 0 | 0.099478 | 0.88078 | 0 | 1 | 1 | 0 | 0.099478 | 1
3211 | 0 | 0.075874 | 0.88078 | 0 | 1 | 1 | 0 | 0.075874 | 1
3212 | 0 | 0.0333 | 0.88078 | 0 | 1 | 1 | 0 | 0.0333 | 1
3213 | 0 | 0.026024 | 0.88078 | 0 | 1 | 1 | 0 | 0.026024 | 1
3214 | 0 | 0.042193 | 0.88078 | 0 | 0 | 1 | 0 | 0.042193 | 1
3215 | 0 | 0.046962 | 0.88078 | 0 | 0 | 1 | 0 | 0.046962 | 1
3216 | 0 | 0.016796 | 0.88078 | 0 | 0 | 1 | 0 | 0.016796 | 1
3217 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3218 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3219 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3220 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3221 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3222 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3223 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3224 | 0 | 0.019366 | 0.88078 | 0 | 0 | 1 | 0 | 0.019366 | 1
3225 | 0.082027 | 0.020257 | 0.88078 | 0 | 0 | 1 | 0.082027 | 0.020257 | 1
3226 | 0.27605 | 0.045295 | 0.88078 | 0 | 0 | 1 | 0.27605 | 0.045295 | 1
3227 | 0.40795 | 0.059484 | 0.88078 | 0 | 0 | 1 | 0.40795 | 0.059484 | 1
3228 | 0.41078 | 0.10523 | 0.88078 | 0 | 0 | 1 | 0.41078 | 0.10523 | 1
3229 | 0.34828 | 0.1271 | 0.88078 | 0 | 0 | 1 | 0.34828 | 0.1271 | 1
3230 | 0.38672 | 0.11778 | 0.88078 | 0 | 0 | 1 | 0.38672 | 0.11778 | 1
3231 | 0.24529 | 0.11638 | 0.88078 | 0 | 0 | 1 | 0.24529 | 0.11638 | 1
3232 | 0.12359 | 0.12397 | 0.88078 | 0 | 0 | 1 | 0.12359 | 0.12397 | 1
3233 | 0.062417 | 0.12136 | 0.88078 | 0 | 0 | 1 | 0.062417 | 0.12136 | 1
3234 | 0 | 0.11573 | 0.88078 | 0 | 1 | 1 | 0 | 0.11573 | 1
3235 | 0 | 0.083317 | 0.88078 | 0 | 1 | 1 | 0 | 0.083317 | 1
3236 | 0 | 0.040449 | 0.88078 | 0 | 1 | 1 | 0 | 0.040449 | 1
3237 | 0 | 0.043489 | 0.88078 | 0 | 1 | 1 | 0 | 0.043489 | 1
3238 | 0 | 0.063488 | 0.88078 | 0 | 0 | 1 | 0 | 0.063488 | 1
3239 | 0 | 0.066154 | 0.88078 | 0 | 0 | 1 | 0 | 0.066154 | 1
3240 | 0 | 0.045277 | 0.88078 | 0 | 0 | 1 | 0 | 0.045277 | 1
3241 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3242 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3243 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3244 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3245 | 0 | 0.011346 | 0.88078 | 0 | 0 | 1 | 0 | 0.011346 | 1
3246 | 0 | 0.016376 | 0.88078 | 0 | 0 | 1 | 0 | 0.016376 | 1
3247 | 0 | 0.01243 | 0.88078 | 0 | 0 | 1 | 0 | 0.01243 | 1
3248 | 0 | 0.028527 | 0.88078 | 0 | 0 | 1 | 0 | 0.028527 | 1
3249 | 0.035086 | 0.0050401 | 0.88078 | 0 | 0 | 1 | 0.035086 | 0.0050401 | 1
3250 | 0.2795 | 0.039321 | 0.88078 | 0 | 0 | 1 | 0.2795 | 0.039321 | 1
3251 | 0.37313 | 0.065808 | 0.88078 | 0 | 0 | 1 | 0.37313 | 0.065808 | 1
3252 | 0.40249 | 0.09431 | 0.88078 | 0 | 0 | 1 | 0.40249 | 0.09431 | 1
3253 | 0.34209 | 0.097688 | 0.88078 | 0 | 0 | 1 | 0.34209 | 0.097688 | 1
3254 | 0.3131 | 0.073191 | 0.88078 | 0 | 0 | 1 | 0.3131 | 0.073191 | 1
3255 | 0.27068 | 0.067828 | 0.88078 | 0 | 0 | 1 | 0.27068 | 0.067828 | 1
3256 | 0.17206 | 0.083305 | 0.88078 | 0 | 0 | 1 | 0.17206 | 0.083305 | 1
3257 | 0.064868 | 0.10743 | 0.88078 | 0 | 0 | 1 | 0.064868 | 0.10743 | 1
3258 | 0 | 0.11169 | 0.88078 | 0 | 1 | 1 | 0 | 0.11169 | 1
3259 | 0 | 0.08327 | 0.88078 | 0 | 1 | 1 | 0 | 0.08327 | 1
3260 | 0 | 0.063059 | 0.88078 | 0 | 1 | 1 | 0 | 0.063059 | 1
3261 | 0 | 0.05239 | 0.88078 | 0 | 1 | 1 | 0 | 0.05239 | 1
3262 | 0 | 0.063839 | 0.88078 | 0 | 0 | 1 | 0 | 0.063839 | 1
3263 | 0 | 0.055331 | 0.88078 | 0 | 0 | 1 | 0 | 0.055331 | 1
3264 | 0 | 0.041567 | 0.88078 | 0 | 0 | 1 | 0 | 0.041567 | 1
3265 | 0 | 0.0078796 | 0.88078 | 0 | 0 | 1 | 0 | 0.0078796 | 1
3266 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3267 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3268 | 0 | 0.0085847 | 0.88078 | 0 | 0 | 1 | 0 | 0.0085847 | 1
3269 | 0 | 0.0066232 | 0.88078 | 0 | 0 | 1 | 0 | 0.0066232 | 1
3270 | 0 | 0.013694 | 0.88078 | 0 | 0 | 1 | 0 | 0.013694 | 1
3271 | 0 | 0.014603 | 0.88078 | 0 | 0 | 1 | 0 | 0.014603 | 1
3272 | 0 | 0.023865 | 0.88078 | 0 | 0 | 1 | 0 | 0.023865 | 1
3273 | 0.07131 | 0.0013811 | 0.88078 | 0 | 0 | 1 | 0.07131 | 0.0013811 | 1
3274 | 0.32719 | 0.02918 | 0.88078 | 0 | 0 | 1 | 0.32719 | 0.02918 | 1
3275 | 0.36115 | 0.057923 | 0.88078 | 0 | 0 | 1 | 0.36115 | 0.057923 | 1
3276 | 0.36968 | 0.10103 | 0.88078 | 0 | 0 | 1 | 0.36968 | 0.10103 | 1
3277 | 0.32816 | 0.10698 | 0.88078 | 0 | 0 | 1 | 0.32816 | 0.10698 | 1
3278 | 0.21311 | 0.092375 | 0.88078 | 0 | 0 | 1 | 0.21311 | 0.092375 | 1
3279 | 0.20275 | 0.080688 | 0.88078 | 0 | 0 | 1 | 0.20275 | 0.080688 | 1
3280 | 0.13914 | 0.074175 | 0.88078 | 0 | 0 | 1 | 0.13914 | 0.074175 | 1
3281 | 0.034066 | 0.0643 | 0.88078 | 0 | 0 | 1 | 0.034066 | 0.0643 | 1
3282 | 0 | 0.077441 | 0.88078 | 0 | 1 | 1 | 0 | 0.077441 | 1
3283 | 0 | 0.05426 | 0.88078 | 0 | 1 | 1 | 0 | 0.05426 | 1
3284 | 0 | 0.036268 | 0.88078 | 0 | 1 | 1 | 0 | 0.036268 | 1
3285 | 0 | 0.02321 | 0.88078 | 0 | 1 | 1 | 0 | 0.02321 | 1
3286 | 0 | 0.010056 | 0.88078 | 0 | 0 | 1 | 0 | 0.010056 | 1
3287 | 0 | 0.0021972 | 0.88078 | 0 | 0 | 1 | 0 | 0.0021972 | 1
3288 | 0 | 0.0012519 | 0.88078 | 0 | 0 | 1 | 0 | 0.0012519 | 1
3289 | 0 | 0.018671 | 0.88078 | 0 | 0 | 1 | 0 | 0.018671 | 1
3290 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3291 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3292 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3293 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3294 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3295 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3296 | 0 | 0.0021562 | 0.88078 | 0 | 0 | 1 | 0 | 0.0021562 | 1
3297 | 0.096076 | 0 | 0.88078 | 0 | 0 | 1 | 0.096076 | 0 | 1
3298 | 0.31777 | 0.0019069 | 0.88078 | 0 | 0 | 1 | 0.31777 | 0.0019069 | 1
3299 | 0.36307 | 0.041091 | 0.88078 | 0 | 0 | 1 | 0.36307 | 0.041091 | 1
3300 | 0.33959 | 0.091228 | 0.88078 | 0 | 0 | 1 | 0.33959 | 0.091228 | 1
3301 | 0.35603 | 0.099456 | 0.88078 | 0 | 0 | 1 | 0.35603 | 0.099456 | 1
3302 | 0.17693 | 0.076861 | 0.88078 | 0 | 0 | 1 | 0.17693 | 0.076861 | 1
3303 | 0.14902 | 0.062482 | 0.88078 | 0 | 0 | 1 | 0.14902 | 0.062482 | 1
3304 | 0.074816 | 0.040111 | 0.88078 | 0 | 0 | 1 | 0.074816 | 0.040111 | 1
3305 | 0 | 0.0096126 | 0.88078 | 0 | 0 | 1 | 0 | 0.0096126 | 1
3306 | 0 | 0.023312 | 0.88078 | 0 | 1 | 1 | 0 | 0.023312 | 1
3307 | 0 | 0.015569 | 0.88078 | 0 | 1 | 1 | 0 | 0.015569 | 1
3308 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3309 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3310 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3311 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3312 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3313 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3314 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3315 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3316 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3317 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3318 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3319 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3320 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3321 | 0.2026 | 0.0051682 | 0.88078 | 0 | 0 | 1 | 0.2026 | 0.0051682 | 1
3322 | 0.335 | 0.00083324 | 0.88078 | 0 | 0 | 1 | 0.335 | 0.00083324 | 1
3323 | 0.33229 | 0.026669 | 0.88078 | 0 | 0 | 1 | 0.33229 | 0.026669 | 1
3324 | 0.277 | 0.06607 | 0.88078 | 0 | 0 | 1 | 0.277 | 0.06607 | 1
3325 | 0.32358 | 0.088199 | 0.88078 | 0 | 0 | 1 | 0.32358 | 0.088199 | 1
3326 | 0.16739 | 0.084441 | 0.88078 | 0 | 0 | 1 | 0.16739 | 0.084441 | 1
3327 | 0.063217 | 0.063506 | 0.88078 | 0 | 0 | 1 | 0.063217 | 0.063506 | 1
3328 | 0 | 0.032311 | 0.88078 | 0 | 0 | 1 | 0 | 0.032311 | 1
3329 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3330 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3331 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3332 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3333 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3334 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3335 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3336 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3337 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3338 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3339 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3340 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3341 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3342 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3343 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3344 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3345 | 0.17487 | 0.0035705 | 0.88078 | 0 | 0 | 1 | 0.17487 | 0.0035705 | 1
3346 | 0.31478 | 0.0076966 | 0.88078 | 0 | 0 | 1 | 0.31478 | 0.0076966 | 1
3347 | 0.34061 | 0.024739 | 0.88078 | 0 | 0 | 1 | 0.34061 | 0.024739 | 1
3348 | 0.31406 | 0.036947 | 0.88078 | 0 | 0 | 1 | 0.31406 | 0.036947 | 1
3349 | 0.38343 | 0.060397 | 0.88078 | 0 | 0 | 1 | 0.38343 | 0.060397 | 1
3350 | 0.28112 | 0.066497 | 0.88078 | 0 | 0 | 1 | 0.28112 | 0.066497 | 1
3351 | 0.12184 | 0.039761 | 0.88078 | 0 | 0 | 1 | 0.12184 | 0.039761 | 1
3352 | 0.024041 | 0.015173 | 0.88078 | 0 | 0 | 1 | 0.024041 | 0.015173 | 1
3353 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3354 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3355 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3356 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3357 | 0 | 0.0026406 | 0.88078 | 0 | 1 | 1 | 0 | 0.0026406 | 1
3358 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3359 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3360 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3361 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3362 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3363 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3364 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3365 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3366 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3367 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3368 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3369 | 0.20281 | 0 | 0.88078 | 0 | 0 | 1 | 0.20281 | 0 | 1
3370 | 0.34146 | 0.013799 | 0.88078 | 0 | 0 | 1 | 0.34146 | 0.013799 | 1
3371 | 0.38365 | 0.018511 | 0.88078 | 0 | 0 | 1 | 0.38365 | 0.018511 | 1
3372 | 0.37421 | 0.025454 | 0.88078 | 0 | 0 | 1 | 0.37421 | 0.025454 | 1
3373 | 0.40536 | 0.046078 | 0.88078 | 0 | 0 | 1 | 0.40536 | 0.046078 | 1
3374 | 0.37741 | 0.042697 | 0.88078 | 0 | 0 | 1 | 0.37741 | 0.042697 | 1
3375 | 0.21154 | 0.011797 | 0.88078 | 0 | 0 | 1 | 0.21154 | 0.011797 | 1
3376 | 0.11225 | 0.0025399 | 0.88078 | 0 | 0 | 1 | 0.11225 | 0.0025399 | 1
3377 | 0 | 0.0056433 | 0.88078 | 0 | 0 | 1 | 0 | 0.0056433 | 1
3378 | 0 | 0.016961 | 0.88078 | 0 | 1 | 1 | 0 | 0.016961 | 1
3379 | 0 | 0.0048443 | 0.88078 | 0 | 1 | 1 | 0 | 0.0048443 | 1
3380 | 0 | 0.0041807 | 0.88078 | 0 | 1 | 1 | 0 | 0.0041807 | 1
3381 | 0 | 0.012434 | 0.88078 | 0 | 1 | 1 | 0 | 0.012434 | 1
3382 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3383 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3384 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3385 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3386 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3387 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3388 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3389 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3390 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3391 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3392 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3393 | 0.18703 | 0 | 0.88078 | 0 | 0 | 1 | 0.18703 | 0 | 1
3394 | 0.32253 | 0.0050269 | 0.88078 | 0 | 0 | 1 | 0.32253 | 0.0050269 | 1
3395 | 0.41639 | 0.021098 | 0.88078 | 0 | 0 | 1 | 0.41639 | 0.021098 | 1
3396 | 0.49121 | 0.044488 | 0.88078 | 0 | 0 | 1 | 0.49121 | 0.044488 | 1
3397 | 0.48991 | 0.05957 | 0.88078 | 0 | 0 | 1 | 0.48991 | 0.05957 | 1
3398 | 0.47931 | 0.047011 | 0.88078 | 0 | 0 | 1 | 0.47931 | 0.047011 | 1
3399 | 0.34631 | 0.030188 | 0.88078 | 0 | 0 | 1 | 0.34631 | 0.030188 | 1
3400 | 0.21223 | 0.035183 | 0.88078 | 0 | 0 | 1 | 0.21223 | 0.035183 | 1
3401 | 0.04711 | 0.0501 | 0.88078 | 0 | 0 | 1 | 0.04711 | 0.0501 | 1
3402 | 0 | 0.039799 | 0.88078 | 0 | 1 | 1 | 0 | 0.039799 | 1
3403 | 0 | 0.02893 | 0.88078 | 0 | 1 | 1 | 0 | 0.02893 | 1
3404 | 0 | 0.0085853 | 0.88078 | 0 | 1 | 1 | 0 | 0.0085853 | 1
3405 | 0 | 0.013048 | 0.88078 | 0 | 1 | 1 | 0 | 0.013048 | 1
3406 | 0 | 0.0028048 | 0.88078 | 0 | 0 | 1 | 0 | 0.0028048 | 1
3407 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3408 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3409 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3410 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3411 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3412 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3413 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3414 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3415 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3416 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3417 | 0.11641 | 0 | 0.88078 | 0 | 0 | 1 | 0.11641 | 0 | 1
3418 | 0.29052 | 0 | 0.88078 | 0 | 0 | 1 | 0.29052 | 0 | 1
3419 | 0.39804 | 0.0095408 | 0.88078 | 0 | 0 | 1 | 0.39804 | 0.0095408 | 1
3420 | 0.45905 | 0.041525 | 0.88078 | 0 | 0 | 1 | 0.45905 | 0.041525 | 1
3421 | 0.36996 | 0.046113 | 0.88078 | 0 | 0 | 1 | 0.36996 | 0.046113 | 1
3422 | 0.3451 | 0.036954 | 0.88078 | 0 | 0 | 1 | 0.3451 | 0.036954 | 1
3423 | 0.24498 | 0.033898 | 0.88078 | 0 | 0 | 1 | 0.24498 | 0.033898 | 1
3424 | 0.18239 | 0.046011 | 0.88078 | 0 | 0 | 1 | 0.18239 | 0.046011 | 1
3425 | 0.040003 | 0.065791 | 0.88078 | 0 | 0 | 1 | 0.040003 | 0.065791 | 1
3426 | 0 | 0.048465 | 0.88078 | 0 | 1 | 1 | 0 | 0.048465 | 1
3427 | 0 | 0.038904 | 0.88078 | 0 | 1 | 1 | 0 | 0.038904 | 1
3428 | 0 | 0.013381 | 0.88078 | 0 | 1 | 1 | 0 | 0.013381 | 1
3429 | 0 | 0.028165 | 0.88078 | 0 | 1 | 1 | 0 | 0.028165 | 1
3430 | 0 | 0.022422 | 0.88078 | 0 | 0 | 1 | 0 | 0.022422 | 1
3431 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3432 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3433 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3434 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3435 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3436 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3437 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3438 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3439 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3440 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3441 | 0.089901 | 0 | 0.88078 | 0 | 0 | 1 | 0.089901 | 0 | 1
3442 | 0.24532 | 0 | 0.88078 | 0 | 0 | 1 | 0.24532 | 0 | 1
3443 | 0.32871 | 0.029441 | 0.88078 | 0 | 0 | 1 | 0.32871 | 0.029441 | 1
3444 | 0.32453 | 0.058641 | 0.88078 | 0 | 0 | 1 | 0.32453 | 0.058641 | 1
3445 | 0.21406 | 0.052559 | 0.88078 | 0 | 0 | 1 | 0.21406 | 0.052559 | 1
3446 | 0.15123 | 0.055977 | 0.88078 | 0 | 0 | 1 | 0.15123 | 0.055977 | 1
3447 | 0.083465 | 0.05501 | 0.88078 | 0 | 0 | 1 | 0.083465 | 0.05501 | 1
3448 | 0.023048 | 0.072899 | 0.88078 | 0 | 0 | 1 | 0.023048 | 0.072899 | 1
3449 | 0 | 0.058864 | 0.88078 | 0 | 0 | 1 | 0 | 0.058864 | 1
3450 | 0 | 0.044826 | 0.88078 | 0 | 1 | 1 | 0 | 0.044826 | 1
3451 | 0 | 0.018582 | 0.88078 | 0 | 1 | 1 | 0 | 0.018582 | 1
3452 | 0 | 0 | 0.88078 | 0 | 1 | 1 | 0 | 0 | 1
3453 | 0 | 0.0032225 | 0.88078 | 0 | 1 | 1 | 0 | 0.0032225 | 1
3454 | 0 | 0.0034134 | 0.88078 | 0 | 0 | 1 | 0 | 0.0034134 | 1
3455 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3456 | 0 | 0 | 0.88078 | 0 | 0 | 1 | 0 | 0 | 1
3457 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3458 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3459 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3460 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3461 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3462 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3463 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3464 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3465 | 0.1181 | 0 | 0.96684 | 0 | 0 | 1 | 0.1181 | 0 | 1
3466 | 0.2725 | 0 | 0.96684 | 0 | 0 | 1 | 0.2725 | 0 | 1
3467 | 0.29867 | 0.0056856 | 0.96684 | 0 | 0 | 1 | 0.29867 | 0.0056856 | 1
3468 | 0.26225 | 0.027489 | 0.96684 | 0 | 0 | 1 | 0.26225 | 0.027489 | 1
3469 | 0.16245 | 0.024641 | 0.96684 | 0 | 0 | 1 | 0.16245 | 0.024641 | 1
3470 | 0.048039 | 0.026718 | 0.96684 | 0 | 0 | 1 | 0.048039 | 0.026718 | 1
3471 | 0.03906 | 0.016093 | 0.96684 | 0 | 0 | 1 | 0.03906 | 0.016093 | 1
3472 | 0.0098611 | 0.04271 | 0.96684 | 0 | 0 | 1 | 0.0098611 | 0.04271 | 1
3473 | 0 | 0.033741 | 0.96684 | 0 | 0 | 1 | 0 | 0.033741 | 1
3474 | 0 | 0.037898 | 0.96684 | 0 | 1 | 1 | 0 | 0.037898 | 1
3475 | 0 | 0.014758 | 0.96684 | 0 | 1 | 1 | 0 | 0.014758 | 1
3476 | 0 | 0 | 0.96684 | 0 | 1 | 1 | 0 | 0 | 1
3477 | 0 | 0.020341 | 0.96684 | 0 | 1 | 1 | 0 | 0.020341 | 1
3478 | 0 | 0.020922 | 0.96684 | 0 | 0 | 1 | 0 | 0.020922 | 1
3479 | 0 | 0.0038058 | 0.96684 | 0 | 0 | 1 | 0 | 0.0038058 | 1
3480 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3481 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3482 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3483 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3484 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3485 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3486 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3487 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3488 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3489 | 0.19827 | 0 | 0.96684 | 0 | 0 | 1 | 0.19827 | 0 | 1
3490 | 0.33533 | 0.010334 | 0.96684 | 0 | 0 | 1 | 0.33533 | 0.010334 | 1
3491 | 0.28697 | 0.028807 | 0.96684 | 0 | 0 | 1 | 0.28697 | 0.028807 | 1
3492 | 0.20093 | 0.033015 | 0.96684 | 0 | 0 | 1 | 0.20093 | 0.033015 | 1
3493 | 0.12922 | 0.031116 | 0.96684 | 0 | 0 | 1 | 0.12922 | 0.031116 | 1
3494 | 0.018823 | 0.029269 | 0.96684 | 0 | 0 | 1 | 0.018823 | 0.029269 | 1
3495 | 0.027456 | 0.019013 | 0.96684 | 0 | 0 | 1 | 0.027456 | 0.019013 | 1
3496 | 0 | 0.041685 | 0.96684 | 0 | 0 | 1 | 0 | 0.041685 | 1
3497 | 0 | 0.024715 | 0.96684 | 0 | 0 | 1 | 0 | 0.024715 | 1
3498 | 0 | 0.031155 | 0.96684 | 0 | 1 | 1 | 0 | 0.031155 | 1
3499 | 0 | 0.010784 | 0.96684 | 0 | 1 | 1 | 0 | 0.010784 | 1
3500 | 0 | 0.0041193 | 0.96684 | 0 | 1 | 1 | 0 | 0.0041193 | 1
3501 | 0 | 0.014554 | 0.96684 | 0 | 1 | 1 | 0 | 0.014554 | 1
3502 | 0 | 0.0080235 | 0.96684 | 0 | 0 | 1 | 0 | 0.0080235 | 1
3503 | 0 | 0.001684 | 0.96684 | 0 | 0 | 1 | 0 | 0.001684 | 1
3504 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3505 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3506 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3507 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3508 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3509 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3510 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3511 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3512 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3513 | 0.14923 | 0 | 0.96684 | 0 | 0 | 1 | 0.14923 | 0 | 1
3514 | 0.28599 | 0.0051232 | 0.96684 | 0 | 0 | 1 | 0.28599 | 0.0051232 | 1
3515 | 0.27606 | 0.0087854 | 0.96684 | 0 | 0 | 1 | 0.27606 | 0.0087854 | 1
3516 | 0.19608 | 0.020275 | 0.96684 | 0 | 0 | 1 | 0.19608 | 0.020275 | 1
3517 | 0.18482 | 0.03993 | 0.96684 | 0 | 0 | 1 | 0.18482 | 0.03993 | 1
3518 | 0.11086 | 0.039146 | 0.96684 | 0 | 0 | 1 | 0.11086 | 0.039146 | 1
3519 | 0.068801 | 0.034924 | 0.96684 | 0 | 0 | 1 | 0.068801 | 0.034924 | 1
3520 | 0.033146 | 0.039449 | 0.96684 | 0 | 0 | 1 | 0.033146 | 0.039449 | 1
3521 | 0 | 0.031632 | 0.96684 | 0 | 0 | 1 | 0 | 0.031632 | 1
3522 | 0 | 0.020055 | 0.96684 | 0 | 1 | 1 | 0 | 0.020055 | 1
3523 | 0 | 0.013465 | 0.96684 | 0 | 1 | 1 | 0 | 0.013465 | 1
3524 | 0 | 0.0015992 | 0.96684 | 0 | 1 | 1 | 0 | 0.0015992 | 1
3525 | 0 | 0.011896 | 0.96684 | 0 | 1 | 1 | 0 | 0.011896 | 1
3526 | 0 | 0.00034401 | 0.96684 | 0 | 0 | 1 | 0 | 0.00034401 | 1
3527 | 0 | 0.00057696 | 0.96684 | 0 | 0 | 1 | 0 | 0.00057696 | 1
3528 | 0 | 0 | 0.96684 | 0 | 0 | 1 | 0 | 0 | 1
3529 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3530 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3531 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3532 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3533 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3534 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3535 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3536 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3537 | 0.092416 | 0 | 0.91055 | 0 | 0 | 1 | 0.092416 | 0 | 1
3538 | 0.25322 | 0 | 0.91055 | 0 | 0 | 1 | 0.25322 | 0 | 1
3539 | 0.30915 | 0 | 0.91055 | 0 | 0 | 1 | 0.30915 | 0 | 1
3540 | 0.23831 | 0 | 0.91055 | 0 | 0 | 1 | 0.23831 | 0 | 1
3541 | 0.2275 | 0.004108 | 0.91055 | 0 | 0 | 1 | 0.2275 | 0.004108 | 1
3542 | 0.21232 | 0.011856 | 0.91055 | 0 | 0 | 1 | 0.21232 | 0.011856 | 1
3543 | 0.049496 | 0.016165 | 0.91055 | 0 | 0 | 1 | 0.049496 | 0.016165 | 1
3544 | 0 | 2.7225e-05 | 0.91055 | 0 | 0 | 1 | 0 | 2.7225e-05 | 1
3545 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3546 | 0 | 0 | 0.91055 | 0 | 1 | 1 | 0 | 0 | 1
3547 | 0 | 0 | 0.91055 | 0 | 1 | 1 | 0 | 0 | 1
3548 | 0 | 0 | 0.91055 | 0 | 1 | 1 | 0 | 0 | 1
3549 | 0 | 0 | 0.91055 | 0 | 1 | 1 | 0 | 0 | 1
3550 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3551 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3552 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3553 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3554 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3555 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3556 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3557 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3558 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3559 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3560 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3561 | 0.054521 | 0 | 0.91055 | 0 | 0 | 1 | 0.054521 | 0 | 1
3562 | 0.16764 | 0 | 0.91055 | 0 | 0 | 1 | 0.16764 | 0 | 1
3563 | 0.22922 | 0 | 0.91055 | 0 | 0 | 1 | 0.22922 | 0 | 1
3564 | 0.2097 | 0.0051694 | 0.91055 | 0 | 0 | 1 | 0.2097 | 0.0051694 | 1
3565 | 0.19214 | 0.03057 | 0.91055 | 0 | 0 | 1 | 0.19214 | 0.03057 | 1
3566 | 0.17501 | 0.057102 | 0.91055 | 0 | 0 | 1 | 0.17501 | 0.057102 | 1
3567 | 0.012912 | 0.056775 | 0.91055 | 0 | 0 | 1 | 0.012912 | 0.056775 | 1
3568 | 0 | 0.045833 | 0.91055 | 0 | 0 | 1 | 0 | 0.045833 | 1
3569 | 0 | 0.045394 | 0.91055 | 0 | 0 | 1 | 0 | 0.045394 | 1
3570 | 0 | 0.038686 | 0.91055 | 0 | 1 | 1 | 0 | 0.038686 | 1
3571 | 0 | 0.039845 | 0.91055 | 0 | 1 | 1 | 0 | 0.039845 | 1
3572 | 0 | 0.028335 | 0.91055 | 0 | 1 | 1 | 0 | 0.028335 | 1
3573 | 0 | 0.012071 | 0.91055 | 0 | 1 | 1 | 0 | 0.012071 | 1
3574 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3575 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3576 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3577 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3578 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3579 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3580 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3581 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3582 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3583 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3584 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3585 | 0.045503 | 0 | 0.91055 | 0 | 0 | 1 | 0.045503 | 0 | 1
3586 | 0.11048 | 0 | 0.91055 | 0 | 0 | 1 | 0.11048 | 0 | 1
3587 | 0.1929 | 0.03035 | 0.91055 | 0 | 0 | 1 | 0.1929 | 0.03035 | 1
3588 | 0.17186 | 0.071607 | 0.91055 | 0 | 0 | 1 | 0.17186 | 0.071607 | 1
3589 | 0.15247 | 0.093098 | 0.91055 | 0 | 0 | 1 | 0.15247 | 0.093098 | 1
3590 | 0.12068 | 0.13123 | 0.91055 | 0 | 0 | 1 | 0.12068 | 0.13123 | 1
3591 | 0 | 0.13259 | 0.91055 | 0 | 0 | 1 | 0 | 0.13259 | 1
3592 | 0 | 0.11764 | 0.91055 | 0 | 0 | 1 | 0 | 0.11764 | 1
3593 | 0 | 0.10757 | 0.91055 | 0 | 0 | 1 | 0 | 0.10757 | 1
3594 | 0 | 0.10549 | 0.91055 | 0 | 1 | 1 | 0 | 0.10549 | 1
3595 | 0 | 0.11238 | 0.91055 | 0 | 1 | 1 | 0 | 0.11238 | 1
3596 | 0 | 0.095843 | 0.91055 | 0 | 1 | 1 | 0 | 0.095843 | 1
3597 | 0 | 0.055503 | 0.91055 | 0 | 1 | 1 | 0 | 0.055503 | 1
3598 | 0 | 0.046485 | 0.91055 | 0 | 0 | 1 | 0 | 0.046485 | 1
3599 | 0 | 0.030316 | 0.91055 | 0 | 0 | 1 | 0 | 0.030316 | 1
3600 | 0 | 0.011325 | 0.91055 | 0 | 0 | 1 | 0 | 0.011325 | 1
3601 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3602 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3603 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3604 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3605 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3606 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3607 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3608 | 0 | 0.0019487 | 0.91055 | 0 | 0 | 1 | 0 | 0.0019487 | 1
3609 | 0.057389 | 0.036861 | 0.91055 | 0 | 0 | 1 | 0.057389 | 0.036861 | 1
3610 | 0.10499 | 0.082231 | 0.91055 | 0 | 0 | 1 | 0.10499 | 0.082231 | 1
3611 | 0.16061 | 0.13823 | 0.91055 | 0 | 0 | 1 | 0.16061 | 0.13823 | 1
3612 | 0.12291 | 0.19272 | 0.91055 | 0 | 0 | 1 | 0.12291 | 0.19272 | 1
3613 | 0.076365 | 0.22699 | 0.91055 | 0 | 0 | 1 | 0.076365 | 0.22699 | 1
3614 | 0.076943 | 0.27476 | 0.91055 | 0 | 0 | 1 | 0.076943 | 0.27476 | 1
3615 | 0.016037 | 0.28049 | 0.91055 | 0 | 0 | 1 | 0.016037 | 0.28049 | 1
3616 | 0 | 0.24089 | 0.91055 | 0 | 0 | 1 | 0 | 0.24089 | 1
3617 | 0 | 0.24033 | 0.91055 | 0 | 0 | 1 | 0 | 0.24033 | 1
3618 | 0 | 0.22668 | 0.91055 | 0 | 1 | 1 | 0 | 0.22668 | 1
3619 | 0 | 0.21711 | 0.91055 | 0 | 1 | 1 | 0 | 0.21711 | 1
3620 | 0 | 0.17749 | 0.91055 | 0 | 1 | 1 | 0 | 0.17749 | 1
3621 | 0 | 0.14258 | 0.91055 | 0 | 1 | 1 | 0 | 0.14258 | 1
3622 | 0 | 0.14745 | 0.91055 | 0 | 0 | 1 | 0 | 0.14745 | 1
3623 | 0 | 0.1208 | 0.91055 | 0 | 0 | 1 | 0 | 0.1208 | 1
3624 | 0 | 0.11096 | 0.91055 | 0 | 0 | 1 | 0 | 0.11096 | 1
3625 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3626 | 0 | 0.056905 | 0.91055 | 0 | 0 | 1 | 0 | 0.056905 | 1
3627 | 0 | 0.060766 | 0.91055 | 0 | 0 | 1 | 0 | 0.060766 | 1
3628 | 0 | 0.066591 | 0.91055 | 0 | 0 | 1 | 0 | 0.066591 | 1
3629 | 0 | 0.062457 | 0.91055 | 0 | 0 | 1 | 0 | 0.062457 | 1
3630 | 0 | 0.060213 | 0.91055 | 0 | 0 | 1 | 0 | 0.060213 | 1
3631 | 0 | 0.068698 | 0.91055 | 0 | 0 | 1 | 0 | 0.068698 | 1
3632 | 0 | 0.08799 | 0.91055 | 0 | 0 | 1 | 0 | 0.08799 | 1
3633 | 0.024614 | 0.13106 | 0.91055 | 0 | 0 | 1 | 0.024614 | 0.13106 | 1
3634 | 0.09389 | 0.17481 | 0.91055 | 0 | 0 | 1 | 0.09389 | 0.17481 | 1
3635 | 0.1443 | 0.20033 | 0.91055 | 0 | 0 | 1 | 0.1443 | 0.20033 | 1
3636 | 0.11846 | 0.21719 | 0.91055 | 0 | 0 | 1 | 0.11846 | 0.21719 | 1
3637 | 0.083387 | 0.23848 | 0.91055 | 0 | 0 | 1 | 0.083387 | 0.23848 | 1
3638 | 0.11716 | 0.27866 | 0.91055 | 0 | 0 | 1 | 0.11716 | 0.27866 | 1
3639 | 0.05226 | 0.28419 | 0.91055 | 0 | 0 | 1 | 0.05226 | 0.28419 | 1
3640 | 0 | 0.23036 | 0.91055 | 0 | 0 | 1 | 0 | 0.23036 | 1
3641 | 0 | 0.21544 | 0.91055 | 0 | 0 | 1 | 0 | 0.21544 | 1
3642 | 0 | 0.17937 | 0.91055 | 0 | 1 | 1 | 0 | 0.17937 | 1
3643 | 0 | 0.14876 | 0.91055 | 0 | 1 | 1 | 0 | 0.14876 | 1
3644 | 0 | 0.11196 | 0.91055 | 0 | 1 | 1 | 0 | 0.11196 | 1
3645 | 0 | 0.10067 | 0.91055 | 0 | 1 | 1 | 0 | 0.10067 | 1
3646 | 0 | 0.095946 | 0.91055 | 0 | 0 | 1 | 0 | 0.095946 | 1
3647 | 0 | 0.054506 | 0.91055 | 0 | 0 | 1 | 0 | 0.054506 | 1
3648 | 0 | 0.051246 | 0.91055 | 0 | 0 | 1 | 0 | 0.051246 | 1
3649 | 0 | 0.089979 | 0.91055 | 0 | 0 | 1 | 0 | 0.089979 | 1
3650 | 0 | 0.021475 | 0.91055 | 0 | 0 | 1 | 0 | 0.021475 | 1
3651 | 0 | 0.036852 | 0.91055 | 0 | 0 | 1 | 0 | 0.036852 | 1
3652 | 0 | 0.027888 | 0.91055 | 0 | 0 | 1 | 0 | 0.027888 | 1
3653 | 0 | 0.021125 | 0.91055 | 0 | 0 | 1 | 0 | 0.021125 | 1
3654 | 0 | 0.017299 | 0.91055 | 0 | 0 | 1 | 0 | 0.017299 | 1
3655 | 0 | 0.023368 | 0.91055 | 0 | 0 | 1 | 0 | 0.023368 | 1
3656 | 0 | 0.037275 | 0.91055 | 0 | 0 | 1 | 0 | 0.037275 | 1
3657 | 0.083715 | 0.084122 | 0.91055 | 0 | 0 | 1 | 0.083715 | 0.084122 | 1
3658 | 0.17418 | 0.12947 | 0.91055 | 0 | 0 | 1 | 0.17418 | 0.12947 | 1
3659 | 0.1682 | 0.16553 | 0.91055 | 0 | 0 | 1 | 0.1682 | 0.16553 | 1
3660 | 0.18359 | 0.18095 | 0.91055 | 0 | 0 | 1 | 0.18359 | 0.18095 | 1
3661 | 0.12761 | 0.20532 | 0.91055 | 0 | 0 | 1 | 0.12761 | 0.20532 | 1
3662 | 0.13086 | 0.22081 | 0.91055 | 0 | 0 | 1 | 0.13086 | 0.22081 | 1
3663 | 0.1665 | 0.21151 | 0.91055 | 0 | 0 | 1 | 0.1665 | 0.21151 | 1
3664 | 0.080355 | 0.19583 | 0.91055 | 0 | 0 | 1 | 0.080355 | 0.19583 | 1
3665 | 0 | 0.18306 | 0.91055 | 0 | 0 | 1 | 0 | 0.18306 | 1
3666 | 0 | 0.13548 | 0.91055 | 0 | 1 | 1 | 0 | 0.13548 | 1
3667 | 0 | 0.10754 | 0.91055 | 0 | 1 | 1 | 0 | 0.10754 | 1
3668 | 0 | 0.075457 | 0.91055 | 0 | 1 | 1 | 0 | 0.075457 | 1
3669 | 0 | 0.097819 | 0.91055 | 0 | 1 | 1 | 0 | 0.097819 | 1
3670 | 0 | 0.091541 | 0.91055 | 0 | 0 | 1 | 0 | 0.091541 | 1
3671 | 0 | 0.049276 | 0.91055 | 0 | 0 | 1 | 0 | 0.049276 | 1
3672 | 0 | 0.073173 | 0.91055 | 0 | 0 | 1 | 0 | 0.073173 | 1
3673 | 0 | 0.044054 | 0.91055 | 0 | 0 | 1 | 0 | 0.044054 | 1
3674 | 0 | 0.050917 | 0.91055 | 0 | 0 | 1 | 0 | 0.050917 | 1
3675 | 0 | 0.045416 | 0.91055 | 0 | 0 | 1 | 0 | 0.045416 | 1
3676 | 0 | 0.021604 | 0.91055 | 0 | 0 | 1 | 0 | 0.021604 | 1
3677 | 0 | 0.016457 | 0.91055 | 0 | 0 | 1 | 0 | 0.016457 | 1
3678 | 0 | 0.0080807 | 0.91055 | 0 | 0 | 1 | 0 | 0.0080807 | 1
3679 | 0 | 0.020675 | 0.91055 | 0 | 0 | 1 | 0 | 0.020675 | 1
3680 | 0 | 0.035218 | 0.91055 | 0 | 0 | 1 | 0 | 0.035218 | 1
3681 | 0.053353 | 0.072454 | 0.91055 | 0 | 0 | 1 | 0.053353 | 0.072454 | 1
3682 | 0.085846 | 0.10925 | 0.91055 | 0 | 0 | 1 | 0.085846 | 0.10925 | 1
3683 | 0.16134 | 0.14423 | 0.91055 | 0 | 0 | 1 | 0.16134 | 0.14423 | 1
3684 | 0.19696 | 0.15748 | 0.91055 | 0 | 0 | 1 | 0.19696 | 0.15748 | 1
3685 | 0.21462 | 0.17844 | 0.91055 | 0 | 0 | 1 | 0.21462 | 0.17844 | 1
3686 | 0.21176 | 0.19052 | 0.91055 | 0 | 0 | 1 | 0.21176 | 0.19052 | 1
3687 | 0.22335 | 0.17307 | 0.91055 | 0 | 0 | 1 | 0.22335 | 0.17307 | 1
3688 | 0.16691 | 0.17701 | 0.91055 | 0 | 0 | 1 | 0.16691 | 0.17701 | 1
3689 | 0.042984 | 0.14721 | 0.91055 | 0 | 0 | 1 | 0.042984 | 0.14721 | 1
3690 | 0 | 0.10279 | 0.91055 | 0 | 1 | 1 | 0 | 0.10279 | 1
3691 | 0 | 0.090982 | 0.91055 | 0 | 1 | 1 | 0 | 0.090982 | 1
3692 | 0 | 0.063858 | 0.91055 | 0 | 1 | 1 | 0 | 0.063858 | 1
3693 | 0 | 0.069294 | 0.91055 | 0 | 1 | 1 | 0 | 0.069294 | 1
3694 | 0 | 0.069404 | 0.91055 | 0 | 0 | 1 | 0 | 0.069404 | 1
3695 | 0 | 0.041249 | 0.91055 | 0 | 0 | 1 | 0 | 0.041249 | 1
3696 | 0 | 0.035196 | 0.91055 | 0 | 0 | 1 | 0 | 0.035196 | 1
3697 | 0 | 0.073592 | 0.91055 | 0 | 0 | 1 | 0 | 0.073592 | 1
3698 | 0 | 0.020933 | 0.91055 | 0 | 0 | 1 | 0 | 0.020933 | 1
3699 | 0 | 0.021215 | 0.91055 | 0 | 0 | 1 | 0 | 0.021215 | 1
3700 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3701 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3702 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3703 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3704 | 0 | 5.5743e-05 | 0.91055 | 0 | 0 | 1 | 0 | 5.5743e-05 | 1
3705 | 0.1089 | 0.031082 | 0.91055 | 0 | 0 | 1 | 0.1089 | 0.031082 | 1
3706 | 0.15618 | 0.062962 | 0.91055 | 0 | 0 | 1 | 0.15618 | 0.062962 | 1
3707 | 0.2594 | 0.097676 | 0.91055 | 0 | 0 | 1 | 0.2594 | 0.097676 | 1
3708 | 0.31433 | 0.12463 | 0.91055 | 0 | 0 | 1 | 0.31433 | 0.12463 | 1
3709 | 0.29135 | 0.15278 | 0.91055 | 0 | 0 | 1 | 0.29135 | 0.15278 | 1
3710 | 0.26474 | 0.1597 | 0.91055 | 0 | 0 | 1 | 0.26474 | 0.1597 | 1
3711 | 0.27766 | 0.14025 | 0.91055 | 0 | 0 | 1 | 0.27766 | 0.14025 | 1
3712 | 0.20785 | 0.14443 | 0.91055 | 0 | 0 | 1 | 0.20785 | 0.14443 | 1
3713 | 0.069297 | 0.11569 | 0.91055 | 0 | 0 | 1 | 0.069297 | 0.11569 | 1
3714 | 0 | 0.096753 | 0.91055 | 0 | 1 | 1 | 0 | 0.096753 | 1
3715 | 0 | 0.094869 | 0.91055 | 0 | 1 | 1 | 0 | 0.094869 | 1
3716 | 0 | 0.057019 | 0.91055 | 0 | 1 | 1 | 0 | 0.057019 | 1
3717 | 0 | 0.043532 | 0.91055 | 0 | 1 | 1 | 0 | 0.043532 | 1
3718 | 0 | 0.05285 | 0.91055 | 0 | 0 | 1 | 0 | 0.05285 | 1
3719 | 0 | 0.050566 | 0.91055 | 0 | 0 | 1 | 0 | 0.050566 | 1
3720 | 0 | 0.048494 | 0.91055 | 0 | 0 | 1 | 0 | 0.048494 | 1
3721 | 0 | 0.028326 | 0.91055 | 0 | 0 | 1 | 0 | 0.028326 | 1
3722 | 0 | 0.031151 | 0.91055 | 0 | 0 | 1 | 0 | 0.031151 | 1
3723 | 0 | 0.026467 | 0.91055 | 0 | 0 | 1 | 0 | 0.026467 | 1
3724 | 0 | 0.021122 | 0.91055 | 0 | 0 | 1 | 0 | 0.021122 | 1
3725 | 0 | 0.016424 | 0.91055 | 0 | 0 | 1 | 0 | 0.016424 | 1
3726 | 0 | 0.0092959 | 0.91055 | 0 | 0 | 1 | 0 | 0.0092959 | 1
3727 | 0 | 0.024048 | 0.91055 | 0 | 0 | 1 | 0 | 0.024048 | 1
3728 | 0 | 0.039214 | 0.91055 | 0 | 0 | 1 | 0 | 0.039214 | 1
3729 | 0.10221 | 0.066299 | 0.91055 | 0 | 0 | 1 | 0.10221 | 0.066299 | 1
3730 | 0.17228 | 0.090765 | 0.91055 | 0 | 0 | 1 | 0.17228 | 0.090765 | 1
3731 | 0.3097 | 0.1235 | 0.91055 | 0 | 0 | 1 | 0.3097 | 0.1235 | 1
3732 | 0.35185 | 0.15472 | 0.91055 | 0 | 0 | 1 | 0.35185 | 0.15472 | 1
3733 | 0.31995 | 0.17247 | 0.91055 | 0 | 0 | 1 | 0.31995 | 0.17247 | 1
3734 | 0.31999 | 0.18006 | 0.91055 | 0 | 0 | 1 | 0.31999 | 0.18006 | 1
3735 | 0.28697 | 0.16744 | 0.91055 | 0 | 0 | 1 | 0.28697 | 0.16744 | 1
3736 | 0.15839 | 0.15349 | 0.91055 | 0 | 0 | 1 | 0.15839 | 0.15349 | 1
3737 | 0.042231 | 0.12341 | 0.91055 | 0 | 0 | 1 | 0.042231 | 0.12341 | 1
3738 | 0 | 0.12753 | 0.91055 | 0 | 1 | 1 | 0 | 0.12753 | 1
3739 | 0 | 0.10666 | 0.91055 | 0 | 1 | 1 | 0 | 0.10666 | 1
3740 | 0 | 0.068079 | 0.91055 | 0 | 1 | 1 | 0 | 0.068079 | 1
3741 | 0 | 0.049262 | 0.91055 | 0 | 1 | 1 | 0 | 0.049262 | 1
3742 | 0 | 0.050214 | 0.91055 | 0 | 0 | 1 | 0 | 0.050214 | 1
3743 | 0 | 0.068059 | 0.91055 | 0 | 0 | 1 | 0 | 0.068059 | 1
3744 | 0 | 0.050249 | 0.91055 | 0 | 0 | 1 | 0 | 0.050249 | 1
3745 | 0 | 0.045717 | 0.91055 | 0 | 0 | 1 | 0 | 0.045717 | 1
3746 | 0 | 0.0088745 | 0.91055 | 0 | 0 | 1 | 0 | 0.0088745 | 1
3747 | 0 | 0.016913 | 0.91055 | 0 | 0 | 1 | 0 | 0.016913 | 1
3748 | 0 | 0.035326 | 0.91055 | 0 | 0 | 1 | 0 | 0.035326 | 1
3749 | 0 | 0.036855 | 0.91055 | 0 | 0 | 1 | 0 | 0.036855 | 1
3750 | 0 | 0.02782 | 0.91055 | 0 | 0 | 1 | 0 | 0.02782 | 1
3751 | 0 | 0.047212 | 0.91055 | 0 | 0 | 1 | 0 | 0.047212 | 1
3752 | 0 | 0.075504 | 0.91055 | 0 | 0 | 1 | 0 | 0.075504 | 1
3753 | 0.099479 | 0.10104 | 0.91055 | 0 | 0 | 1 | 0.099479 | 0.10104 | 1
3754 | 0.25241 | 0.13086 | 0.91055 | 0 | 0 | 1 | 0.25241 | 0.13086 | 1
3755 | 0.35015 | 0.15743 | 0.91055 | 0 | 0 | 1 | 0.35015 | 0.15743 | 1
3756 | 0.37935 | 0.18363 | 0.91055 | 0 | 0 | 1 | 0.37935 | 0.18363 | 1
3757 | 0.34139 | 0.19262 | 0.91055 | 0 | 0 | 1 | 0.34139 | 0.19262 | 1
3758 | 0.3787 | 0.19939 | 0.91055 | 0 | 0 | 1 | 0.3787 | 0.19939 | 1
3759 | 0.34569 | 0.18774 | 0.91055 | 0 | 0 | 1 | 0.34569 | 0.18774 | 1
3760 | 0.19158 | 0.17202 | 0.91055 | 0 | 0 | 1 | 0.19158 | 0.17202 | 1
3761 | 0.047358 | 0.13798 | 0.91055 | 0 | 0 | 1 | 0.047358 | 0.13798 | 1
3762 | 0 | 0.14876 | 0.91055 | 0 | 1 | 1 | 0 | 0.14876 | 1
3763 | 0 | 0.12913 | 0.91055 | 0 | 1 | 1 | 0 | 0.12913 | 1
3764 | 0 | 0.085107 | 0.91055 | 0 | 1 | 1 | 0 | 0.085107 | 1
3765 | 0 | 0.070681 | 0.91055 | 0 | 1 | 1 | 0 | 0.070681 | 1
3766 | 0 | 0.060836 | 0.91055 | 0 | 0 | 1 | 0 | 0.060836 | 1
3767 | 0 | 0.074915 | 0.91055 | 0 | 0 | 1 | 0 | 0.074915 | 1
3768 | 0 | 0.072595 | 0.91055 | 0 | 0 | 1 | 0 | 0.072595 | 1
3769 | 0 | 0.039737 | 0.91055 | 0 | 0 | 1 | 0 | 0.039737 | 1
3770 | 0 | 0.050214 | 0.91055 | 0 | 0 | 1 | 0 | 0.050214 | 1
3771 | 0 | 0.046178 | 0.91055 | 0 | 0 | 1 | 0 | 0.046178 | 1
3772 | 0 | 0.056016 | 0.91055 | 0 | 0 | 1 | 0 | 0.056016 | 1
3773 | 0 | 0.063231 | 0.91055 | 0 | 0 | 1 | 0 | 0.063231 | 1
3774 | 0 | 0.04942 | 0.91055 | 0 | 0 | 1 | 0 | 0.04942 | 1
3775 | 0 | 0.070666 | 0.91055 | 0 | 0 | 1 | 0 | 0.070666 | 1
3776 | 0 | 0.093383 | 0.91055 | 0 | 0 | 1 | 0 | 0.093383 | 1
3777 | 0.099301 | 0.11583 | 0.91055 | 0 | 0 | 1 | 0.099301 | 0.11583 | 1
3778 | 0.2766 | 0.14781 | 0.91055 | 0 | 0 | 1 | 0.2766 | 0.14781 | 1
3779 | 0.35162 | 0.17605 | 0.91055 | 0 | 0 | 1 | 0.35162 | 0.17605 | 1
3780 | 0.35445 | 0.19981 | 0.91055 | 0 | 0 | 1 | 0.35445 | 0.19981 | 1
3781 | 0.33599 | 0.203 | 0.91055 | 0 | 0 | 1 | 0.33599 | 0.203 | 1
3782 | 0.35255 | 0.19241 | 0.91055 | 0 | 0 | 1 | 0.35255 | 0.19241 | 1
3783 | 0.30703 | 0.19036 | 0.91055 | 0 | 0 | 1 | 0.30703 | 0.19036 | 1
3784 | 0.18376 | 0.17733 | 0.91055 | 0 | 0 | 1 | 0.18376 | 0.17733 | 1
3785 | 0.044572 | 0.14251 | 0.91055 | 0 | 0 | 1 | 0.044572 | 0.14251 | 1
3786 | 0 | 0.15931 | 0.91055 | 0 | 1 | 1 | 0 | 0.15931 | 1
3787 | 0 | 0.13458 | 0.91055 | 0 | 1 | 1 | 0 | 0.13458 | 1
3788 | 0 | 0.10462 | 0.91055 | 0 | 1 | 1 | 0 | 0.10462 | 1
3789 | 0 | 0.10545 | 0.91055 | 0 | 1 | 1 | 0 | 0.10545 | 1
3790 | 0 | 0.1078 | 0.91055 | 0 | 0 | 1 | 0 | 0.1078 | 1
3791 | 0 | 0.10494 | 0.91055 | 0 | 0 | 1 | 0 | 0.10494 | 1
3792 | 0 | 0.091498 | 0.91055 | 0 | 0 | 1 | 0 | 0.091498 | 1
3793 | 0 | 0.069911 | 0.91055 | 0 | 0 | 1 | 0 | 0.069911 | 1
3794 | 0 | 0.063826 | 0.91055 | 0 | 0 | 1 | 0 | 0.063826 | 1
3795 | 0 | 0.042761 | 0.91055 | 0 | 0 | 1 | 0 | 0.042761 | 1
3796 | 0 | 0.064649 | 0.91055 | 0 | 0 | 1 | 0 | 0.064649 | 1
3797 | 0 | 0.081667 | 0.91055 | 0 | 0 | 1 | 0 | 0.081667 | 1
3798 | 0 | 0.069906 | 0.91055 | 0 | 0 | 1 | 0 | 0.069906 | 1
3799 | 0 | 0.086295 | 0.91055 | 0 | 0 | 1 | 0 | 0.086295 | 1
3800 | 0 | 0.084227 | 0.91055 | 0 | 0 | 1 | 0 | 0.084227 | 1
3801 | 0.10866 | 0.13005 | 0.91055 | 0 | 0 | 1 | 0.10866 | 0.13005 | 1
3802 | 0.27368 | 0.1664 | 0.91055 | 0 | 0 | 1 | 0.27368 | 0.1664 | 1
3803 | 0.27017 | 0.18509 | 0.91055 | 0 | 0 | 1 | 0.27017 | 0.18509 | 1
3804 | 0.31393 | 0.19583 | 0.91055 | 0 | 0 | 1 | 0.31393 | 0.19583 | 1
3805 | 0.33681 | 0.20816 | 0.91055 | 0 | 0 | 1 | 0.33681 | 0.20816 | 1
3806 | 0.34723 | 0.19473 | 0.91055 | 0 | 0 | 1 | 0.34723 | 0.19473 | 1
3807 | 0.19677 | 0.1786 | 0.91055 | 0 | 0 | 1 | 0.19677 | 0.1786 | 1
3808 | 0.15064 | 0.1822 | 0.91055 | 0 | 0 | 1 | 0.15064 | 0.1822 | 1
3809 | 0.015386 | 0.14868 | 0.91055 | 0 | 0 | 1 | 0.015386 | 0.14868 | 1
3810 | 0 | 0.15744 | 0.91055 | 0 | 1 | 1 | 0 | 0.15744 | 1
3811 | 0 | 0.12791 | 0.91055 | 0 | 1 | 1 | 0 | 0.12791 | 1
3812 | 0 | 0.11202 | 0.91055 | 0 | 1 | 1 | 0 | 0.11202 | 1
3813 | 0 | 0.11674 | 0.91055 | 0 | 1 | 1 | 0 | 0.11674 | 1
3814 | 0 | 0.12726 | 0.91055 | 0 | 0 | 1 | 0 | 0.12726 | 1
3815 | 0 | 0.10351 | 0.91055 | 0 | 0 | 1 | 0 | 0.10351 | 1
3816 | 0 | 0.082581 | 0.91055 | 0 | 0 | 1 | 0 | 0.082581 | 1
3817 | 0 | 0.086958 | 0.91055 | 0 | 0 | 1 | 0 | 0.086958 | 1
3818 | 0 | 0.056174 | 0.91055 | 0 | 0 | 1 | 0 | 0.056174 | 1
3819 | 0 | 0.038587 | 0.91055 | 0 | 0 | 1 | 0 | 0.038587 | 1
3820 | 0 | 0.036659 | 0.91055 | 0 | 0 | 1 | 0 | 0.036659 | 1
3821 | 0 | 0.060057 | 0.91055 | 0 | 0 | 1 | 0 | 0.060057 | 1
3822 | 0 | 0.052451 | 0.91055 | 0 | 0 | 1 | 0 | 0.052451 | 1
3823 | 0 | 0.069995 | 0.91055 | 0 | 0 | 1 | 0 | 0.069995 | 1
3824 | 0 | 0.057381 | 0.91055 | 0 | 0 | 1 | 0 | 0.057381 | 1
3825 | 0.13828 | 0.10242 | 0.91055 | 0 | 0 | 1 | 0.13828 | 0.10242 | 1
3826 | 0.2979 | 0.12755 | 0.91055 | 0 | 0 | 1 | 0.2979 | 0.12755 | 1
3827 | 0.27262 | 0.16385 | 0.91055 | 0 | 0 | 1 | 0.27262 | 0.16385 | 1
3828 | 0.29733 | 0.17894 | 0.91055 | 0 | 0 | 1 | 0.29733 | 0.17894 | 1
3829 | 0.33138 | 0.20687 | 0.91055 | 0 | 0 | 1 | 0.33138 | 0.20687 | 1
3830 | 0.31145 | 0.18289 | 0.91055 | 0 | 0 | 1 | 0.31145 | 0.18289 | 1
3831 | 0.19997 | 0.15967 | 0.91055 | 0 | 0 | 1 | 0.19997 | 0.15967 | 1
3832 | 0.097369 | 0.16611 | 0.91055 | 0 | 0 | 1 | 0.097369 | 0.16611 | 1
3833 | 0 | 0.13309 | 0.91055 | 0 | 0 | 1 | 0 | 0.13309 | 1
3834 | 0 | 0.14413 | 0.91055 | 0 | 1 | 1 | 0 | 0.14413 | 1
3835 | 0 | 0.10972 | 0.91055 | 0 | 1 | 1 | 0 | 0.10972 | 1
3836 | 0 | 0.090224 | 0.91055 | 0 | 1 | 1 | 0 | 0.090224 | 1
3837 | 0 | 0.091175 | 0.91055 | 0 | 1 | 1 | 0 | 0.091175 | 1
3838 | 0 | 0.10037 | 0.91055 | 0 | 0 | 1 | 0 | 0.10037 | 1
3839 | 0 | 0.089122 | 0.91055 | 0 | 0 | 1 | 0 | 0.089122 | 1
3840 | 0 | 0.063422 | 0.91055 | 0 | 0 | 1 | 0 | 0.063422 | 1
3841 | 0 | 0.073079 | 0.91055 | 0 | 0 | 1 | 0 | 0.073079 | 1
3842 | 0 | 0.040607 | 0.91055 | 0 | 0 | 1 | 0 | 0.040607 | 1
3843 | 0 | 0.02136 | 0.91055 | 0 | 0 | 1 | 0 | 0.02136 | 1
3844 | 0 | 0.0058537 | 0.91055 | 0 | 0 | 1 | 0 | 0.0058537 | 1
3845 | 0 | 0.029456 | 0.91055 | 0 | 0 | 1 | 0 | 0.029456 | 1
3846 | 0 | 0.024363 | 0.91055 | 0 | 0 | 1 | 0 | 0.024363 | 1
3847 | 0 | 0.057963 | 0.91055 | 0 | 0 | 1 | 0 | 0.057963 | 1
3848 | 0 | 0.067723 | 0.91055 | 0 | 0 | 1 | 0 | 0.067723 | 1
3849 | 0.15032 | 0.11073 | 0.91055 | 0 | 0 | 1 | 0.15032 | 0.11073 | 1
3850 | 0.28601 | 0.14006 | 0.91055 | 0 | 0 | 1 | 0.28601 | 0.14006 | 1
3851 | 0.24659 | 0.18431 | 0.91055 | 0 | 0 | 1 | 0.24659 | 0.18431 | 1
3852 | 0.27164 | 0.21005 | 0.91055 | 0 | 0 | 1 | 0.27164 | 0.21005 | 1
3853 | 0.315 | 0.24784 | 0.91055 | 0 | 0 | 1 | 0.315 | 0.24784 | 1
3854 | 0.30172 | 0.2421 | 0.91055 | 0 | 0 | 1 | 0.30172 | 0.2421 | 1
3855 | 0.19284 | 0.20938 | 0.91055 | 0 | 0 | 1 | 0.19284 | 0.20938 | 1
3856 | 0.083339 | 0.21836 | 0.91055 | 0 | 0 | 1 | 0.083339 | 0.21836 | 1
3857 | 0 | 0.18385 | 0.91055 | 0 | 0 | 1 | 0 | 0.18385 | 1
3858 | 0 | 0.17322 | 0.91055 | 0 | 1 | 1 | 0 | 0.17322 | 1
3859 | 0 | 0.12447 | 0.91055 | 0 | 1 | 1 | 0 | 0.12447 | 1
3860 | 0 | 0.090152 | 0.91055 | 0 | 1 | 1 | 0 | 0.090152 | 1
3861 | 0 | 0.076216 | 0.91055 | 0 | 1 | 1 | 0 | 0.076216 | 1
3862 | 0 | 0.071187 | 0.91055 | 0 | 0 | 1 | 0 | 0.071187 | 1
3863 | 0 | 0.072291 | 0.91055 | 0 | 0 | 1 | 0 | 0.072291 | 1
3864 | 0 | 0.038897 | 0.91055 | 0 | 0 | 1 | 0 | 0.038897 | 1
3865 | 0 | 0.05623 | 0.91055 | 0 | 0 | 1 | 0 | 0.05623 | 1
3866 | 0 | 0.034531 | 0.91055 | 0 | 0 | 1 | 0 | 0.034531 | 1
3867 | 0 | 0.027485 | 0.91055 | 0 | 0 | 1 | 0 | 0.027485 | 1
3868 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3869 | 0 | 0.0073869 | 0.91055 | 0 | 0 | 1 | 0 | 0.0073869 | 1
3870 | 0 | 0.008048 | 0.91055 | 0 | 0 | 1 | 0 | 0.008048 | 1
3871 | 0 | 0.036623 | 0.91055 | 0 | 0 | 1 | 0 | 0.036623 | 1
3872 | 0 | 0.060893 | 0.91055 | 0 | 0 | 1 | 0 | 0.060893 | 1
3873 | 0.13102 | 0.088683 | 0.91055 | 0 | 0 | 1 | 0.13102 | 0.088683 | 1
3874 | 0.26241 | 0.12203 | 0.91055 | 0 | 0 | 1 | 0.26241 | 0.12203 | 1
3875 | 0.25115 | 0.17844 | 0.91055 | 0 | 0 | 1 | 0.25115 | 0.17844 | 1
3876 | 0.26184 | 0.23048 | 0.91055 | 0 | 0 | 1 | 0.26184 | 0.23048 | 1
3877 | 0.31892 | 0.25678 | 0.91055 | 0 | 0 | 1 | 0.31892 | 0.25678 | 1
3878 | 0.29863 | 0.25087 | 0.91055 | 0 | 0 | 1 | 0.29863 | 0.25087 | 1
3879 | 0.26479 | 0.23704 | 0.91055 | 0 | 0 | 1 | 0.26479 | 0.23704 | 1
3880 | 0.10984 | 0.24624 | 0.91055 | 0 | 0 | 1 | 0.10984 | 0.24624 | 1
3881 | 0.051051 | 0.19914 | 0.91055 | 0 | 0 | 1 | 0.051051 | 0.19914 | 1
3882 | 0 | 0.16589 | 0.91055 | 0 | 1 | 1 | 0 | 0.16589 | 1
3883 | 0 | 0.12631 | 0.91055 | 0 | 1 | 1 | 0 | 0.12631 | 1
3884 | 0 | 0.11093 | 0.91055 | 0 | 1 | 1 | 0 | 0.11093 | 1
3885 | 0 | 0.098452 | 0.91055 | 0 | 1 | 1 | 0 | 0.098452 | 1
3886 | 0 | 0.078898 | 0.91055 | 0 | 0 | 1 | 0 | 0.078898 | 1
3887 | 0 | 0.085922 | 0.91055 | 0 | 0 | 1 | 0 | 0.085922 | 1
3888 | 0 | 0.068127 | 0.91055 | 0 | 0 | 1 | 0 | 0.068127 | 1
3889 | 0 | 0.035625 | 0.91055 | 0 | 0 | 1 | 0 | 0.035625 | 1
3890 | 0 | 0.063186 | 0.91055 | 0 | 0 | 1 | 0 | 0.063186 | 1
3891 | 0 | 0.037409 | 0.91055 | 0 | 0 | 1 | 0 | 0.037409 | 1
3892 | 0 | 0.024893 | 0.91055 | 0 | 0 | 1 | 0 | 0.024893 | 1
3893 | 0 | 0.029264 | 0.91055 | 0 | 0 | 1 | 0 | 0.029264 | 1
3894 | 0 | 0.021272 | 0.91055 | 0 | 0 | 1 | 0 | 0.021272 | 1
3895 | 0 | 0.02626 | 0.91055 | 0 | 0 | 1 | 0 | 0.02626 | 1
3896 | 0 | 0.054702 | 0.91055 | 0 | 0 | 1 | 0 | 0.054702 | 1
3897 | 0.14714 | 0.081206 | 0.91055 | 0 | 0 | 1 | 0.14714 | 0.081206 | 1
3898 | 0.2763 | 0.13615 | 0.91055 | 0 | 0 | 1 | 0.2763 | 0.13615 | 1
3899 | 0.2434 | 0.17584 | 0.91055 | 0 | 0 | 1 | 0.2434 | 0.17584 | 1
3900 | 0.26372 | 0.23228 | 0.91055 | 0 | 0 | 1 | 0.26372 | 0.23228 | 1
3901 | 0.31355 | 0.25253 | 0.91055 | 0 | 0 | 1 | 0.31355 | 0.25253 | 1
3902 | 0.29046 | 0.27267 | 0.91055 | 0 | 0 | 1 | 0.29046 | 0.27267 | 1
3903 | 0.25191 | 0.27307 | 0.91055 | 0 | 0 | 1 | 0.25191 | 0.27307 | 1
3904 | 0.13334 | 0.26338 | 0.91055 | 0 | 0 | 1 | 0.13334 | 0.26338 | 1
3905 | 0.042593 | 0.23642 | 0.91055 | 0 | 0 | 1 | 0.042593 | 0.23642 | 1
3906 | 0 | 0.21533 | 0.91055 | 0 | 1 | 1 | 0 | 0.21533 | 1
3907 | 0 | 0.1685 | 0.91055 | 0 | 1 | 1 | 0 | 0.1685 | 1
3908 | 0 | 0.14884 | 0.91055 | 0 | 1 | 1 | 0 | 0.14884 | 1
3909 | 0 | 0.12447 | 0.91055 | 0 | 1 | 1 | 0 | 0.12447 | 1
3910 | 0 | 0.10217 | 0.91055 | 0 | 0 | 1 | 0 | 0.10217 | 1
3911 | 0 | 0.099998 | 0.91055 | 0 | 0 | 1 | 0 | 0.099998 | 1
3912 | 0 | 0.08524 | 0.91055 | 0 | 0 | 1 | 0 | 0.08524 | 1
3913 | 0 | 0.072907 | 0.91055 | 0 | 0 | 1 | 0 | 0.072907 | 1
3914 | 0 | 0.053533 | 0.91055 | 0 | 0 | 1 | 0 | 0.053533 | 1
3915 | 0 | 0.026963 | 0.91055 | 0 | 0 | 1 | 0 | 0.026963 | 1
3916 | 0 | 0.038968 | 0.91055 | 0 | 0 | 1 | 0 | 0.038968 | 1
3917 | 0 | 0.034874 | 0.91055 | 0 | 0 | 1 | 0 | 0.034874 | 1
3918 | 0 | 0.024587 | 0.91055 | 0 | 0 | 1 | 0 | 0.024587 | 1
3919 | 0 | 0.030972 | 0.91055 | 0 | 0 | 1 | 0 | 0.030972 | 1
3920 | 0 | 0.032891 | 0.91055 | 0 | 0 | 1 | 0 | 0.032891 | 1
3921 | 0.16395 | 0.060964 | 0.91055 | 0 | 0 | 1 | 0.16395 | 0.060964 | 1
3922 | 0.27764 | 0.1231 | 0.91055 | 0 | 0 | 1 | 0.27764 | 0.1231 | 1
3923 | 0.24942 | 0.16694 | 0.91055 | 0 | 0 | 1 | 0.24942 | 0.16694 | 1
3924 | 0.28109 | 0.23047 | 0.91055 | 0 | 0 | 1 | 0.28109 | 0.23047 | 1
3925 | 0.28263 | 0.24143 | 0.91055 | 0 | 0 | 1 | 0.28263 | 0.24143 | 1
3926 | 0.27107 | 0.27882 | 0.91055 | 0 | 0 | 1 | 0.27107 | 0.27882 | 1
3927 | 0.28738 | 0.26192 | 0.91055 | 0 | 0 | 1 | 0.28738 | 0.26192 | 1
3928 | 0.17569 | 0.24274 | 0.91055 | 0 | 0 | 1 | 0.17569 | 0.24274 | 1
3929 | 0.035494 | 0.22369 | 0.91055 | 0 | 0 | 1 | 0.035494 | 0.22369 | 1
3930 | 0 | 0.1676 | 0.91055 | 0 | 1 | 1 | 0 | 0.1676 | 1
3931 | 0 | 0.12982 | 0.91055 | 0 | 1 | 1 | 0 | 0.12982 | 1
3932 | 0 | 0.18193 | 0.91055 | 0 | 1 | 1 | 0 | 0.18193 | 1
3933 | 0 | 0.16033 | 0.91055 | 0 | 1 | 1 | 0 | 0.16033 | 1
3934 | 0 | 0.15321 | 0.91055 | 0 | 0 | 1 | 0 | 0.15321 | 1
3935 | 0 | 0.1332 | 0.91055 | 0 | 0 | 1 | 0 | 0.1332 | 1
3936 | 0 | 0.07663 | 0.91055 | 0 | 0 | 1 | 0 | 0.07663 | 1
3937 | 0 | 0.094376 | 0.91055 | 0 | 0 | 1 | 0 | 0.094376 | 1
3938 | 0 | 0.018109 | 0.91055 | 0 | 0 | 1 | 0 | 0.018109 | 1
3939 | 0 | 0.00026909 | 0.91055 | 0 | 0 | 1 | 0 | 0.00026909 | 1
3940 | 0 | 0.027127 | 0.91055 | 0 | 0 | 1 | 0 | 0.027127 | 1
3941 | 0 | 0.049353 | 0.91055 | 0 | 0 | 1 | 0 | 0.049353 | 1
3942 | 0 | 0.040585 | 0.91055 | 0 | 0 | 1 | 0 | 0.040585 | 1
3943 | 0 | 0.059321 | 0.91055 | 0 | 0 | 1 | 0 | 0.059321 | 1
3944 | 0 | 0.049435 | 0.91055 | 0 | 0 | 1 | 0 | 0.049435 | 1
3945 | 0.12257 | 0.068723 | 0.91055 | 0 | 0 | 1 | 0.12257 | 0.068723 | 1
3946 | 0.26237 | 0.12473 | 0.91055 | 0 | 0 | 1 | 0.26237 | 0.12473 | 1
3947 | 0.29916 | 0.16028 | 0.91055 | 0 | 0 | 1 | 0.29916 | 0.16028 | 1
3948 | 0.2551 | 0.21369 | 0.91055 | 0 | 0 | 1 | 0.2551 | 0.21369 | 1
3949 | 0.19195 | 0.22584 | 0.91055 | 0 | 0 | 1 | 0.19195 | 0.22584 | 1
3950 | 0.14254 | 0.24484 | 0.91055 | 0 | 0 | 1 | 0.14254 | 0.24484 | 1
3951 | 0.20118 | 0.23522 | 0.91055 | 0 | 0 | 1 | 0.20118 | 0.23522 | 1
3952 | 0.083276 | 0.2093 | 0.91055 | 0 | 0 | 1 | 0.083276 | 0.2093 | 1
3953 | 0.0077622 | 0.17345 | 0.91055 | 0 | 0 | 1 | 0.0077622 | 0.17345 | 1
3954 | 0 | 0.15074 | 0.91055 | 0 | 1 | 1 | 0 | 0.15074 | 1
3955 | 0 | 0.13905 | 0.91055 | 0 | 1 | 1 | 0 | 0.13905 | 1
3956 | 0 | 0.19342 | 0.91055 | 0 | 1 | 1 | 0 | 0.19342 | 1
3957 | 0 | 0.14147 | 0.91055 | 0 | 1 | 1 | 0 | 0.14147 | 1
3958 | 0 | 0.11313 | 0.91055 | 0 | 0 | 1 | 0 | 0.11313 | 1
3959 | 0 | 0.087099 | 0.91055 | 0 | 0 | 1 | 0 | 0.087099 | 1
3960 | 0 | 0.023305 | 0.91055 | 0 | 0 | 1 | 0 | 0.023305 | 1
3961 | 0 | 0.065639 | 0.91055 | 0 | 0 | 1 | 0 | 0.065639 | 1
3962 | 0 | 0.0094611 | 0.91055 | 0 | 0 | 1 | 0 | 0.0094611 | 1
3963 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3964 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3965 | 0 | 0.003895 | 0.91055 | 0 | 0 | 1 | 0 | 0.003895 | 1
3966 | 0 | 0.0072562 | 0.91055 | 0 | 0 | 1 | 0 | 0.0072562 | 1
3967 | 0 | 0.035716 | 0.91055 | 0 | 0 | 1 | 0 | 0.035716 | 1
3968 | 0 | 0.021163 | 0.91055 | 0 | 0 | 1 | 0 | 0.021163 | 1
3969 | 0.12699 | 0.059329 | 0.91055 | 0 | 0 | 1 | 0.12699 | 0.059329 | 1
3970 | 0.29477 | 0.10656 | 0.91055 | 0 | 0 | 1 | 0.29477 | 0.10656 | 1
3971 | 0.3573 | 0.14935 | 0.91055 | 0 | 0 | 1 | 0.3573 | 0.14935 | 1
3972 | 0.28816 | 0.19367 | 0.91055 | 0 | 0 | 1 | 0.28816 | 0.19367 | 1
3973 | 0.21453 | 0.20731 | 0.91055 | 0 | 0 | 1 | 0.21453 | 0.20731 | 1
3974 | 0.13064 | 0.2202 | 0.91055 | 0 | 0 | 1 | 0.13064 | 0.2202 | 1
3975 | 0.18181 | 0.20997 | 0.91055 | 0 | 0 | 1 | 0.18181 | 0.20997 | 1
3976 | 0.10796 | 0.17353 | 0.91055 | 0 | 0 | 1 | 0.10796 | 0.17353 | 1
3977 | 0.056113 | 0.16784 | 0.91055 | 0 | 0 | 1 | 0.056113 | 0.16784 | 1
3978 | 0 | 0.13368 | 0.91055 | 0 | 1 | 1 | 0 | 0.13368 | 1
3979 | 0 | 0.11996 | 0.91055 | 0 | 1 | 1 | 0 | 0.11996 | 1
3980 | 0 | 0.1598 | 0.91055 | 0 | 1 | 1 | 0 | 0.1598 | 1
3981 | 0 | 0.1338 | 0.91055 | 0 | 1 | 1 | 0 | 0.1338 | 1
3982 | 0 | 0.10964 | 0.91055 | 0 | 0 | 1 | 0 | 0.10964 | 1
3983 | 0 | 0.083761 | 0.91055 | 0 | 0 | 1 | 0 | 0.083761 | 1
3984 | 0 | 0.013359 | 0.91055 | 0 | 0 | 1 | 0 | 0.013359 | 1
3985 | 0 | 0.039009 | 0.91055 | 0 | 0 | 1 | 0 | 0.039009 | 1
3986 | 0 | 0.015355 | 0.91055 | 0 | 0 | 1 | 0 | 0.015355 | 1
3987 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
3988 | 0 | 0.0002928 | 0.91055 | 0 | 0 | 1 | 0 | 0.0002928 | 1
3989 | 0 | 0.0072203 | 0.91055 | 0 | 0 | 1 | 0 | 0.0072203 | 1
3990 | 0 | 0.013669 | 0.91055 | 0 | 0 | 1 | 0 | 0.013669 | 1
3991 | 0 | 0.036507 | 0.91055 | 0 | 0 | 1 | 0 | 0.036507 | 1
3992 | 0 | 0.03471 | 0.91055 | 0 | 0 | 1 | 0 | 0.03471 | 1
3993 | 0.080843 | 0.046978 | 0.91055 | 0 | 0 | 1 | 0.080843 | 0.046978 | 1
3994 | 0.27289 | 0.095487 | 0.91055 | 0 | 0 | 1 | 0.27289 | 0.095487 | 1
3995 | 0.36136 | 0.13422 | 0.91055 | 0 | 0 | 1 | 0.36136 | 0.13422 | 1
3996 | 0.29473 | 0.18096 | 0.91055 | 0 | 0 | 1 | 0.29473 | 0.18096 | 1
3997 | 0.22753 | 0.20234 | 0.91055 | 0 | 0 | 1 | 0.22753 | 0.20234 | 1
3998 | 0.13782 | 0.20408 | 0.91055 | 0 | 0 | 1 | 0.13782 | 0.20408 | 1
3999 | 0.15906 | 0.20515 | 0.91055 | 0 | 0 | 1 | 0.15906 | 0.20515 | 1
4000 | 0.075637 | 0.16743 | 0.91055 | 0 | 0 | 1 | 0.075637 | 0.16743 | 1
4001 | 0.057363 | 0.16729 | 0.91055 | 0 | 0 | 1 | 0.057363 | 0.16729 | 1
4002 | 0 | 0.18088 | 0.91055 | 0 | 1 | 1 | 0 | 0.18088 | 1
4003 | 0 | 0.17076 | 0.91055 | 0 | 1 | 1 | 0 | 0.17076 | 1
4004 | 0 | 0.15165 | 0.91055 | 0 | 1 | 1 | 0 | 0.15165 | 1
4005 | 0 | 0.13722 | 0.91055 | 0 | 1 | 1 | 0 | 0.13722 | 1
4006 | 0 | 0.088872 | 0.91055 | 0 | 0 | 1 | 0 | 0.088872 | 1
4007 | 0 | 0.069924 | 0.91055 | 0 | 0 | 1 | 0 | 0.069924 | 1
4008 | 0 | 0.042488 | 0.91055 | 0 | 0 | 1 | 0 | 0.042488 | 1
4009 | 0 | 0.035332 | 0.91055 | 0 | 0 | 1 | 0 | 0.035332 | 1
4010 | 0 | 0.039217 | 0.91055 | 0 | 0 | 1 | 0 | 0.039217 | 1
4011 | 0 | 0.019349 | 0.91055 | 0 | 0 | 1 | 0 | 0.019349 | 1
4012 | 0 | 0.0071998 | 0.91055 | 0 | 0 | 1 | 0 | 0.0071998 | 1
4013 | 0 | 0 | 0.91055 | 0 | 0 | 1 | 0 | 0 | 1
4014 | 0 | 0.012948 | 0.91055 | 0 | 0 | 1 | 0 | 0.012948 | 1
4015 | 0 | 0.025214 | 0.91055 | 0 | 0 | 1 | 0 | 0.025214 | 1
4016 | 0 | 0.037359 | 0.91055 | 0 | 0 | 1 | 0 | 0.037359 | 1
4017 | 0.05174 | 0.061674 | 0.91055 | 0 | 0 | 1 | 0.05174 | 0.061674 | 1
4018 | 0.24108 | 0.10545 | 0.91055 | 0 | 0 | 1 | 0.24108 | 0.10545 | 1
4019 | 0.3016 | 0.14053 | 0.91055 | 0 | 0 | 1 | 0.3016 | 0.14053 | 1
4020 | 0.2866 | 0.17124 | 0.91055 | 0 | 0 | 1 | 0.2866 | 0.17124 | 1
4021 | 0.32198 | 0.19071 | 0.91055 | 0 | 0 | 1 | 0.32198 | 0.19071 | 1
4022 | 0.27458 | 0.20411 | 0.91055 | 0 | 0 | 1 | 0.27458 | 0.20411 | 1
4023 | 0.25814 | 0.19692 | 0.91055 | 0 | 0 | 1 | 0.25814 | 0.19692 | 1
4024 | 0.21027 | 0.16496 | 0.91055 | 0 | 0 | 1 | 0.21027 | 0.16496 | 1
4025 | 0.09511 | 0.18364 | 0.91055 | 0 | 0 | 1 | 0.09511 | 0.18364 | 1
4026 | 0 | 0.16769 | 0.91055 | 0 | 1 | 1 | 0 | 0.16769 | 1
4027 | 0 | 0.13983 | 0.91055 | 0 | 1 | 1 | 0 | 0.13983 | 1
4028 | 0 | 0.11302 | 0.91055 | 0 | 1 | 1 | 0 | 0.11302 | 1
4029 | 0 | 0.11264 | 0.91055 | 0 | 1 | 1 | 0 | 0.11264 | 1
4030 | 0 | 0.092154 | 0.91055 | 0 | 0 | 1 | 0 | 0.092154 | 1
4031 | 0 | 0.069752 | 0.91055 | 0 | 0 | 1 | 0 | 0.069752 | 1
4032 | 0 | 0.054632 | 0.91055 | 0 | 0 | 1 | 0 | 0.054632 | 1
4033 | 0 | 0.076628 | 0.91055 | 0 | 0 | 1 | 0 | 0.076628 | 1
4034 | 0 | 0.029764 | 0.91055 | 0 | 0 | 1 | 0 | 0.029764 | 1
4035 | 0 | 0.024519 | 0.91055 | 0 | 0 | 1 | 0 | 0.024519 | 1
4036 | 0 | 0.018582 | 0.91055 | 0 | 0 | 1 | 0 | 0.018582 | 1
4037 | 0 | 0.0079395 | 0.91055 | 0 | 0 | 1 | 0 | 0.0079395 | 1
4038 | 0 | 0.032921 | 0.91055 | 0 | 0 | 1 | 0 | 0.032921 | 1
4039 | 0 | 0.013391 | 0.91055 | 0 | 0 | 1 | 0 | 0.013391 | 1
4040 | 0 | 0.046922 | 0.91055 | 0 | 0 | 1 | 0 | 0.046922 | 1
4041 | 0.05108 | 0.051687 | 0.91055 | 0 | 0 | 1 | 0.05108 | 0.051687 | 1
4042 | 0.24935 | 0.065365 | 0.91055 | 0 | 0 | 1 | 0.24935 | 0.065365 | 1
4043 | 0.32383 | 0.087029 | 0.91055 | 0 | 0 | 1 | 0.32383 | 0.087029 | 1
4044 | 0.31555 | 0.11619 | 0.91055 | 0 | 0 | 1 | 0.31555 | 0.11619 | 1
4045 | 0.34627 | 0.11986 | 0.91055 | 0 | 0 | 1 | 0.34627 | 0.11986 | 1
4046 | 0.34102 | 0.12925 | 0.91055 | 0 | 0 | 1 | 0.34102 | 0.12925 | 1
4047 | 0.34685 | 0.12857 | 0.91055 | 0 | 0 | 1 | 0.34685 | 0.12857 | 1
4048 | 0.25589 | 0.11033 | 0.91055 | 0 | 0 | 1 | 0.25589 | 0.11033 | 1
4049 | 0.1034 | 0.10121 | 0.91055 | 0 | 0 | 1 | 0.1034 | 0.10121 | 1
4050 | 0 | 0.08176 | 0.91055 | 0 | 1 | 1 | 0 | 0.08176 | 1
4051 | 0 | 0.067186 | 0.91055 | 0 | 1 | 1 | 0 | 0.067186 | 1
4052 | 0 | 0.088984 | 0.91055 | 0 | 1 | 1 | 0 | 0.088984 | 1
4053 | 0 | 0.10313 | 0.91055 | 0 | 1 | 1 | 0 | 0.10313 | 1
4054 | 0 | 0.074463 | 0.91055 | 0 | 0 | 1 | 0 | 0.074463 | 1
4055 | 0 | 0.0565 | 0.91055 | 0 | 0 | 1 | 0 | 0.0565 | 1
4056 | 0 | 0.049516 | 0.91055 | 0 | 0 | 1 | 0 | 0.049516 | 1
4057 | 0 | 0.06141 | 0.91055 | 0 | 0 | 1 | 0 | 0.06141 | 1
4058 | 0 | 0.022225 | 0.91055 | 0 | 0 | 1 | 0 | 0.022225 | 1
4059 | 0 | 0.01807 | 0.91055 | 0 | 0 | 1 | 0 | 0.01807 | 1
4060 | 0 | 0.019446 | 0.91055 | 0 | 0 | 1 | 0 | 0.019446 | 1
4061 | 0 | 0.00548 | 0.91055 | 0 | 0 | 1 | 0 | 0.00548 | 1
4062 | 0 | 0.011402 | 0.91055 | 0 | 0 | 1 | 0 | 0.011402 | 1
4063 | 0 | 0.020185 | 0.91055 | 0 | 0 | 1 | 0 | 0.020185 | 1
4064 | 0 | 0.048693 | 0.91055 | 0 | 0 | 1 | 0 | 0.048693 | 1
4065 | 0.060597 | 0.069989 | 0.91055 | 0 | 0 | 1 | 0.060597 | 0.069989 | 1
4066 | 0.2822 | 0.055251 | 0.91055 | 0 | 0 | 1 | 0.2822 | 0.055251 | 1
4067 | 0.36961 | 0.065001 | 0.91055 | 0 | 0 | 1 | 0.36961 | 0.065001 | 1
4068 | 0.27011 | 0.09531 | 0.91055 | 0 | 0 | 1 | 0.27011 | 0.09531 | 1
4069 | 0.33748 | 0.097948 | 0.91055 | 0 | 0 | 1 | 0.33748 | 0.097948 | 1
4070 | 0.28484 | 0.12088 | 0.91055 | 0 | 0 | 1 | 0.28484 | 0.12088 | 1
4071 | 0.28155 | 0.12147 | 0.91055 | 0 | 0 | 1 | 0.28155 | 0.12147 | 1
4072 | 0.23053 | 0.12049 | 0.91055 | 0 | 0 | 1 | 0.23053 | 0.12049 | 1
4073 | 0.106 | 0.10805 | 0.91055 | 0 | 0 | 1 | 0.106 | 0.10805 | 1
4074 | 0 | 0.079466 | 0.91055 | 0 | 1 | 1 | 0 | 0.079466 | 1
4075 | 0 | 0.059777 | 0.91055 | 0 | 1 | 1 | 0 | 0.059777 | 1
4076 | 0 | 0.086995 | 0.91055 | 0 | 1 | 1 | 0 | 0.086995 | 1
4077 | 0 | 0.098737 | 0.91055 | 0 | 1 | 1 | 0 | 0.098737 | 1
4078 | 0 | 0.081914 | 0.91055 | 0 | 0 | 1 | 0 | 0.081914 | 1
4079 | 0 | 0.070597 | 0.91055 | 0 | 0 | 1 | 0 | 0.070597 | 1
4080 | 0 | 0.052824 | 0.91055 | 0 | 0 | 1 | 0 | 0.052824 | 1
4081 | 0 | 0.040105 | 0.91055 | 0 | 0 | 1 | 0 | 0.040105 | 1
4082 | 0 | 0.029454 | 0.91055 | 0 | 0 | 1 | 0 | 0.029454 | 1
4083 | 0 | 0.030403 | 0.91055 | 0 | 0 | 1 | 0 | 0.030403 | 1
4084 | 0 | 0.032771 | 0.91055 | 0 | 0 | 1 | 0 | 0.032771 | 1
4085 | 0 | 0.013417 | 0.91055 | 0 | 0 | 1 | 0 | 0.013417 | 1
4086 | 0 | 0.0027146 | 0.91055 | 0 | 0 | 1 | 0 | 0.0027146 | 1
4087 | 0 | 0.015323 | 0.91055 | 0 | 0 | 1 | 0 | 0.015323 | 1
4088 | 0 | 0.012525 | 0.91055 | 0 | 0 | 1 | 0 | 0.012525 | 1
4089 | 0.13314 | 0.02324 | 0.91055 | 0 | 0 | 1 | 0.13314 | 0.02324 | 1
4090 | 0.35731 | 0.0041245 | 0.91055 | 0 | 0 | 1 | 0.35731 | 0.0041245 | 1
4091 | 0.43122 | 0.026161 | 0.91055 | 0 | 0 | 1 | 0.43122 | 0.026161 | 1
4092 | 0.29843 | 0.063699 | 0.91055 | 0 | 0 | 1 | 0.29843 | 0.063699 | 1
4093 | 0.31487 | 0.071751 | 0.91055 | 0 | 0 | 1 | 0.31487 | 0.071751 | 1
4094 | 0.21042 | 0.087213 | 0.91055 | 0 | 0 | 1 | 0.21042 | 0.087213 | 1
4095 | 0.19148 | 0.097077 | 0.91055 | 0 | 0 | 1 | 0.19148 | 0.097077 | 1
4096 | 0.15376 | 0.082647 | 0.91055 | 0 | 0 | 1 | 0.15376 | 0.082647 | 1
4097 | 0.081181 | 0.071159 | 0.91055 | 0 | 0 | 1 | 0.081181 | 0.071159 | 1
4098 | 0 | 0.070862 | 0.91055 | 0 | 1 | 1 | 0 | 0.070862 | 1
4099 | 0 | 0.08441 | 0.91055 | 0 | 1 | 1 | 0 | 0.08441 | 1
4100 | 0 | 0.099837 | 0.91055 | 0 | 1 | 1 | 0 | 0.099837 | 1
4101 | 0 | 0.096733 | 0.91055 | 0 | 1 | 1 | 0 | 0.096733 | 1
4102 | 0 | 0.075989 | 0.91055 | 0 | 0 | 1 | 0 | 0.075989 | 1
4103 | 0 | 0.077134 | 0.91055 | 0 | 0 | 1 | 0 | 0.077134 | 1
4104 | 0 | 0.075829 | 0.91055 | 0 | 0 | 1 | 0 | 0.075829 | 1
4105 | 0 | 0.035497 | 0.91055 | 0 | 0 | 1 | 0 | 0.035497 | 1
4106 | 0 | 0.050964 | 0.91055 | 0 | 0 | 1 | 0 | 0.050964 | 1
4107 | 0 | 0.036418 | 0.91055 | 0 | 0 | 1 | 0 | 0.036418 | 1
4108 | 0 | 0.042079 | 0.91055 | 0 | 0 | 1 | 0 | 0.042079 | 1
4109 | 0 | 0.021603 | 0.91055 | 0 | 0 | 1 | 0 | 0.021603 | 1
4110 | 0 | 0.016666 | 0.91055 | 0 | 0 | 1 | 0 | 0.016666 | 1
4111 | 0 | 0.046976 | 0.91055 | 0 | 0 | 1 | 0 | 0.046976 | 1
4112 | 0 | 0.027454 | 0.91055 | 0 | 0 | 1 | 0 | 0.027454 | 1
4113 | 0.13791 | 0.038597 | 0.91055 | 0 | 0 | 1 | 0.13791 | 0.038597 | 1
4114 | 0.34957 | 0.036269 | 0.91055 | 0 | 0 | 1 | 0.34957 | 0.036269 | 1
4115 | 0.42667 | 0.057275 | 0.91055 | 0 | 0 | 1 | 0.42667 | 0.057275 | 1
4116 | 0.30555 | 0.10575 | 0.91055 | 0 | 0 | 1 | 0.30555 | 0.10575 | 1
4117 | 0.31889 | 0.12859 | 0.91055 | 0 | 0 | 1 | 0.31889 | 0.12859 | 1
4118 | 0.13354 | 0.12736 | 0.91055 | 0 | 0 | 1 | 0.13354 | 0.12736 | 1
4119 | 0.16267 | 0.14955 | 0.91055 | 0 | 0 | 1 | 0.16267 | 0.14955 | 1
4120 | 0.12691 | 0.13778 | 0.91055 | 0 | 0 | 1 | 0.12691 | 0.13778 | 1
4121 | 0.062533 | 0.13007 | 0.91055 | 0 | 0 | 1 | 0.062533 | 0.13007 | 1
4122 | 0 | 0.12555 | 0.91055 | 0 | 1 | 1 | 0 | 0.12555 | 1
4123 | 0 | 0.12249 | 0.91055 | 0 | 1 | 1 | 0 | 0.12249 | 1
4124 | 0 | 0.095088 | 0.91055 | 0 | 1 | 1 | 0 | 0.095088 | 1
4125 | 0 | 0.087869 | 0.91055 | 0 | 1 | 1 | 0 | 0.087869 | 1
4126 | 0 | 0.08988 | 0.91055 | 0 | 0 | 1 | 0 | 0.08988 | 1
4127 | 0 | 0.08015 | 0.91055 | 0 | 0 | 1 | 0 | 0.08015 | 1
4128 | 0 | 0.071223 | 0.91055 | 0 | 0 | 1 | 0 | 0.071223 | 1
4129 | 0 | 0.068031 | 0.91055 | 0 | 0 | 1 | 0 | 0.068031 | 1
4130 | 0 | 0.066076 | 0.91055 | 0 | 0 | 1 | 0 | 0.066076 | 1
4131 | 0 | 0.060295 | 0.91055 | 0 | 0 | 1 | 0 | 0.060295 | 1
4132 | 0 | 0.061279 | 0.91055 | 0 | 0 | 1 | 0 | 0.061279 | 1
4133 | 0 | 0.041192 | 0.91055 | 0 | 0 | 1 | 0 | 0.041192 | 1
4134 | 0 | 0.035578 | 0.91055 | 0 | 0 | 1 | 0 | 0.035578 | 1
4135 | 0 | 0.060877 | 0.91055 | 0 | 0 | 1 | 0 | 0.060877 | 1
4136 | 0 | 0.04684 | 0.91055 | 0 | 0 | 1 | 0 | 0.04684 | 1
4137 | 0.13655 | 0.059624 | 0.91055 | 0 | 0 | 1 | 0.13655 | 0.059624 | 1
4138 | 0.36232 | 0.08003 | 0.91055 | 0 | 0 | 1 | 0.36232 | 0.08003 | 1
4139 | 0.38941 | 0.10342 | 0.91055 | 0 | 0 | 1 | 0.38941 | 0.10342 | 1
4140 | 0.40226 | 0.1474 | 0.91055 | 0 | 0 | 1 | 0.40226 | 0.1474 | 1
4141 | 0.38477 | 0.17031 | 0.91055 | 0 | 0 | 1 | 0.38477 | 0.17031 | 1
4142 | 0.22702 | 0.15469 | 0.91055 | 0 | 0 | 1 | 0.22702 | 0.15469 | 1
4143 | 0.27127 | 0.18645 | 0.91055 | 0 | 0 | 1 | 0.27127 | 0.18645 | 1
4144 | 0.19747 | 0.16637 | 0.91055 | 0 | 0 | 1 | 0.19747 | 0.16637 | 1
4145 | 0.079877 | 0.15676 | 0.91055 | 0 | 0 | 1 | 0.079877 | 0.15676 | 1
4146 | 0 | 0.14467 | 0.91055 | 0 | 1 | 1 | 0 | 0.14467 | 1
4147 | 0 | 0.13613 | 0.91055 | 0 | 1 | 1 | 0 | 0.13613 | 1
4148 | 0 | 0.10521 | 0.91055 | 0 | 1 | 1 | 0 | 0.10521 | 1
4149 | 0 | 0.10058 | 0.91055 | 0 | 1 | 1 | 0 | 0.10058 | 1
4150 | 0 | 0.10769 | 0.91055 | 0 | 0 | 1 | 0 | 0.10769 | 1
4151 | 0 | 0.087894 | 0.91055 | 0 | 0 | 1 | 0 | 0.087894 | 1
4152 | 0 | 0.092809 | 0.91055 | 0 | 0 | 1 | 0 | 0.092809 | 1
4153 | 0 | 0.076097 | 0.96684 | 0 | 0 | 1 | 0 | 0.076097 | 1
4154 | 0 | 0.082608 | 0.96684 | 0 | 0 | 1 | 0 | 0.082608 | 1
4155 | 0 | 0.067621 | 0.96684 | 0 | 0 | 1 | 0 | 0.067621 | 1
4156 | 0 | 0.068515 | 0.96684 | 0 | 0 | 1 | 0 | 0.068515 | 1
4157 | 0 | 0.0535 | 0.96684 | 0 | 0 | 1 | 0 | 0.0535 | 1
4158 | 0 | 0.042744 | 0.96684 | 0 | 0 | 1 | 0 | 0.042744 | 1
4159 | 0 | 0.061464 | 0.96684 | 0 | 0 | 1 | 0 | 0.061464 | 1
4160 | 0 | 0.09296 | 0.96684 | 0 | 0 | 1 | 0 | 0.09296 | 1
4161 | 0.11865 | 0.11546 | 0.96684 | 0 | 0 | 1 | 0.11865 | 0.11546 | 1
4162 | 0.33221 | 0.13137 | 0.96684 | 0 | 0 | 1 | 0.33221 | 0.13137 | 1
4163 | 0.34619 | 0.16227 | 0.96684 | 0 | 0 | 1 | 0.34619 | 0.16227 | 1
4164 | 0.4445 | 0.20589 | 0.96684 | 0 | 0 | 1 | 0.4445 | 0.20589 | 1
4165 | 0.38801 | 0.22652 | 0.96684 | 0 | 0 | 1 | 0.38801 | 0.22652 | 1
4166 | 0.2352 | 0.2184 | 0.96684 | 0 | 0 | 1 | 0.2352 | 0.2184 | 1
4167 | 0.29074 | 0.22883 | 0.96684 | 0 | 0 | 1 | 0.29074 | 0.22883 | 1
4168 | 0.19088 | 0.22773 | 0.96684 | 0 | 0 | 1 | 0.19088 | 0.22773 | 1
4169 | 0.10395 | 0.20539 | 0.96684 | 0 | 0 | 1 | 0.10395 | 0.20539 | 1
4170 | 0 | 0.18077 | 0.96684 | 0 | 1 | 1 | 0 | 0.18077 | 1
4171 | 0 | 0.15187 | 0.96684 | 0 | 1 | 1 | 0 | 0.15187 | 1
4172 | 0 | 0.11819 | 0.96684 | 0 | 1 | 1 | 0 | 0.11819 | 1
4173 | 0 | 0.11928 | 0.96684 | 0 | 1 | 1 | 0 | 0.11928 | 1
4174 | 0 | 0.12506 | 0.96684 | 0 | 0 | 1 | 0 | 0.12506 | 1
4175 | 0 | 0.10369 | 0.96684 | 0 | 0 | 1 | 0 | 0.10369 | 1
4176 | 0 | 0.10674 | 0.96684 | 0 | 0 | 1 | 0 | 0.10674 | 1
4177 | 0 | 0.095806 | 0.96684 | 0 | 0 | 1 | 0 | 0.095806 | 1
4178 | 0 | 0.075728 | 0.96684 | 0 | 0 | 1 | 0 | 0.075728 | 1
4179 | 0 | 0.064083 | 0.96684 | 0 | 0 | 1 | 0 | 0.064083 | 1
4180 | 0 | 0.054791 | 0.96684 | 0 | 0 | 1 | 0 | 0.054791 | 1
4181 | 0 | 0.04964 | 0.96684 | 0 | 0 | 1 | 0 | 0.04964 | 1
4182 | 0 | 0.036932 | 0.96684 | 0 | 0 | 1 | 0 | 0.036932 | 1
4183 | 0 | 0.054152 | 0.96684 | 0 | 0 | 1 | 0 | 0.054152 | 1
4184 | 0 | 0.095344 | 0.96684 | 0 | 0 | 1 | 0 | 0.095344 | 1
4185 | 0.10544 | 0.1378 | 0.96684 | 0 | 0 | 1 | 0.10544 | 0.1378 | 1
4186 | 0.30038 | 0.15536 | 0.96684 | 0 | 0 | 1 | 0.30038 | 0.15536 | 1
4187 | 0.31457 | 0.19844 | 0.96684 | 0 | 0 | 1 | 0.31457 | 0.19844 | 1
4188 | 0.4136 | 0.22993 | 0.96684 | 0 | 0 | 1 | 0.4136 | 0.22993 | 1
4189 | 0.38599 | 0.24801 | 0.96684 | 0 | 0 | 1 | 0.38599 | 0.24801 | 1
4190 | 0.3275 | 0.27925 | 0.96684 | 0 | 0 | 1 | 0.3275 | 0.27925 | 1
4191 | 0.29581 | 0.26692 | 0.96684 | 0 | 0 | 1 | 0.29581 | 0.26692 | 1
4192 | 0.19357 | 0.24953 | 0.96684 | 0 | 0 | 1 | 0.19357 | 0.24953 | 1
4193 | 0.10347 | 0.22224 | 0.96684 | 0 | 0 | 1 | 0.10347 | 0.22224 | 1
4194 | 0 | 0.21472 | 0.96684 | 0 | 1 | 1 | 0 | 0.21472 | 1
4195 | 0 | 0.19473 | 0.96684 | 0 | 1 | 1 | 0 | 0.19473 | 1
4196 | 0 | 0.17154 | 0.96684 | 0 | 1 | 1 | 0 | 0.17154 | 1
4197 | 0 | 0.17772 | 0.96684 | 0 | 1 | 1 | 0 | 0.17772 | 1
4198 | 0 | 0.16029 | 0.96684 | 0 | 0 | 1 | 0 | 0.16029 | 1
4199 | 0 | 0.14197 | 0.96684 | 0 | 0 | 1 | 0 | 0.14197 | 1
4200 | 0 | 0.15286 | 0.96684 | 0 | 0 | 1 | 0 | 0.15286 | 1
4201 | 0 | 0.086369 | 0.93132 | 0 | 0 | 1 | 0 | 0.086369 | 1
4202 | 0 | 0.12007 | 0.93132 | 0 | 0 | 1 | 0 | 0.12007 | 1
4203 | 0 | 0.063466 | 0.93132 | 0 | 0 | 1 | 0 | 0.063466 | 1
4204 | 0 | 0.043794 | 0.93132 | 0 | 0 | 1 | 0 | 0.043794 | 1
4205 | 0 | 0.04543 | 0.93132 | 0 | 0 | 1 | 0 | 0.04543 | 1
4206 | 0 | 0.025698 | 0.93132 | 0 | 0 | 1 | 0 | 0.025698 | 1
4207 | 0 | 0.045331 | 0.93132 | 0 | 0 | 1 | 0 | 0.045331 | 1
4208 | 0 | 0.073754 | 0.93132 | 0 | 0 | 1 | 0 | 0.073754 | 1
4209 | 0.10154 | 0.13408 | 0.93132 | 0 | 0 | 1 | 0.10154 | 0.13408 | 1
4210 | 0.25397 | 0.13983 | 0.93132 | 0 | 0 | 1 | 0.25397 | 0.13983 | 1
4211 | 0.23306 | 0.18735 | 0.93132 | 0 | 0 | 1 | 0.23306 | 0.18735 | 1
4212 | 0.35934 | 0.2208 | 0.93132 | 0 | 0 | 1 | 0.35934 | 0.2208 | 1
4213 | 0.34914 | 0.24426 | 0.93132 | 0 | 0 | 1 | 0.34914 | 0.24426 | 1
4214 | 0.29501 | 0.28655 | 0.93132 | 0 | 0 | 1 | 0.29501 | 0.28655 | 1
4215 | 0.24518 | 0.25486 | 0.93132 | 0 | 0 | 1 | 0.24518 | 0.25486 | 1
4216 | 0.13621 | 0.22765 | 0.93132 | 0 | 0 | 1 | 0.13621 | 0.22765 | 1
4217 | 0.079547 | 0.18297 | 0.93132 | 0 | 0 | 1 | 0.079547 | 0.18297 | 1
4218 | 0 | 0.19882 | 0.93132 | 0 | 1 | 1 | 0 | 0.19882 | 1
4219 | 0 | 0.19388 | 0.93132 | 0 | 1 | 1 | 0 | 0.19388 | 1
4220 | 0 | 0.14873 | 0.93132 | 0 | 1 | 1 | 0 | 0.14873 | 1
4221 | 0 | 0.1295 | 0.93132 | 0 | 1 | 1 | 0 | 0.1295 | 1
4222 | 0 | 0.11698 | 0.93132 | 0 | 0 | 1 | 0 | 0.11698 | 1
4223 | 0 | 0.11 | 0.93132 | 0 | 0 | 1 | 0 | 0.11 | 1
4224 | 0 | 0.12454 | 0.93132 | 0 | 0 | 1 | 0 | 0.12454 | 1
4225 | 0 | 0.12381 | 0.93132 | 0 | 0 | 1 | 0 | 0.12381 | 1
4226 | 0 | 0.1033 | 0.93132 | 0 | 0 | 1 | 0 | 0.1033 | 1
4227 | 0 | 0.049468 | 0.93132 | 0 | 0 | 1 | 0 | 0.049468 | 1
4228 | 0 | 0.033944 | 0.93132 | 0 | 0 | 1 | 0 | 0.033944 | 1
4229 | 0 | 0.032011 | 0.93132 | 0 | 0 | 1 | 0 | 0.032011 | 1
4230 | 0 | 0.017968 | 0.93132 | 0 | 0 | 1 | 0 | 0.017968 | 1
4231 | 0 | 0.048989 | 0.93132 | 0 | 0 | 1 | 0 | 0.048989 | 1
4232 | 0 | 0.060079 | 0.93132 | 0 | 0 | 1 | 0 | 0.060079 | 1
4233 | 0.1075 | 0.10868 | 0.93132 | 0 | 0 | 1 | 0.1075 | 0.10868 | 1
4234 | 0.27363 | 0.13544 | 0.93132 | 0 | 0 | 1 | 0.27363 | 0.13544 | 1
4235 | 0.25826 | 0.17366 | 0.93132 | 0 | 0 | 1 | 0.25826 | 0.17366 | 1
4236 | 0.30497 | 0.19848 | 0.93132 | 0 | 0 | 1 | 0.30497 | 0.19848 | 1
4237 | 0.30174 | 0.2238 | 0.93132 | 0 | 0 | 1 | 0.30174 | 0.2238 | 1
4238 | 0.27544 | 0.26049 | 0.93132 | 0 | 0 | 1 | 0.27544 | 0.26049 | 1
4239 | 0.21098 | 0.25639 | 0.93132 | 0 | 0 | 1 | 0.21098 | 0.25639 | 1
4240 | 0.15145 | 0.22868 | 0.93132 | 0 | 0 | 1 | 0.15145 | 0.22868 | 1
4241 | 0.01145 | 0.21371 | 0.93132 | 0 | 0 | 1 | 0.01145 | 0.21371 | 1
4242 | 0 | 0.21367 | 0.93132 | 0 | 1 | 1 | 0 | 0.21367 | 1
4243 | 0 | 0.16762 | 0.93132 | 0 | 1 | 1 | 0 | 0.16762 | 1
4244 | 0 | 0.14953 | 0.93132 | 0 | 1 | 1 | 0 | 0.14953 | 1
4245 | 0 | 0.1187 | 0.93132 | 0 | 1 | 1 | 0 | 0.1187 | 1
4246 | 0 | 0.077007 | 0.93132 | 0 | 0 | 1 | 0 | 0.077007 | 1
4247 | 0 | 0.059176 | 0.93132 | 0 | 0 | 1 | 0 | 0.059176 | 1
4248 | 0 | 0.061808 | 0.93132 | 0 | 0 | 1 | 0 | 0.061808 | 1
4249 | 0 | 0.10126 | 0.93132 | 0 | 0 | 1 | 0 | 0.10126 | 1
4250 | 0 | 0.071018 | 0.93132 | 0 | 0 | 1 | 0 | 0.071018 | 1
4251 | 0 | 0.028091 | 0.93132 | 0 | 0 | 1 | 0 | 0.028091 | 1
4252 | 0 | 0.015747 | 0.93132 | 0 | 0 | 1 | 0 | 0.015747 | 1
4253 | 0 | 0.028656 | 0.93132 | 0 | 0 | 1 | 0 | 0.028656 | 1
4254 | 0 | 0.012942 | 0.93132 | 0 | 0 | 1 | 0 | 0.012942 | 1
4255 | 0 | 0.034479 | 0.93132 | 0 | 0 | 1 | 0 | 0.034479 | 1
4256 | 0 | 0.034179 | 0.93132 | 0 | 0 | 1 | 0 | 0.034179 | 1
4257 | 0.098363 | 0.071906 | 0.93132 | 0 | 0 | 1 | 0.098363 | 0.071906 | 1
4258 | 0.29001 | 0.10066 | 0.93132 | 0 | 0 | 1 | 0.29001 | 0.10066 | 1
4259 | 0.24561 | 0.14392 | 0.93132 | 0 | 0 | 1 | 0.24561 | 0.14392 | 1
4260 | 0.23819 | 0.1778 | 0.93132 | 0 | 0 | 1 | 0.23819 | 0.1778 | 1
4261 | 0.2087 | 0.20393 | 0.93132 | 0 | 0 | 1 | 0.2087 | 0.20393 | 1
4262 | 0.15975 | 0.23048 | 0.93132 | 0 | 0 | 1 | 0.15975 | 0.23048 | 1
4263 | 0.14343 | 0.22743 | 0.93132 | 0 | 0 | 1 | 0.14343 | 0.22743 | 1
4264 | 0.10623 | 0.19519 | 0.93132 | 0 | 0 | 1 | 0.10623 | 0.19519 | 1
4265 | 0.004948 | 0.19004 | 0.93132 | 0 | 0 | 1 | 0.004948 | 0.19004 | 1
4266 | 0 | 0.20455 | 0.93132 | 0 | 1 | 1 | 0 | 0.20455 | 1
4267 | 0 | 0.14605 | 0.93132 | 0 | 1 | 1 | 0 | 0.14605 | 1
4268 | 0 | 0.10498 | 0.93132 | 0 | 1 | 1 | 0 | 0.10498 | 1
4269 | 0 | 0.053753 | 0.93132 | 0 | 1 | 1 | 0 | 0.053753 | 1
4270 | 0 | 0.010112 | 0.93132 | 0 | 0 | 1 | 0 | 0.010112 | 1
4271 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4272 | 0 | 0.002093 | 0.93132 | 0 | 0 | 1 | 0 | 0.002093 | 1
4273 | 0 | 0.047223 | 0.93132 | 0 | 0 | 1 | 0 | 0.047223 | 1
4274 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4275 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4276 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4277 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4278 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4279 | 0 | 0.012102 | 0.93132 | 0 | 0 | 1 | 0 | 0.012102 | 1
4280 | 0 | 0.0064299 | 0.93132 | 0 | 0 | 1 | 0 | 0.0064299 | 1
4281 | 0.10963 | 0.025343 | 0.93132 | 0 | 0 | 1 | 0.10963 | 0.025343 | 1
4282 | 0.32472 | 0.070471 | 0.93132 | 0 | 0 | 1 | 0.32472 | 0.070471 | 1
4283 | 0.33165 | 0.10583 | 0.93132 | 0 | 0 | 1 | 0.33165 | 0.10583 | 1
4284 | 0.22384 | 0.1369 | 0.93132 | 0 | 0 | 1 | 0.22384 | 0.1369 | 1
4285 | 0.16593 | 0.15161 | 0.93132 | 0 | 0 | 1 | 0.16593 | 0.15161 | 1
4286 | 0.11876 | 0.16986 | 0.93132 | 0 | 0 | 1 | 0.11876 | 0.16986 | 1
4287 | 0.14723 | 0.16405 | 0.93132 | 0 | 0 | 1 | 0.14723 | 0.16405 | 1
4288 | 0.13295 | 0.15151 | 0.93132 | 0 | 0 | 1 | 0.13295 | 0.15151 | 1
4289 | 0.017689 | 0.15214 | 0.93132 | 0 | 0 | 1 | 0.017689 | 0.15214 | 1
4290 | 0 | 0.14896 | 0.93132 | 0 | 1 | 1 | 0 | 0.14896 | 1
4291 | 0 | 0.10017 | 0.93132 | 0 | 1 | 1 | 0 | 0.10017 | 1
4292 | 0 | 0.070602 | 0.93132 | 0 | 1 | 1 | 0 | 0.070602 | 1
4293 | 0 | 0.040826 | 0.93132 | 0 | 1 | 1 | 0 | 0.040826 | 1
4294 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4295 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4296 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4297 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4298 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4299 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4300 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4301 | 0 | 0.0023913 | 0.93132 | 0 | 0 | 1 | 0 | 0.0023913 | 1
4302 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4303 | 0 | 0.014868 | 0.93132 | 0 | 0 | 1 | 0 | 0.014868 | 1
4304 | 0 | 0.013487 | 0.93132 | 0 | 0 | 1 | 0 | 0.013487 | 1
4305 | 0.11341 | 0.026014 | 0.93132 | 0 | 0 | 1 | 0.11341 | 0.026014 | 1
4306 | 0.23185 | 0.060239 | 0.93132 | 0 | 0 | 1 | 0.23185 | 0.060239 | 1
4307 | 0.33811 | 0.09279 | 0.93132 | 0 | 0 | 1 | 0.33811 | 0.09279 | 1
4308 | 0.27143 | 0.1338 | 0.93132 | 0 | 0 | 1 | 0.27143 | 0.1338 | 1
4309 | 0.20638 | 0.14728 | 0.93132 | 0 | 0 | 1 | 0.20638 | 0.14728 | 1
4310 | 0.18506 | 0.15582 | 0.93132 | 0 | 0 | 1 | 0.18506 | 0.15582 | 1
4311 | 0.19615 | 0.14264 | 0.93132 | 0 | 0 | 1 | 0.19615 | 0.14264 | 1
4312 | 0.13481 | 0.1271 | 0.93132 | 0 | 0 | 1 | 0.13481 | 0.1271 | 1
4313 | 0.058228 | 0.10764 | 0.93132 | 0 | 0 | 1 | 0.058228 | 0.10764 | 1
4314 | 0 | 0.10012 | 0.93132 | 0 | 1 | 1 | 0 | 0.10012 | 1
4315 | 0 | 0.065432 | 0.93132 | 0 | 1 | 1 | 0 | 0.065432 | 1
4316 | 0 | 0.024386 | 0.93132 | 0 | 1 | 1 | 0 | 0.024386 | 1
4317 | 0 | 0.002836 | 0.93132 | 0 | 1 | 1 | 0 | 0.002836 | 1
4318 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4319 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4320 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4321 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4322 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4323 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4324 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4325 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4326 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4327 | 0 | 0.007891 | 0.93132 | 0 | 0 | 1 | 0 | 0.007891 | 1
4328 | 0 | 0.012145 | 0.93132 | 0 | 0 | 1 | 0 | 0.012145 | 1
4329 | 0.11142 | 0.01923 | 0.93132 | 0 | 0 | 1 | 0.11142 | 0.01923 | 1
4330 | 0.15917 | 0.050702 | 0.93132 | 0 | 0 | 1 | 0.15917 | 0.050702 | 1
4331 | 0.29728 | 0.08824 | 0.93132 | 0 | 0 | 1 | 0.29728 | 0.08824 | 1
4332 | 0.29685 | 0.10542 | 0.93132 | 0 | 0 | 1 | 0.29685 | 0.10542 | 1
4333 | 0.21044 | 0.12444 | 0.93132 | 0 | 0 | 1 | 0.21044 | 0.12444 | 1
4334 | 0.23282 | 0.12173 | 0.93132 | 0 | 0 | 1 | 0.23282 | 0.12173 | 1
4335 | 0.18756 | 0.10119 | 0.93132 | 0 | 0 | 1 | 0.18756 | 0.10119 | 1
4336 | 0.13833 | 0.095358 | 0.93132 | 0 | 0 | 1 | 0.13833 | 0.095358 | 1
4337 | 0.043511 | 0.062827 | 0.93132 | 0 | 0 | 1 | 0.043511 | 0.062827 | 1
4338 | 0 | 0.05117 | 0.93132 | 0 | 1 | 1 | 0 | 0.05117 | 1
4339 | 0 | 0.043215 | 0.93132 | 0 | 1 | 1 | 0 | 0.043215 | 1
4340 | 0 | 0.0077586 | 0.93132 | 0 | 1 | 1 | 0 | 0.0077586 | 1
4341 | 0 | 0.0015927 | 0.93132 | 0 | 1 | 1 | 0 | 0.0015927 | 1
4342 | 0 | 0.0048556 | 0.93132 | 0 | 0 | 1 | 0 | 0.0048556 | 1
4343 | 0 | 0.0032103 | 0.93132 | 0 | 0 | 1 | 0 | 0.0032103 | 1
4344 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4345 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4346 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4347 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4348 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4349 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4350 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4351 | 0 | 0.0099996 | 0.93132 | 0 | 0 | 1 | 0 | 0.0099996 | 1
4352 | 0 | 0.011283 | 0.93132 | 0 | 0 | 1 | 0 | 0.011283 | 1
4353 | 0.13084 | 0.016927 | 0.93132 | 0 | 0 | 1 | 0.13084 | 0.016927 | 1
4354 | 0.14279 | 0.046506 | 0.93132 | 0 | 0 | 1 | 0.14279 | 0.046506 | 1
4355 | 0.26356 | 0.070925 | 0.93132 | 0 | 0 | 1 | 0.26356 | 0.070925 | 1
4356 | 0.29066 | 0.083506 | 0.93132 | 0 | 0 | 1 | 0.29066 | 0.083506 | 1
4357 | 0.231 | 0.11132 | 0.93132 | 0 | 0 | 1 | 0.231 | 0.11132 | 1
4358 | 0.255 | 0.097945 | 0.93132 | 0 | 0 | 1 | 0.255 | 0.097945 | 1
4359 | 0.20207 | 0.09906 | 0.93132 | 0 | 0 | 1 | 0.20207 | 0.09906 | 1
4360 | 0.12721 | 0.10805 | 0.93132 | 0 | 0 | 1 | 0.12721 | 0.10805 | 1
4361 | 0.047101 | 0.076223 | 0.93132 | 0 | 0 | 1 | 0.047101 | 0.076223 | 1
4362 | 0 | 0.058923 | 0.93132 | 0 | 1 | 1 | 0 | 0.058923 | 1
4363 | 0 | 0.054586 | 0.93132 | 0 | 1 | 1 | 0 | 0.054586 | 1
4364 | 0 | 0.012571 | 0.93132 | 0 | 1 | 1 | 0 | 0.012571 | 1
4365 | 0 | 0.015142 | 0.93132 | 0 | 1 | 1 | 0 | 0.015142 | 1
4366 | 0 | 0.016528 | 0.93132 | 0 | 0 | 1 | 0 | 0.016528 | 1
4367 | 0 | 0.038983 | 0.93132 | 0 | 0 | 1 | 0 | 0.038983 | 1
4368 | 0 | 0.028019 | 0.93132 | 0 | 0 | 1 | 0 | 0.028019 | 1
4369 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4370 | 0 | 0.0061443 | 0.93132 | 0 | 0 | 1 | 0 | 0.0061443 | 1
4371 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4372 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4373 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4374 | 0 | 0.0060446 | 0.93132 | 0 | 0 | 1 | 0 | 0.0060446 | 1
4375 | 0 | 0.05407 | 0.93132 | 0 | 0 | 1 | 0 | 0.05407 | 1
4376 | 0 | 0.048185 | 0.93132 | 0 | 0 | 1 | 0 | 0.048185 | 1
4377 | 0.069735 | 0.059049 | 0.93132 | 0 | 0 | 1 | 0.069735 | 0.059049 | 1
4378 | 0.10741 | 0.086226 | 0.93132 | 0 | 0 | 1 | 0.10741 | 0.086226 | 1
4379 | 0.16367 | 0.10647 | 0.93132 | 0 | 0 | 1 | 0.16367 | 0.10647 | 1
4380 | 0.2602 | 0.1073 | 0.93132 | 0 | 0 | 1 | 0.2602 | 0.1073 | 1
4381 | 0.21637 | 0.14022 | 0.93132 | 0 | 0 | 1 | 0.21637 | 0.14022 | 1
4382 | 0.20982 | 0.12975 | 0.93132 | 0 | 0 | 1 | 0.20982 | 0.12975 | 1
4383 | 0.18257 | 0.13433 | 0.93132 | 0 | 0 | 1 | 0.18257 | 0.13433 | 1
4384 | 0.13263 | 0.14168 | 0.93132 | 0 | 0 | 1 | 0.13263 | 0.14168 | 1
4385 | 0.053714 | 0.11985 | 0.93132 | 0 | 0 | 1 | 0.053714 | 0.11985 | 1
4386 | 0 | 0.10447 | 0.93132 | 0 | 1 | 1 | 0 | 0.10447 | 1
4387 | 0 | 0.10657 | 0.93132 | 0 | 1 | 1 | 0 | 0.10657 | 1
4388 | 0 | 0.062674 | 0.93132 | 0 | 1 | 1 | 0 | 0.062674 | 1
4389 | 0 | 0.067593 | 0.93132 | 0 | 1 | 1 | 0 | 0.067593 | 1
4390 | 0 | 0.063453 | 0.93132 | 0 | 0 | 1 | 0 | 0.063453 | 1
4391 | 0 | 0.077223 | 0.93132 | 0 | 0 | 1 | 0 | 0.077223 | 1
4392 | 0 | 0.054604 | 0.93132 | 0 | 0 | 1 | 0 | 0.054604 | 1
4393 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4394 | 0 | 0.025126 | 0.93132 | 0 | 0 | 1 | 0 | 0.025126 | 1
4395 | 0 | 0.011896 | 0.93132 | 0 | 0 | 1 | 0 | 0.011896 | 1
4396 | 0 | 0.013141 | 0.93132 | 0 | 0 | 1 | 0 | 0.013141 | 1
4397 | 0 | 0.024325 | 0.93132 | 0 | 0 | 1 | 0 | 0.024325 | 1
4398 | 0 | 0.036308 | 0.93132 | 0 | 0 | 1 | 0 | 0.036308 | 1
4399 | 0 | 0.0864 | 0.93132 | 0 | 0 | 1 | 0 | 0.0864 | 1
4400 | 0 | 0.075277 | 0.93132 | 0 | 0 | 1 | 0 | 0.075277 | 1
4401 | 0.044916 | 0.10416 | 0.93132 | 0 | 0 | 1 | 0.044916 | 0.10416 | 1
4402 | 0.12703 | 0.13386 | 0.93132 | 0 | 0 | 1 | 0.12703 | 0.13386 | 1
4403 | 0.17512 | 0.13915 | 0.93132 | 0 | 0 | 1 | 0.17512 | 0.13915 | 1
4404 | 0.23525 | 0.16327 | 0.93132 | 0 | 0 | 1 | 0.23525 | 0.16327 | 1
4405 | 0.25234 | 0.189 | 0.93132 | 0 | 0 | 1 | 0.25234 | 0.189 | 1
4406 | 0.22977 | 0.17478 | 0.93132 | 0 | 0 | 1 | 0.22977 | 0.17478 | 1
4407 | 0.20738 | 0.20241 | 0.93132 | 0 | 0 | 1 | 0.20738 | 0.20241 | 1
4408 | 0.15272 | 0.21233 | 0.93132 | 0 | 0 | 1 | 0.15272 | 0.21233 | 1
4409 | 0.059058 | 0.19686 | 0.93132 | 0 | 0 | 1 | 0.059058 | 0.19686 | 1
4410 | 0 | 0.16127 | 0.93132 | 0 | 1 | 1 | 0 | 0.16127 | 1
4411 | 0 | 0.13799 | 0.93132 | 0 | 1 | 1 | 0 | 0.13799 | 1
4412 | 0 | 0.097933 | 0.93132 | 0 | 1 | 1 | 0 | 0.097933 | 1
4413 | 0 | 0.099399 | 0.93132 | 0 | 1 | 1 | 0 | 0.099399 | 1
4414 | 0 | 0.099841 | 0.93132 | 0 | 0 | 1 | 0 | 0.099841 | 1
4415 | 0 | 0.10451 | 0.93132 | 0 | 0 | 1 | 0 | 0.10451 | 1
4416 | 0 | 0.10642 | 0.93132 | 0 | 0 | 1 | 0 | 0.10642 | 1
4417 | 0 | 0.023249 | 0.93132 | 0 | 0 | 1 | 0 | 0.023249 | 1
4418 | 0 | 0.069001 | 0.93132 | 0 | 0 | 1 | 0 | 0.069001 | 1
4419 | 0 | 0.053244 | 0.93132 | 0 | 0 | 1 | 0 | 0.053244 | 1
4420 | 0 | 0.05012 | 0.93132 | 0 | 0 | 1 | 0 | 0.05012 | 1
4421 | 0 | 0.058092 | 0.93132 | 0 | 0 | 1 | 0 | 0.058092 | 1
4422 | 0 | 0.063543 | 0.93132 | 0 | 0 | 1 | 0 | 0.063543 | 1
4423 | 0 | 0.10567 | 0.93132 | 0 | 0 | 1 | 0 | 0.10567 | 1
4424 | 0 | 0.10259 | 0.93132 | 0 | 0 | 1 | 0 | 0.10259 | 1
4425 | 0.026086 | 0.10443 | 0.93132 | 0 | 0 | 1 | 0.026086 | 0.10443 | 1
4426 | 0.11973 | 0.131 | 0.93132 | 0 | 0 | 1 | 0.11973 | 0.131 | 1
4427 | 0.18359 | 0.15502 | 0.93132 | 0 | 0 | 1 | 0.18359 | 0.15502 | 1
4428 | 0.23555 | 0.18162 | 0.93132 | 0 | 0 | 1 | 0.23555 | 0.18162 | 1
4429 | 0.24922 | 0.1899 | 0.93132 | 0 | 0 | 1 | 0.24922 | 0.1899 | 1
4430 | 0.22963 | 0.19765 | 0.93132 | 0 | 0 | 1 | 0.22963 | 0.19765 | 1
4431 | 0.17512 | 0.21155 | 0.93132 | 0 | 0 | 1 | 0.17512 | 0.21155 | 1
4432 | 0.15254 | 0.21416 | 0.93132 | 0 | 0 | 1 | 0.15254 | 0.21416 | 1
4433 | 0.058696 | 0.18472 | 0.93132 | 0 | 0 | 1 | 0.058696 | 0.18472 | 1
4434 | 0 | 0.18139 | 0.93132 | 0 | 1 | 1 | 0 | 0.18139 | 1
4435 | 0 | 0.14022 | 0.93132 | 0 | 1 | 1 | 0 | 0.14022 | 1
4436 | 0 | 0.11354 | 0.93132 | 0 | 1 | 1 | 0 | 0.11354 | 1
4437 | 0 | 0.10416 | 0.93132 | 0 | 1 | 1 | 0 | 0.10416 | 1
4438 | 0 | 0.10067 | 0.93132 | 0 | 0 | 1 | 0 | 0.10067 | 1
4439 | 0 | 0.08441 | 0.93132 | 0 | 0 | 1 | 0 | 0.08441 | 1
4440 | 0 | 0.06941 | 0.93132 | 0 | 0 | 1 | 0 | 0.06941 | 1
4441 | 0 | 0.083083 | 0.93132 | 0 | 0 | 1 | 0 | 0.083083 | 1
4442 | 0 | 0.034613 | 0.93132 | 0 | 0 | 1 | 0 | 0.034613 | 1
4443 | 0 | 0.034323 | 0.93132 | 0 | 0 | 1 | 0 | 0.034323 | 1
4444 | 0 | 0.032757 | 0.93132 | 0 | 0 | 1 | 0 | 0.032757 | 1
4445 | 0 | 0.030765 | 0.93132 | 0 | 0 | 1 | 0 | 0.030765 | 1
4446 | 0 | 0.01979 | 0.93132 | 0 | 0 | 1 | 0 | 0.01979 | 1
4447 | 0 | 0.055764 | 0.93132 | 0 | 0 | 1 | 0 | 0.055764 | 1
4448 | 0 | 0.071526 | 0.93132 | 0 | 0 | 1 | 0 | 0.071526 | 1
4449 | 0.038409 | 0.068319 | 0.93132 | 0 | 0 | 1 | 0.038409 | 0.068319 | 1
4450 | 0.15515 | 0.10092 | 0.93132 | 0 | 0 | 1 | 0.15515 | 0.10092 | 1
4451 | 0.25901 | 0.12337 | 0.93132 | 0 | 0 | 1 | 0.25901 | 0.12337 | 1
4452 | 0.24635 | 0.16395 | 0.93132 | 0 | 0 | 1 | 0.24635 | 0.16395 | 1
4453 | 0.29544 | 0.17568 | 0.93132 | 0 | 0 | 1 | 0.29544 | 0.17568 | 1
4454 | 0.28015 | 0.1794 | 0.93132 | 0 | 0 | 1 | 0.28015 | 0.1794 | 1
4455 | 0.23957 | 0.17513 | 0.93132 | 0 | 0 | 1 | 0.23957 | 0.17513 | 1
4456 | 0.17359 | 0.17988 | 0.93132 | 0 | 0 | 1 | 0.17359 | 0.17988 | 1
4457 | 0.037887 | 0.15348 | 0.93132 | 0 | 0 | 1 | 0.037887 | 0.15348 | 1
4458 | 0 | 0.14043 | 0.93132 | 0 | 1 | 1 | 0 | 0.14043 | 1
4459 | 0 | 0.10739 | 0.93132 | 0 | 1 | 1 | 0 | 0.10739 | 1
4460 | 0 | 0.095558 | 0.93132 | 0 | 1 | 1 | 0 | 0.095558 | 1
4461 | 0 | 0.094212 | 0.93132 | 0 | 1 | 1 | 0 | 0.094212 | 1
4462 | 0 | 0.085991 | 0.93132 | 0 | 0 | 1 | 0 | 0.085991 | 1
4463 | 0 | 0.082769 | 0.93132 | 0 | 0 | 1 | 0 | 0.082769 | 1
4464 | 0 | 0.077737 | 0.93132 | 0 | 0 | 1 | 0 | 0.077737 | 1
4465 | 0 | 0.048229 | 0.93132 | 0 | 0 | 1 | 0 | 0.048229 | 1
4466 | 0 | 0.055375 | 0.93132 | 0 | 0 | 1 | 0 | 0.055375 | 1
4467 | 0 | 0.060519 | 0.93132 | 0 | 0 | 1 | 0 | 0.060519 | 1
4468 | 0 | 0.056053 | 0.93132 | 0 | 0 | 1 | 0 | 0.056053 | 1
4469 | 0 | 0.053013 | 0.93132 | 0 | 0 | 1 | 0 | 0.053013 | 1
4470 | 0 | 0.056143 | 0.93132 | 0 | 0 | 1 | 0 | 0.056143 | 1
4471 | 0 | 0.057857 | 0.93132 | 0 | 0 | 1 | 0 | 0.057857 | 1
4472 | 0 | 0.085083 | 0.93132 | 0 | 0 | 1 | 0 | 0.085083 | 1
4473 | 0.057023 | 0.064652 | 0.93132 | 0 | 0 | 1 | 0.057023 | 0.064652 | 1
4474 | 0.13739 | 0.080891 | 0.93132 | 0 | 0 | 1 | 0.13739 | 0.080891 | 1
4475 | 0.29362 | 0.10527 | 0.93132 | 0 | 0 | 1 | 0.29362 | 0.10527 | 1
4476 | 0.31176 | 0.13657 | 0.93132 | 0 | 0 | 1 | 0.31176 | 0.13657 | 1
4477 | 0.33907 | 0.15969 | 0.93132 | 0 | 0 | 1 | 0.33907 | 0.15969 | 1
4478 | 0.2994 | 0.17449 | 0.93132 | 0 | 0 | 1 | 0.2994 | 0.17449 | 1
4479 | 0.29493 | 0.16659 | 0.93132 | 0 | 0 | 1 | 0.29493 | 0.16659 | 1
4480 | 0.18997 | 0.14924 | 0.93132 | 0 | 0 | 1 | 0.18997 | 0.14924 | 1
4481 | 0.086344 | 0.1278 | 0.93132 | 0 | 0 | 1 | 0.086344 | 0.1278 | 1
4482 | 0 | 0.14203 | 0.93132 | 0 | 1 | 1 | 0 | 0.14203 | 1
4483 | 0 | 0.1265 | 0.93132 | 0 | 1 | 1 | 0 | 0.1265 | 1
4484 | 0 | 0.11346 | 0.93132 | 0 | 1 | 1 | 0 | 0.11346 | 1
4485 | 0 | 0.11273 | 0.93132 | 0 | 1 | 1 | 0 | 0.11273 | 1
4486 | 0 | 0.092707 | 0.93132 | 0 | 0 | 1 | 0 | 0.092707 | 1
4487 | 0 | 0.088747 | 0.93132 | 0 | 0 | 1 | 0 | 0.088747 | 1
4488 | 0 | 0.068647 | 0.93132 | 0 | 0 | 1 | 0 | 0.068647 | 1
4489 | 0 | 0.048479 | 0.93132 | 0 | 0 | 1 | 0 | 0.048479 | 1
4490 | 0 | 0.036456 | 0.93132 | 0 | 0 | 1 | 0 | 0.036456 | 1
4491 | 0 | 0.041808 | 0.93132 | 0 | 0 | 1 | 0 | 0.041808 | 1
4492 | 0 | 0.04532 | 0.93132 | 0 | 0 | 1 | 0 | 0.04532 | 1
4493 | 0 | 0.054066 | 0.93132 | 0 | 0 | 1 | 0 | 0.054066 | 1
4494 | 0 | 0.054944 | 0.93132 | 0 | 0 | 1 | 0 | 0.054944 | 1
4495 | 0 | 0.051758 | 0.93132 | 0 | 0 | 1 | 0 | 0.051758 | 1
4496 | 0 | 0.081533 | 0.93132 | 0 | 0 | 1 | 0 | 0.081533 | 1
4497 | 0.040556 | 0.094164 | 0.93132 | 0 | 0 | 1 | 0.040556 | 0.094164 | 1
4498 | 0.10292 | 0.10996 | 0.93132 | 0 | 0 | 1 | 0.10292 | 0.10996 | 1
4499 | 0.31965 | 0.12596 | 0.93132 | 0 | 0 | 1 | 0.31965 | 0.12596 | 1
4500 | 0.31218 | 0.15595 | 0.93132 | 0 | 0 | 1 | 0.31218 | 0.15595 | 1
4501 | 0.35269 | 0.19081 | 0.93132 | 0 | 0 | 1 | 0.35269 | 0.19081 | 1
4502 | 0.31629 | 0.20111 | 0.93132 | 0 | 0 | 1 | 0.31629 | 0.20111 | 1
4503 | 0.32113 | 0.18867 | 0.93132 | 0 | 0 | 1 | 0.32113 | 0.18867 | 1
4504 | 0.16891 | 0.16912 | 0.93132 | 0 | 0 | 1 | 0.16891 | 0.16912 | 1
4505 | 0.066689 | 0.16151 | 0.93132 | 0 | 0 | 1 | 0.066689 | 0.16151 | 1
4506 | 0 | 0.14843 | 0.93132 | 0 | 1 | 1 | 0 | 0.14843 | 1
4507 | 0 | 0.14565 | 0.93132 | 0 | 1 | 1 | 0 | 0.14565 | 1
4508 | 0 | 0.13898 | 0.93132 | 0 | 1 | 1 | 0 | 0.13898 | 1
4509 | 0 | 0.14391 | 0.93132 | 0 | 1 | 1 | 0 | 0.14391 | 1
4510 | 0 | 0.1402 | 0.93132 | 0 | 0 | 1 | 0 | 0.1402 | 1
4511 | 0 | 0.15124 | 0.93132 | 0 | 0 | 1 | 0 | 0.15124 | 1
4512 | 0 | 0.13942 | 0.93132 | 0 | 0 | 1 | 0 | 0.13942 | 1
4513 | 0 | 0.030284 | 0.93132 | 0 | 0 | 1 | 0 | 0.030284 | 1
4514 | 0 | 0.092623 | 0.93132 | 0 | 0 | 1 | 0 | 0.092623 | 1
4515 | 0 | 0.088088 | 0.93132 | 0 | 0 | 1 | 0 | 0.088088 | 1
4516 | 0 | 0.092045 | 0.93132 | 0 | 0 | 1 | 0 | 0.092045 | 1
4517 | 0 | 0.090764 | 0.93132 | 0 | 0 | 1 | 0 | 0.090764 | 1
4518 | 0 | 0.090059 | 0.93132 | 0 | 0 | 1 | 0 | 0.090059 | 1
4519 | 0 | 0.095187 | 0.93132 | 0 | 0 | 1 | 0 | 0.095187 | 1
4520 | 0 | 0.10017 | 0.93132 | 0 | 0 | 1 | 0 | 0.10017 | 1
4521 | 0.097807 | 0.12478 | 0.93132 | 0 | 0 | 1 | 0.097807 | 0.12478 | 1
4522 | 0.16889 | 0.14487 | 0.93132 | 0 | 0 | 1 | 0.16889 | 0.14487 | 1
4523 | 0.28458 | 0.16681 | 0.93132 | 0 | 0 | 1 | 0.28458 | 0.16681 | 1
4524 | 0.27927 | 0.19421 | 0.93132 | 0 | 0 | 1 | 0.27927 | 0.19421 | 1
4525 | 0.28274 | 0.22719 | 0.93132 | 0 | 0 | 1 | 0.28274 | 0.22719 | 1
4526 | 0.29786 | 0.2485 | 0.93132 | 0 | 0 | 1 | 0.29786 | 0.2485 | 1
4527 | 0.31596 | 0.24626 | 0.93132 | 0 | 0 | 1 | 0.31596 | 0.24626 | 1
4528 | 0.16764 | 0.22124 | 0.93132 | 0 | 0 | 1 | 0.16764 | 0.22124 | 1
4529 | 0.10059 | 0.21286 | 0.93132 | 0 | 0 | 1 | 0.10059 | 0.21286 | 1
4530 | 0 | 0.21511 | 0.93132 | 0 | 1 | 1 | 0 | 0.21511 | 1
4531 | 0 | 0.20131 | 0.93132 | 0 | 1 | 1 | 0 | 0.20131 | 1
4532 | 0 | 0.18971 | 0.93132 | 0 | 1 | 1 | 0 | 0.18971 | 1
4533 | 0 | 0.1832 | 0.93132 | 0 | 1 | 1 | 0 | 0.1832 | 1
4534 | 0 | 0.17406 | 0.93132 | 0 | 0 | 1 | 0 | 0.17406 | 1
4535 | 0 | 0.17009 | 0.93132 | 0 | 0 | 1 | 0 | 0.17009 | 1
4536 | 0 | 0.1588 | 0.93132 | 0 | 0 | 1 | 0 | 0.1588 | 1
4537 | 0 | 0.090375 | 0.93132 | 0 | 0 | 1 | 0 | 0.090375 | 1
4538 | 0 | 0.07441 | 0.93132 | 0 | 0 | 1 | 0 | 0.07441 | 1
4539 | 0 | 0.080307 | 0.93132 | 0 | 0 | 1 | 0 | 0.080307 | 1
4540 | 0 | 0.069932 | 0.93132 | 0 | 0 | 1 | 0 | 0.069932 | 1
4541 | 0 | 0.07463 | 0.93132 | 0 | 0 | 1 | 0 | 0.07463 | 1
4542 | 0 | 0.086877 | 0.93132 | 0 | 0 | 1 | 0 | 0.086877 | 1
4543 | 0 | 0.089295 | 0.93132 | 0 | 0 | 1 | 0 | 0.089295 | 1
4544 | 0 | 0.1026 | 0.93132 | 0 | 0 | 1 | 0 | 0.1026 | 1
4545 | 0.10276 | 0.12647 | 0.93132 | 0 | 0 | 1 | 0.10276 | 0.12647 | 1
4546 | 0.20288 | 0.16431 | 0.93132 | 0 | 0 | 1 | 0.20288 | 0.16431 | 1
4547 | 0.27956 | 0.18653 | 0.93132 | 0 | 0 | 1 | 0.27956 | 0.18653 | 1
4548 | 0.27685 | 0.21807 | 0.93132 | 0 | 0 | 1 | 0.27685 | 0.21807 | 1
4549 | 0.27249 | 0.24932 | 0.93132 | 0 | 0 | 1 | 0.27249 | 0.24932 | 1
4550 | 0.37077 | 0.26139 | 0.93132 | 0 | 0 | 1 | 0.37077 | 0.26139 | 1
4551 | 0.38512 | 0.24172 | 0.93132 | 0 | 0 | 1 | 0.38512 | 0.24172 | 1
4552 | 0.22166 | 0.23259 | 0.93132 | 0 | 0 | 1 | 0.22166 | 0.23259 | 1
4553 | 0.088532 | 0.21154 | 0.93132 | 0 | 0 | 1 | 0.088532 | 0.21154 | 1
4554 | 0 | 0.2008 | 0.93132 | 0 | 1 | 1 | 0 | 0.2008 | 1
4555 | 0 | 0.19341 | 0.93132 | 0 | 1 | 1 | 0 | 0.19341 | 1
4556 | 0 | 0.1765 | 0.93132 | 0 | 1 | 1 | 0 | 0.1765 | 1
4557 | 0 | 0.15948 | 0.93132 | 0 | 1 | 1 | 0 | 0.15948 | 1
4558 | 0 | 0.15737 | 0.93132 | 0 | 0 | 1 | 0 | 0.15737 | 1
4559 | 0 | 0.15235 | 0.93132 | 0 | 0 | 1 | 0 | 0.15235 | 1
4560 | 0 | 0.13888 | 0.93132 | 0 | 0 | 1 | 0 | 0.13888 | 1
4561 | 0 | 0.098448 | 0.93132 | 0 | 0 | 1 | 0 | 0.098448 | 1
4562 | 0 | 0.04914 | 0.93132 | 0 | 0 | 1 | 0 | 0.04914 | 1
4563 | 0 | 0.059779 | 0.93132 | 0 | 0 | 1 | 0 | 0.059779 | 1
4564 | 0 | 0.053367 | 0.93132 | 0 | 0 | 1 | 0 | 0.053367 | 1
4565 | 0 | 0.045955 | 0.93132 | 0 | 0 | 1 | 0 | 0.045955 | 1
4566 | 0 | 0.044452 | 0.93132 | 0 | 0 | 1 | 0 | 0.044452 | 1
4567 | 0 | 0.038361 | 0.93132 | 0 | 0 | 1 | 0 | 0.038361 | 1
4568 | 0 | 0.062426 | 0.93132 | 0 | 0 | 1 | 0 | 0.062426 | 1
4569 | 0.085009 | 0.080747 | 0.93132 | 0 | 0 | 1 | 0.085009 | 0.080747 | 1
4570 | 0.23543 | 0.1148 | 0.93132 | 0 | 0 | 1 | 0.23543 | 0.1148 | 1
4571 | 0.2222 | 0.14048 | 0.93132 | 0 | 0 | 1 | 0.2222 | 0.14048 | 1
4572 | 0.25585 | 0.17464 | 0.93132 | 0 | 0 | 1 | 0.25585 | 0.17464 | 1
4573 | 0.24397 | 0.19411 | 0.93132 | 0 | 0 | 1 | 0.24397 | 0.19411 | 1
4574 | 0.33581 | 0.20805 | 0.93132 | 0 | 0 | 1 | 0.33581 | 0.20805 | 1
4575 | 0.33322 | 0.19161 | 0.93132 | 0 | 0 | 1 | 0.33322 | 0.19161 | 1
4576 | 0.23233 | 0.18788 | 0.93132 | 0 | 0 | 1 | 0.23233 | 0.18788 | 1
4577 | 0.14388 | 0.12055 | 0.93132 | 0 | 0 | 1 | 0.14388 | 0.12055 | 1
4578 | 0 | 0.15416 | 0.93132 | 0 | 1 | 1 | 0 | 0.15416 | 1
4579 | 0 | 0.15567 | 0.93132 | 0 | 1 | 1 | 0 | 0.15567 | 1
4580 | 0 | 0.12769 | 0.93132 | 0 | 1 | 1 | 0 | 0.12769 | 1
4581 | 0 | 0.11203 | 0.93132 | 0 | 1 | 1 | 0 | 0.11203 | 1
4582 | 0 | 0.095443 | 0.93132 | 0 | 0 | 1 | 0 | 0.095443 | 1
4583 | 0 | 0.088328 | 0.93132 | 0 | 0 | 1 | 0 | 0.088328 | 1
4584 | 0 | 0.077302 | 0.93132 | 0 | 0 | 1 | 0 | 0.077302 | 1
4585 | 0 | 0.071113 | 0.93132 | 0 | 0 | 1 | 0 | 0.071113 | 1
4586 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4587 | 0 | 0.0060272 | 0.93132 | 0 | 0 | 1 | 0 | 0.0060272 | 1
4588 | 0 | 0.00088237 | 0.93132 | 0 | 0 | 1 | 0 | 0.00088237 | 1
4589 | 0 | 0.007461 | 0.93132 | 0 | 0 | 1 | 0 | 0.007461 | 1
4590 | 0 | 0.011496 | 0.93132 | 0 | 0 | 1 | 0 | 0.011496 | 1
4591 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4592 | 0 | 0.012224 | 0.93132 | 0 | 0 | 1 | 0 | 0.012224 | 1
4593 | 0.078241 | 0.034023 | 0.93132 | 0 | 0 | 1 | 0.078241 | 0.034023 | 1
4594 | 0.22017 | 0.057738 | 0.93132 | 0 | 0 | 1 | 0.22017 | 0.057738 | 1
4595 | 0.23416 | 0.073885 | 0.93132 | 0 | 0 | 1 | 0.23416 | 0.073885 | 1
4596 | 0.27266 | 0.065769 | 0.93132 | 0 | 0 | 1 | 0.27266 | 0.065769 | 1
4597 | 0.22159 | 0.07909 | 0.93132 | 0 | 0 | 1 | 0.22159 | 0.07909 | 1
4598 | 0.26617 | 0.10508 | 0.93132 | 0 | 0 | 1 | 0.26617 | 0.10508 | 1
4599 | 0.31958 | 0.10767 | 0.93132 | 0 | 0 | 1 | 0.31958 | 0.10767 | 1
4600 | 0.21986 | 0.098038 | 0.93132 | 0 | 0 | 1 | 0.21986 | 0.098038 | 1
4601 | 0.12197 | 0.056988 | 0.93132 | 0 | 0 | 1 | 0.12197 | 0.056988 | 1
4602 | 0 | 0.061008 | 0.93132 | 0 | 1 | 1 | 0 | 0.061008 | 1
4603 | 0 | 0.064093 | 0.93132 | 0 | 1 | 1 | 0 | 0.064093 | 1
4604 | 0 | 0.060507 | 0.93132 | 0 | 1 | 1 | 0 | 0.060507 | 1
4605 | 0 | 0.059187 | 0.93132 | 0 | 1 | 1 | 0 | 0.059187 | 1
4606 | 0 | 0.063492 | 0.93132 | 0 | 0 | 1 | 0 | 0.063492 | 1
4607 | 0 | 0.054984 | 0.93132 | 0 | 0 | 1 | 0 | 0.054984 | 1
4608 | 0 | 0.054054 | 0.93132 | 0 | 0 | 1 | 0 | 0.054054 | 1
4609 | 0 | 0.023907 | 0.93132 | 0 | 0 | 1 | 0 | 0.023907 | 1
4610 | 0 | 0.00028863 | 0.93132 | 0 | 0 | 1 | 0 | 0.00028863 | 1
4611 | 0 | 0.013669 | 0.93132 | 0 | 0 | 1 | 0 | 0.013669 | 1
4612 | 0 | 0.00079168 | 0.93132 | 0 | 0 | 1 | 0 | 0.00079168 | 1
4613 | 0 | 0.0042414 | 0.93132 | 0 | 0 | 1 | 0 | 0.0042414 | 1
4614 | 0 | 0.0024554 | 0.93132 | 0 | 0 | 1 | 0 | 0.0024554 | 1
4615 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4616 | 0 | 0.0072383 | 0.93132 | 0 | 0 | 1 | 0 | 0.0072383 | 1
4617 | 0.070453 | 0.024225 | 0.93132 | 0 | 0 | 1 | 0.070453 | 0.024225 | 1
4618 | 0.15146 | 0.036503 | 0.93132 | 0 | 0 | 1 | 0.15146 | 0.036503 | 1
4619 | 0.19027 | 0.063256 | 0.93132 | 0 | 0 | 1 | 0.19027 | 0.063256 | 1
4620 | 0.23794 | 0.051476 | 0.93132 | 0 | 0 | 1 | 0.23794 | 0.051476 | 1
4621 | 0.2383 | 0.059941 | 0.93132 | 0 | 0 | 1 | 0.2383 | 0.059941 | 1
4622 | 0.24678 | 0.094623 | 0.93132 | 0 | 0 | 1 | 0.24678 | 0.094623 | 1
4623 | 0.28095 | 0.11368 | 0.93132 | 0 | 0 | 1 | 0.28095 | 0.11368 | 1
4624 | 0.22138 | 0.11744 | 0.93132 | 0 | 0 | 1 | 0.22138 | 0.11744 | 1
4625 | 0.12143 | 0.082145 | 0.93132 | 0 | 0 | 1 | 0.12143 | 0.082145 | 1
4626 | 0 | 0.080829 | 0.93132 | 0 | 1 | 1 | 0 | 0.080829 | 1
4627 | 0 | 0.065104 | 0.93132 | 0 | 1 | 1 | 0 | 0.065104 | 1
4628 | 0 | 0.063285 | 0.93132 | 0 | 1 | 1 | 0 | 0.063285 | 1
4629 | 0 | 0.061625 | 0.93132 | 0 | 1 | 1 | 0 | 0.061625 | 1
4630 | 0 | 0.070056 | 0.93132 | 0 | 0 | 1 | 0 | 0.070056 | 1
4631 | 0 | 0.069122 | 0.93132 | 0 | 0 | 1 | 0 | 0.069122 | 1
4632 | 0 | 0.064958 | 0.93132 | 0 | 0 | 1 | 0 | 0.064958 | 1
4633 | 0 | 0.030188 | 0.93132 | 0 | 0 | 1 | 0 | 0.030188 | 1
4634 | 0 | 0.043704 | 0.93132 | 0 | 0 | 1 | 0 | 0.043704 | 1
4635 | 0 | 0.052845 | 0.93132 | 0 | 0 | 1 | 0 | 0.052845 | 1
4636 | 0 | 0.023519 | 0.93132 | 0 | 0 | 1 | 0 | 0.023519 | 1
4637 | 0 | 0.032991 | 0.93132 | 0 | 0 | 1 | 0 | 0.032991 | 1
4638 | 0 | 0.030646 | 0.93132 | 0 | 0 | 1 | 0 | 0.030646 | 1
4639 | 0 | 0.028174 | 0.93132 | 0 | 0 | 1 | 0 | 0.028174 | 1
4640 | 0 | 0.015837 | 0.93132 | 0 | 0 | 1 | 0 | 0.015837 | 1
4641 | 0.10034 | 0.04032 | 0.93132 | 0 | 0 | 1 | 0.10034 | 0.04032 | 1
4642 | 0.12175 | 0.052275 | 0.93132 | 0 | 0 | 1 | 0.12175 | 0.052275 | 1
4643 | 0.19505 | 0.075548 | 0.93132 | 0 | 0 | 1 | 0.19505 | 0.075548 | 1
4644 | 0.22305 | 0.056009 | 0.93132 | 0 | 0 | 1 | 0.22305 | 0.056009 | 1
4645 | 0.21307 | 0.078738 | 0.93132 | 0 | 0 | 1 | 0.21307 | 0.078738 | 1
4646 | 0.2175 | 0.10666 | 0.93132 | 0 | 0 | 1 | 0.2175 | 0.10666 | 1
4647 | 0.30007 | 0.14029 | 0.93132 | 0 | 0 | 1 | 0.30007 | 0.14029 | 1
4648 | 0.19127 | 0.13717 | 0.93132 | 0 | 0 | 1 | 0.19127 | 0.13717 | 1
4649 | 0.092831 | 0.1232 | 0.93132 | 0 | 0 | 1 | 0.092831 | 0.1232 | 1
4650 | 0 | 0.10195 | 0.93132 | 0 | 1 | 1 | 0 | 0.10195 | 1
4651 | 0 | 0.081283 | 0.93132 | 0 | 1 | 1 | 0 | 0.081283 | 1
4652 | 0 | 0.088534 | 0.93132 | 0 | 1 | 1 | 0 | 0.088534 | 1
4653 | 0 | 0.10023 | 0.93132 | 0 | 1 | 1 | 0 | 0.10023 | 1
4654 | 0 | 0.11935 | 0.93132 | 0 | 0 | 1 | 0 | 0.11935 | 1
4655 | 0 | 0.10323 | 0.93132 | 0 | 0 | 1 | 0 | 0.10323 | 1
4656 | 0 | 0.090045 | 0.93132 | 0 | 0 | 1 | 0 | 0.090045 | 1
4657 | 0 | 0.067975 | 0.93132 | 0 | 0 | 1 | 0 | 0.067975 | 1
4658 | 0 | 0.10045 | 0.93132 | 0 | 0 | 1 | 0 | 0.10045 | 1
4659 | 0 | 0.086304 | 0.93132 | 0 | 0 | 1 | 0 | 0.086304 | 1
4660 | 0 | 0.061439 | 0.93132 | 0 | 0 | 1 | 0 | 0.061439 | 1
4661 | 0 | 0.082403 | 0.93132 | 0 | 0 | 1 | 0 | 0.082403 | 1
4662 | 0 | 0.052175 | 0.93132 | 0 | 0 | 1 | 0 | 0.052175 | 1
4663 | 0 | 0.058685 | 0.93132 | 0 | 0 | 1 | 0 | 0.058685 | 1
4664 | 0 | 0.052537 | 0.93132 | 0 | 0 | 1 | 0 | 0.052537 | 1
4665 | 0.11697 | 0.078365 | 0.93132 | 0 | 0 | 1 | 0.11697 | 0.078365 | 1
4666 | 0.13861 | 0.099125 | 0.93132 | 0 | 0 | 1 | 0.13861 | 0.099125 | 1
4667 | 0.22158 | 0.13887 | 0.93132 | 0 | 0 | 1 | 0.22158 | 0.13887 | 1
4668 | 0.22655 | 0.14934 | 0.93132 | 0 | 0 | 1 | 0.22655 | 0.14934 | 1
4669 | 0.256 | 0.16921 | 0.93132 | 0 | 0 | 1 | 0.256 | 0.16921 | 1
4670 | 0.23297 | 0.17136 | 0.93132 | 0 | 0 | 1 | 0.23297 | 0.17136 | 1
4671 | 0.22197 | 0.20668 | 0.93132 | 0 | 0 | 1 | 0.22197 | 0.20668 | 1
4672 | 0.1935 | 0.19717 | 0.93132 | 0 | 0 | 1 | 0.1935 | 0.19717 | 1
4673 | 0.10313 | 0.17383 | 0.93132 | 0 | 0 | 1 | 0.10313 | 0.17383 | 1
4674 | 0 | 0.18138 | 0.93132 | 0 | 1 | 1 | 0 | 0.18138 | 1
4675 | 0 | 0.16539 | 0.93132 | 0 | 1 | 1 | 0 | 0.16539 | 1
4676 | 0 | 0.14748 | 0.93132 | 0 | 1 | 1 | 0 | 0.14748 | 1
4677 | 0 | 0.14834 | 0.93132 | 0 | 1 | 1 | 0 | 0.14834 | 1
4678 | 0 | 0.12923 | 0.93132 | 0 | 0 | 1 | 0 | 0.12923 | 1
4679 | 0 | 0.11986 | 0.93132 | 0 | 0 | 1 | 0 | 0.11986 | 1
4680 | 0 | 0.10904 | 0.93132 | 0 | 0 | 1 | 0 | 0.10904 | 1
4681 | 0 | 0.096744 | 0.93132 | 0 | 0 | 1 | 0 | 0.096744 | 1
4682 | 0 | 0.10588 | 0.93132 | 0 | 0 | 1 | 0 | 0.10588 | 1
4683 | 0 | 0.096509 | 0.93132 | 0 | 0 | 1 | 0 | 0.096509 | 1
4684 | 0 | 0.076553 | 0.93132 | 0 | 0 | 1 | 0 | 0.076553 | 1
4685 | 0 | 0.11796 | 0.93132 | 0 | 0 | 1 | 0 | 0.11796 | 1
4686 | 0 | 0.085343 | 0.93132 | 0 | 0 | 1 | 0 | 0.085343 | 1
4687 | 0 | 0.095856 | 0.93132 | 0 | 0 | 1 | 0 | 0.095856 | 1
4688 | 0 | 0.082011 | 0.93132 | 0 | 0 | 1 | 0 | 0.082011 | 1
4689 | 0.11188 | 0.10995 | 0.93132 | 0 | 0 | 1 | 0.11188 | 0.10995 | 1
4690 | 0.20444 | 0.11781 | 0.93132 | 0 | 0 | 1 | 0.20444 | 0.11781 | 1
4691 | 0.24026 | 0.15866 | 0.93132 | 0 | 0 | 1 | 0.24026 | 0.15866 | 1
4692 | 0.26748 | 0.16457 | 0.93132 | 0 | 0 | 1 | 0.26748 | 0.16457 | 1
4693 | 0.27792 | 0.18934 | 0.93132 | 0 | 0 | 1 | 0.27792 | 0.18934 | 1
4694 | 0.23344 | 0.18641 | 0.93132 | 0 | 0 | 1 | 0.23344 | 0.18641 | 1
4695 | 0.22409 | 0.19995 | 0.93132 | 0 | 0 | 1 | 0.22409 | 0.19995 | 1
4696 | 0.15911 | 0.20179 | 0.93132 | 0 | 0 | 1 | 0.15911 | 0.20179 | 1
4697 | 0.07664 | 0.17069 | 0.93132 | 0 | 0 | 1 | 0.07664 | 0.17069 | 1
4698 | 0 | 0.18104 | 0.93132 | 0 | 1 | 1 | 0 | 0.18104 | 1
4699 | 0 | 0.16341 | 0.93132 | 0 | 1 | 1 | 0 | 0.16341 | 1
4700 | 0 | 0.15906 | 0.93132 | 0 | 1 | 1 | 0 | 0.15906 | 1
4701 | 0 | 0.14827 | 0.93132 | 0 | 1 | 1 | 0 | 0.14827 | 1
4702 | 0 | 0.12436 | 0.93132 | 0 | 0 | 1 | 0 | 0.12436 | 1
4703 | 0 | 0.10734 | 0.93132 | 0 | 0 | 1 | 0 | 0.10734 | 1
4704 | 0 | 0.10335 | 0.93132 | 0 | 0 | 1 | 0 | 0.10335 | 1
4705 | 0 | 0.1164 | 0.93132 | 0 | 0 | 1 | 0 | 0.1164 | 1
4706 | 0 | 0.097711 | 0.93132 | 0 | 0 | 1 | 0 | 0.097711 | 1
4707 | 0 | 0.075463 | 0.93132 | 0 | 0 | 1 | 0 | 0.075463 | 1
4708 | 0 | 0.075079 | 0.93132 | 0 | 0 | 1 | 0 | 0.075079 | 1
4709 | 0 | 0.094121 | 0.93132 | 0 | 0 | 1 | 0 | 0.094121 | 1
4710 | 0 | 0.075059 | 0.93132 | 0 | 0 | 1 | 0 | 0.075059 | 1
4711 | 0 | 0.10695 | 0.93132 | 0 | 0 | 1 | 0 | 0.10695 | 1
4712 | 0 | 0.11363 | 0.93132 | 0 | 0 | 1 | 0 | 0.11363 | 1
4713 | 0.083412 | 0.14436 | 0.93132 | 0 | 0 | 1 | 0.083412 | 0.14436 | 1
4714 | 0.21103 | 0.17201 | 0.93132 | 0 | 0 | 1 | 0.21103 | 0.17201 | 1
4715 | 0.24606 | 0.21082 | 0.93132 | 0 | 0 | 1 | 0.24606 | 0.21082 | 1
4716 | 0.32441 | 0.22427 | 0.93132 | 0 | 0 | 1 | 0.32441 | 0.22427 | 1
4717 | 0.3682 | 0.22542 | 0.93132 | 0 | 0 | 1 | 0.3682 | 0.22542 | 1
4718 | 0.29702 | 0.21885 | 0.93132 | 0 | 0 | 1 | 0.29702 | 0.21885 | 1
4719 | 0.22148 | 0.21669 | 0.93132 | 0 | 0 | 1 | 0.22148 | 0.21669 | 1
4720 | 0.19933 | 0.22075 | 0.93132 | 0 | 0 | 1 | 0.19933 | 0.22075 | 1
4721 | 0.066184 | 0.20367 | 0.93132 | 0 | 0 | 1 | 0.066184 | 0.20367 | 1
4722 | 0 | 0.20635 | 0.93132 | 0 | 1 | 1 | 0 | 0.20635 | 1
4723 | 0 | 0.18491 | 0.93132 | 0 | 1 | 1 | 0 | 0.18491 | 1
4724 | 0 | 0.16808 | 0.93132 | 0 | 1 | 1 | 0 | 0.16808 | 1
4725 | 0 | 0.13147 | 0.93132 | 0 | 1 | 1 | 0 | 0.13147 | 1
4726 | 0 | 0.11577 | 0.93132 | 0 | 0 | 1 | 0 | 0.11577 | 1
4727 | 0 | 0.12986 | 0.93132 | 0 | 0 | 1 | 0 | 0.12986 | 1
4728 | 0 | 0.12277 | 0.93132 | 0 | 0 | 1 | 0 | 0.12277 | 1
4729 | 0 | 0.10562 | 0.93132 | 0 | 0 | 1 | 0 | 0.10562 | 1
4730 | 0 | 0.095922 | 0.93132 | 0 | 0 | 1 | 0 | 0.095922 | 1
4731 | 0 | 0.099263 | 0.93132 | 0 | 0 | 1 | 0 | 0.099263 | 1
4732 | 0 | 0.093856 | 0.93132 | 0 | 0 | 1 | 0 | 0.093856 | 1
4733 | 0 | 0.085534 | 0.93132 | 0 | 0 | 1 | 0 | 0.085534 | 1
4734 | 0 | 0.0849 | 0.93132 | 0 | 0 | 1 | 0 | 0.0849 | 1
4735 | 0 | 0.10387 | 0.93132 | 0 | 0 | 1 | 0 | 0.10387 | 1
4736 | 0 | 0.089207 | 0.93132 | 0 | 0 | 1 | 0 | 0.089207 | 1
4737 | 0.04191 | 0.13014 | 0.93132 | 0 | 0 | 1 | 0.04191 | 0.13014 | 1
4738 | 0.18017 | 0.16172 | 0.93132 | 0 | 0 | 1 | 0.18017 | 0.16172 | 1
4739 | 0.18123 | 0.16748 | 0.93132 | 0 | 0 | 1 | 0.18123 | 0.16748 | 1
4740 | 0.26538 | 0.15714 | 0.93132 | 0 | 0 | 1 | 0.26538 | 0.15714 | 1
4741 | 0.35186 | 0.16929 | 0.93132 | 0 | 0 | 1 | 0.35186 | 0.16929 | 1
4742 | 0.33659 | 0.17248 | 0.93132 | 0 | 0 | 1 | 0.33659 | 0.17248 | 1
4743 | 0.25538 | 0.16569 | 0.93132 | 0 | 0 | 1 | 0.25538 | 0.16569 | 1
4744 | 0.14506 | 0.1624 | 0.93132 | 0 | 0 | 1 | 0.14506 | 0.1624 | 1
4745 | 0.025519 | 0.14852 | 0.93132 | 0 | 0 | 1 | 0.025519 | 0.14852 | 1
4746 | 0 | 0.16626 | 0.93132 | 0 | 1 | 1 | 0 | 0.16626 | 1
4747 | 0 | 0.15266 | 0.93132 | 0 | 1 | 1 | 0 | 0.15266 | 1
4748 | 0 | 0.11267 | 0.93132 | 0 | 1 | 1 | 0 | 0.11267 | 1
4749 | 0 | 0.088177 | 0.93132 | 0 | 1 | 1 | 0 | 0.088177 | 1
4750 | 0 | 0.089424 | 0.93132 | 0 | 0 | 1 | 0 | 0.089424 | 1
4751 | 0 | 0.10316 | 0.93132 | 0 | 0 | 1 | 0 | 0.10316 | 1
4752 | 0 | 0.08908 | 0.93132 | 0 | 0 | 1 | 0 | 0.08908 | 1
4753 | 0 | 0.10488 | 0.93132 | 0 | 0 | 1 | 0 | 0.10488 | 1
4754 | 0 | 0.073561 | 0.93132 | 0 | 0 | 1 | 0 | 0.073561 | 1
4755 | 0 | 0.069217 | 0.93132 | 0 | 0 | 1 | 0 | 0.069217 | 1
4756 | 0 | 0.056062 | 0.93132 | 0 | 0 | 1 | 0 | 0.056062 | 1
4757 | 0 | 0.034456 | 0.93132 | 0 | 0 | 1 | 0 | 0.034456 | 1
4758 | 0 | 0.027332 | 0.93132 | 0 | 0 | 1 | 0 | 0.027332 | 1
4759 | 0 | 0.053634 | 0.93132 | 0 | 0 | 1 | 0 | 0.053634 | 1
4760 | 0 | 0.030849 | 0.93132 | 0 | 0 | 1 | 0 | 0.030849 | 1
4761 | 0.061406 | 0.090491 | 0.93132 | 0 | 0 | 1 | 0.061406 | 0.090491 | 1
4762 | 0.18047 | 0.13864 | 0.93132 | 0 | 0 | 1 | 0.18047 | 0.13864 | 1
4763 | 0.23564 | 0.14979 | 0.93132 | 0 | 0 | 1 | 0.23564 | 0.14979 | 1
4764 | 0.28985 | 0.15852 | 0.93132 | 0 | 0 | 1 | 0.28985 | 0.15852 | 1
4765 | 0.34507 | 0.16943 | 0.93132 | 0 | 0 | 1 | 0.34507 | 0.16943 | 1
4766 | 0.32058 | 0.18074 | 0.93132 | 0 | 0 | 1 | 0.32058 | 0.18074 | 1
4767 | 0.22995 | 0.17323 | 0.93132 | 0 | 0 | 1 | 0.22995 | 0.17323 | 1
4768 | 0.17673 | 0.14357 | 0.93132 | 0 | 0 | 1 | 0.17673 | 0.14357 | 1
4769 | 0.060091 | 0.14249 | 0.93132 | 0 | 0 | 1 | 0.060091 | 0.14249 | 1
4770 | 0 | 0.15604 | 0.93132 | 0 | 1 | 1 | 0 | 0.15604 | 1
4771 | 0 | 0.14734 | 0.93132 | 0 | 1 | 1 | 0 | 0.14734 | 1
4772 | 0 | 0.099007 | 0.93132 | 0 | 1 | 1 | 0 | 0.099007 | 1
4773 | 0 | 0.083921 | 0.93132 | 0 | 1 | 1 | 0 | 0.083921 | 1
4774 | 0 | 0.10669 | 0.93132 | 0 | 0 | 1 | 0 | 0.10669 | 1
4775 | 0 | 0.10839 | 0.93132 | 0 | 0 | 1 | 0 | 0.10839 | 1
4776 | 0 | 0.095247 | 0.93132 | 0 | 0 | 1 | 0 | 0.095247 | 1
4777 | 0 | 0.071448 | 0.93132 | 0 | 0 | 1 | 0 | 0.071448 | 1
4778 | 0 | 0.067681 | 0.93132 | 0 | 0 | 1 | 0 | 0.067681 | 1
4779 | 0 | 0.068121 | 0.93132 | 0 | 0 | 1 | 0 | 0.068121 | 1
4780 | 0 | 0.043453 | 0.93132 | 0 | 0 | 1 | 0 | 0.043453 | 1
4781 | 0 | 0.032034 | 0.93132 | 0 | 0 | 1 | 0 | 0.032034 | 1
4782 | 0 | 0.024808 | 0.93132 | 0 | 0 | 1 | 0 | 0.024808 | 1
4783 | 0 | 0.028465 | 0.93132 | 0 | 0 | 1 | 0 | 0.028465 | 1
4784 | 0 | 0.021912 | 0.93132 | 0 | 0 | 1 | 0 | 0.021912 | 1
4785 | 0.10198 | 0.071336 | 0.93132 | 0 | 0 | 1 | 0.10198 | 0.071336 | 1
4786 | 0.25155 | 0.1221 | 0.93132 | 0 | 0 | 1 | 0.25155 | 0.1221 | 1
4787 | 0.24343 | 0.14423 | 0.93132 | 0 | 0 | 1 | 0.24343 | 0.14423 | 1
4788 | 0.28565 | 0.15556 | 0.93132 | 0 | 0 | 1 | 0.28565 | 0.15556 | 1
4789 | 0.29315 | 0.15971 | 0.93132 | 0 | 0 | 1 | 0.29315 | 0.15971 | 1
4790 | 0.24119 | 0.17086 | 0.93132 | 0 | 0 | 1 | 0.24119 | 0.17086 | 1
4791 | 0.20737 | 0.1715 | 0.93132 | 0 | 0 | 1 | 0.20737 | 0.1715 | 1
4792 | 0.15991 | 0.15225 | 0.93132 | 0 | 0 | 1 | 0.15991 | 0.15225 | 1
4793 | 0.073855 | 0.15507 | 0.93132 | 0 | 0 | 1 | 0.073855 | 0.15507 | 1
4794 | 0 | 0.17108 | 0.93132 | 0 | 1 | 1 | 0 | 0.17108 | 1
4795 | 0 | 0.16798 | 0.93132 | 0 | 1 | 1 | 0 | 0.16798 | 1
4796 | 0 | 0.091339 | 0.93132 | 0 | 1 | 1 | 0 | 0.091339 | 1
4797 | 0 | 0.06472 | 0.93132 | 0 | 1 | 1 | 0 | 0.06472 | 1
4798 | 0 | 0.088739 | 0.93132 | 0 | 0 | 1 | 0 | 0.088739 | 1
4799 | 0 | 0.090491 | 0.93132 | 0 | 0 | 1 | 0 | 0.090491 | 1
4800 | 0 | 0.073062 | 0.93132 | 0 | 0 | 1 | 0 | 0.073062 | 1
4801 | 0 | 0.073934 | 0.93132 | 0 | 0 | 1 | 0 | 0.073934 | 1
4802 | 0 | 0.050044 | 0.93132 | 0 | 0 | 1 | 0 | 0.050044 | 1
4803 | 0 | 0.056111 | 0.93132 | 0 | 0 | 1 | 0 | 0.056111 | 1
4804 | 0 | 0.027719 | 0.93132 | 0 | 0 | 1 | 0 | 0.027719 | 1
4805 | 0 | 0.034358 | 0.93132 | 0 | 0 | 1 | 0 | 0.034358 | 1
4806 | 0 | 0 | 0.93132 | 0 | 0 | 1 | 0 | 0 | 1
4807 | 0 | 0.023348 | 0.93132 | 0 | 0 | 1 | 0 | 0.023348 | 1
4808 | 0 | 0.032932 | 0.93132 | 0 | 0 | 1 | 0 | 0.032932 | 1
4809 | 0.14217 | 0.084278 | 0.93132 | 0 | 0 | 1 | 0.14217 | 0.084278 | 1
4810 | 0.28549 | 0.14873 | 0.93132 | 0 | 0 | 1 | 0.28549 | 0.14873 | 1
4811 | 0.28837 | 0.19052 | 0.93132 | 0 | 0 | 1 | 0.28837 | 0.19052 | 1
4812 | 0.40296 | 0.21735 | 0.93132 | 0 | 0 | 1 | 0.40296 | 0.21735 | 1
4813 | 0.32754 | 0.22283 | 0.93132 | 0 | 0 | 1 | 0.32754 | 0.22283 | 1
4814 | 0.24167 | 0.2254 | 0.93132 | 0 | 0 | 1 | 0.24167 | 0.2254 | 1
4815 | 0.21883 | 0.2141 | 0.93132 | 0 | 0 | 1 | 0.21883 | 0.2141 | 1
4816 | 0.19137 | 0.19513 | 0.93132 | 0 | 0 | 1 | 0.19137 | 0.19513 | 1
4817 | 0.12854 | 0.20593 | 0.93132 | 0 | 0 | 1 | 0.12854 | 0.20593 | 1
4818 | 0 | 0.18916 | 0.93132 | 0 | 1 | 1 | 0 | 0.18916 | 1
4819 | 0 | 0.1602 | 0.93132 | 0 | 1 | 1 | 0 | 0.1602 | 1
4820 | 0 | 0.090223 | 0.93132 | 0 | 1 | 1 | 0 | 0.090223 | 1
4821 | 0 | 0.068308 | 0.93132 | 0 | 1 | 1 | 0 | 0.068308 | 1
4822 | 0 | 0.086598 | 0.93132 | 0 | 0 | 1 | 0 | 0.086598 | 1
4823 | 0 | 0.097101 | 0.93132 | 0 | 0 | 1 | 0 | 0.097101 | 1
4824 | 0 | 0.074983 | 0.93132 | 0 | 0 | 1 | 0 | 0.074983 | 1
4825 | 0 | 0.061051 | 0.93132 | 0 | 0 | 1 | 0 | 0.061051 | 1
4826 | 0 | 0.04519 | 0.93132 | 0 | 0 | 1 | 0 | 0.04519 | 1
4827 | 0 | 0.043095 | 0.93132 | 0 | 0 | 1 | 0 | 0.043095 | 1
4828 | 0 | 0.024116 | 0.93132 | 0 | 0 | 1 | 0 | 0.024116 | 1
4829 | 0 | 0.039126 | 0.93132 | 0 | 0 | 1 | 0 | 0.039126 | 1
4830 | 0 | 0.0023632 | 0.93132 | 0 | 0 | 1 | 0 | 0.0023632 | 1
4831 | 0 | 0.025545 | 0.93132 | 0 | 0 | 1 | 0 | 0.025545 | 1
4832 | 0 | 0.057174 | 0.93132 | 0 | 0 | 1 | 0 | 0.057174 | 1
4833 | 0.096611 | 0.08948 | 0.93132 | 0 | 0 | 1 | 0.096611 | 0.08948 | 1
4834 | 0.28007 | 0.11356 | 0.93132 | 0 | 0 | 1 | 0.28007 | 0.11356 | 1
4835 | 0.27616 | 0.15728 | 0.93132 | 0 | 0 | 1 | 0.27616 | 0.15728 | 1
4836 | 0.34087 | 0.17823 | 0.93132 | 0 | 0 | 1 | 0.34087 | 0.17823 | 1
4837 | 0.27857 | 0.19572 | 0.93132 | 0 | 0 | 1 | 0.27857 | 0.19572 | 1
4838 | 0.19756 | 0.21564 | 0.93132 | 0 | 0 | 1 | 0.19756 | 0.21564 | 1
4839 | 0.17867 | 0.21755 | 0.93132 | 0 | 0 | 1 | 0.17867 | 0.21755 | 1
4840 | 0.12786 | 0.20884 | 0.93132 | 0 | 0 | 1 | 0.12786 | 0.20884 | 1
4841 | 0.044701 | 0.19978 | 0.93132 | 0 | 0 | 1 | 0.044701 | 0.19978 | 1
4842 | 0 | 0.17103 | 0.93132 | 0 | 1 | 1 | 0 | 0.17103 | 1
4843 | 0 | 0.15089 | 0.93132 | 0 | 1 | 1 | 0 | 0.15089 | 1
4844 | 0 | 0.084888 | 0.93132 | 0 | 1 | 1 | 0 | 0.084888 | 1
4845 | 0 | 0.06253 | 0.93132 | 0 | 1 | 1 | 0 | 0.06253 | 1
4846 | 0 | 0.071526 | 0.93132 | 0 | 0 | 1 | 0 | 0.071526 | 1
4847 | 0 | 0.099529 | 0.93132 | 0 | 0 | 1 | 0 | 0.099529 | 1
4848 | 0 | 0.072479 | 0.93132 | 0 | 0 | 1 | 0 | 0.072479 | 1
4849 | 0 | 0.056126 | 0.96448 | 0 | 0 | 1 | 0 | 0.056126 | 1
4850 | 0 | 0.057211 | 0.96448 | 0 | 0 | 1 | 0 | 0.057211 | 1
4851 | 0 | 0.047478 | 0.96448 | 0 | 0 | 1 | 0 | 0.047478 | 1
4852 | 0 | 0.03388 | 0.96448 | 0 | 0 | 1 | 0 | 0.03388 | 1
4853 | 0 | 0.036787 | 0.96448 | 0 | 0 | 1 | 0 | 0.036787 | 1
4854 | 0 | 0.0051408 | 0.96448 | 0 | 0 | 1 | 0 | 0.0051408 | 1
4855 | 0 | 0.039073 | 0.96448 | 0 | 0 | 1 | 0 | 0.039073 | 1
4856 | 0 | 0.060361 | 0.96448 | 0 | 0 | 1 | 0 | 0.060361 | 1
4857 | 0.041749 | 0.11156 | 0.96448 | 0 | 0 | 1 | 0.041749 | 0.11156 | 1
4858 | 0.16848 | 0.12281 | 0.96448 | 0 | 0 | 1 | 0.16848 | 0.12281 | 1
4859 | 0.22556 | 0.16384 | 0.96448 | 0 | 0 | 1 | 0.22556 | 0.16384 | 1
4860 | 0.33156 | 0.18171 | 0.96448 | 0 | 0 | 1 | 0.33156 | 0.18171 | 1
4861 | 0.29501 | 0.21924 | 0.96448 | 0 | 0 | 1 | 0.29501 | 0.21924 | 1
4862 | 0.25078 | 0.23157 | 0.96448 | 0 | 0 | 1 | 0.25078 | 0.23157 | 1
4863 | 0.2384 | 0.22125 | 0.96448 | 0 | 0 | 1 | 0.2384 | 0.22125 | 1
4864 | 0.12159 | 0.20012 | 0.96448 | 0 | 0 | 1 | 0.12159 | 0.20012 | 1
4865 | 0.025609 | 0.18932 | 0.96448 | 0 | 0 | 1 | 0.025609 | 0.18932 | 1
4866 | 0 | 0.17056 | 0.96448 | 0 | 1 | 1 | 0 | 0.17056 | 1
4867 | 0 | 0.13942 | 0.96448 | 0 | 1 | 1 | 0 | 0.13942 | 1
4868 | 0 | 0.10253 | 0.96448 | 0 | 1 | 1 | 0 | 0.10253 | 1
4869 | 0 | 0.089877 | 0.96448 | 0 | 1 | 1 | 0 | 0.089877 | 1
4870 | 0 | 0.097627 | 0.96448 | 0 | 0 | 1 | 0 | 0.097627 | 1
4871 | 0 | 0.10567 | 0.96448 | 0 | 0 | 1 | 0 | 0.10567 | 1
4872 | 0 | 0.08063 | 0.96448 | 0 | 0 | 1 | 0 | 0.08063 | 1
4873 | 0 | 0.046505 | 0.96448 | 0 | 0 | 1 | 0 | 0.046505 | 1
4874 | 0 | 0.077811 | 0.96448 | 0 | 0 | 1 | 0 | 0.077811 | 1
4875 | 0 | 0.056031 | 0.96448 | 0 | 0 | 1 | 0 | 0.056031 | 1
4876 | 0 | 0.036203 | 0.96448 | 0 | 0 | 1 | 0 | 0.036203 | 1
4877 | 0 | 0.031651 | 0.96448 | 0 | 0 | 1 | 0 | 0.031651 | 1
4878 | 0 | 0.020926 | 0.96448 | 0 | 0 | 1 | 0 | 0.020926 | 1
4879 | 0 | 0.048097 | 0.96448 | 0 | 0 | 1 | 0 | 0.048097 | 1
4880 | 0 | 0.068112 | 0.96448 | 0 | 0 | 1 | 0 | 0.068112 | 1
4881 | 0 | 0.10496 | 0.96448 | 0 | 0 | 1 | 0 | 0.10496 | 1
4882 | 0.11075 | 0.11546 | 0.96448 | 0 | 0 | 1 | 0.11075 | 0.11546 | 1
4883 | 0.16559 | 0.15353 | 0.96448 | 0 | 0 | 1 | 0.16559 | 0.15353 | 1
4884 | 0.18882 | 0.14637 | 0.96448 | 0 | 0 | 1 | 0.18882 | 0.14637 | 1
4885 | 0.2269 | 0.186 | 0.96448 | 0 | 0 | 1 | 0.2269 | 0.186 | 1
4886 | 0.2212 | 0.21006 | 0.96448 | 0 | 0 | 1 | 0.2212 | 0.21006 | 1
4887 | 0.21188 | 0.22875 | 0.96448 | 0 | 0 | 1 | 0.21188 | 0.22875 | 1
4888 | 0.11873 | 0.23386 | 0.96448 | 0 | 0 | 1 | 0.11873 | 0.23386 | 1
4889 | 0.0041791 | 0.19919 | 0.96448 | 0 | 0 | 1 | 0.0041791 | 0.19919 | 1
4890 | 0 | 0.17169 | 0.96448 | 0 | 1 | 1 | 0 | 0.17169 | 1
4891 | 0 | 0.12066 | 0.96448 | 0 | 1 | 1 | 0 | 0.12066 | 1
4892 | 0 | 0.076432 | 0.96448 | 0 | 1 | 1 | 0 | 0.076432 | 1
4893 | 0 | 0.068798 | 0.96448 | 0 | 1 | 1 | 0 | 0.068798 | 1
4894 | 0 | 0.081149 | 0.96448 | 0 | 0 | 1 | 0 | 0.081149 | 1
4895 | 0 | 0.09908 | 0.96448 | 0 | 0 | 1 | 0 | 0.09908 | 1
4896 | 0 | 0.063825 | 0.96448 | 0 | 0 | 1 | 0 | 0.063825 | 1
4897 | 0 | 0.06834 | 0.96448 | 0 | 0 | 1 | 0 | 0.06834 | 1
4898 | 0 | 0.0729 | 0.96448 | 0 | 0 | 1 | 0 | 0.0729 | 1
4899 | 0 | 0.053088 | 0.96448 | 0 | 0 | 1 | 0 | 0.053088 | 1
4900 | 0 | 0.041069 | 0.96448 | 0 | 0 | 1 | 0 | 0.041069 | 1
4901 | 0 | 0.033366 | 0.96448 | 0 | 0 | 1 | 0 | 0.033366 | 1
4902 | 0 | 0.024133 | 0.96448 | 0 | 0 | 1 | 0 | 0.024133 | 1
4903 | 0 | 0.048847 | 0.96448 | 0 | 0 | 1 | 0 | 0.048847 | 1
4904 | 0 | 0.074675 | 0.96448 | 0 | 0 | 1 | 0 | 0.074675 | 1
4905 | 0 | 0.084712 | 0.96448 | 0 | 0 | 1 | 0 | 0.084712 | 1
4906 | 0.12608 | 0.12333 | 0.96448 | 0 | 0 | 1 | 0.12608 | 0.12333 | 1
4907 | 0.17616 | 0.14026 | 0.96448 | 0 | 0 | 1 | 0.17616 | 0.14026 | 1
4908 | 0.23533 | 0.13481 | 0.96448 | 0 | 0 | 1 | 0.23533 | 0.13481 | 1
4909 | 0.2664 | 0.16292 | 0.96448 | 0 | 0 | 1 | 0.2664 | 0.16292 | 1
4910 | 0.25275 | 0.16277 | 0.96448 | 0 | 0 | 1 | 0.25275 | 0.16277 | 1
4911 | 0.28456 | 0.18055 | 0.96448 | 0 | 0 | 1 | 0.28456 | 0.18055 | 1
4912 | 0.18414 | 0.16073 | 0.96448 | 0 | 0 | 1 | 0.18414 | 0.16073 | 1
4913 | 0.067474 | 0.14027 | 0.96448 | 0 | 0 | 1 | 0.067474 | 0.14027 | 1
4914 | 0 | 0.11743 | 0.96448 | 0 | 1 | 1 | 0 | 0.11743 | 1
4915 | 0 | 0.087959 | 0.96448 | 0 | 1 | 1 | 0 | 0.087959 | 1
4916 | 0 | 0.047606 | 0.96448 | 0 | 1 | 1 | 0 | 0.047606 | 1
4917 | 0 | 0.038936 | 0.96448 | 0 | 1 | 1 | 0 | 0.038936 | 1
4918 | 0 | 0.038908 | 0.96448 | 0 | 0 | 1 | 0 | 0.038908 | 1
4919 | 0 | 0.063659 | 0.96448 | 0 | 0 | 1 | 0 | 0.063659 | 1
4920 | 0 | 0.034621 | 0.96448 | 0 | 0 | 1 | 0 | 0.034621 | 1
4921 | 0 | 0.062404 | 0.96448 | 0 | 0 | 1 | 0 | 0.062404 | 1
4922 | 0 | 0.050646 | 0.96448 | 0 | 0 | 1 | 0 | 0.050646 | 1
4923 | 0 | 0.038663 | 0.96448 | 0 | 0 | 1 | 0 | 0.038663 | 1
4924 | 0 | 0.0058103 | 0.96448 | 0 | 0 | 1 | 0 | 0.0058103 | 1
4925 | 0 | 0.014604 | 0.96448 | 0 | 0 | 1 | 0 | 0.014604 | 1
4926 | 0 | 0.012345 | 0.96448 | 0 | 0 | 1 | 0 | 0.012345 | 1
4927 | 0 | 0.030741 | 0.96448 | 0 | 0 | 1 | 0 | 0.030741 | 1
4928 | 0 | 0.029966 | 0.96448 | 0 | 0 | 1 | 0 | 0.029966 | 1
4929 | 0 | 0.050314 | 0.96448 | 0 | 0 | 1 | 0 | 0.050314 | 1
4930 | 0.14703 | 0.087293 | 0.96448 | 0 | 0 | 1 | 0.14703 | 0.087293 | 1
4931 | 0.19682 | 0.12209 | 0.96448 | 0 | 0 | 1 | 0.19682 | 0.12209 | 1
4932 | 0.23759 | 0.12105 | 0.96448 | 0 | 0 | 1 | 0.23759 | 0.12105 | 1
4933 | 0.29819 | 0.13677 | 0.96448 | 0 | 0 | 1 | 0.29819 | 0.13677 | 1
4934 | 0.29711 | 0.14228 | 0.96448 | 0 | 0 | 1 | 0.29711 | 0.14228 | 1
4935 | 0.26529 | 0.14913 | 0.96448 | 0 | 0 | 1 | 0.26529 | 0.14913 | 1
4936 | 0.25704 | 0.13046 | 0.96448 | 0 | 0 | 1 | 0.25704 | 0.13046 | 1
4937 | 0.094365 | 0.10632 | 0.96448 | 0 | 0 | 1 | 0.094365 | 0.10632 | 1
4938 | 0 | 0.08193 | 0.96448 | 0 | 1 | 1 | 0 | 0.08193 | 1
4939 | 0 | 0.064322 | 0.96448 | 0 | 1 | 1 | 0 | 0.064322 | 1
4940 | 0 | 0.0060231 | 0.96448 | 0 | 1 | 1 | 0 | 0.0060231 | 1
4941 | 0 | 0.0047676 | 0.96448 | 0 | 1 | 1 | 0 | 0.0047676 | 1
4942 | 0 | 0.0053538 | 0.96448 | 0 | 0 | 1 | 0 | 0.0053538 | 1
4943 | 0 | 0.037301 | 0.96448 | 0 | 0 | 1 | 0 | 0.037301 | 1
4944 | 0 | 0.0035736 | 0.96448 | 0 | 0 | 1 | 0 | 0.0035736 | 1
4945 | 0 | 0.027379 | 0.96448 | 0 | 0 | 1 | 0 | 0.027379 | 1
4946 | 0 | 0.0039331 | 0.96448 | 0 | 0 | 1 | 0 | 0.0039331 | 1
4947 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4948 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4949 | 0 | 0.0031428 | 0.96448 | 0 | 0 | 1 | 0 | 0.0031428 | 1
4950 | 0 | 0.012762 | 0.96448 | 0 | 0 | 1 | 0 | 0.012762 | 1
4951 | 0 | 0.010968 | 0.96448 | 0 | 0 | 1 | 0 | 0.010968 | 1
4952 | 0 | 0.009654 | 0.96448 | 0 | 0 | 1 | 0 | 0.009654 | 1
4953 | 0.059711 | 0.047096 | 0.96448 | 0 | 0 | 1 | 0.059711 | 0.047096 | 1
4954 | 0.22573 | 0.068621 | 0.96448 | 0 | 0 | 1 | 0.22573 | 0.068621 | 1
4955 | 0.31958 | 0.10897 | 0.96448 | 0 | 0 | 1 | 0.31958 | 0.10897 | 1
4956 | 0.36191 | 0.14052 | 0.96448 | 0 | 0 | 1 | 0.36191 | 0.14052 | 1
4957 | 0.39012 | 0.15365 | 0.96448 | 0 | 0 | 1 | 0.39012 | 0.15365 | 1
4958 | 0.37893 | 0.1552 | 0.96448 | 0 | 0 | 1 | 0.37893 | 0.1552 | 1
4959 | 0.33523 | 0.12224 | 0.96448 | 0 | 0 | 1 | 0.33523 | 0.12224 | 1
4960 | 0.22688 | 0.10012 | 0.96448 | 0 | 0 | 1 | 0.22688 | 0.10012 | 1
4961 | 0.074394 | 0.08562 | 0.96448 | 0 | 0 | 1 | 0.074394 | 0.08562 | 1
4962 | 0 | 0.063128 | 0.96448 | 0 | 1 | 1 | 0 | 0.063128 | 1
4963 | 0 | 0.05297 | 0.96448 | 0 | 1 | 1 | 0 | 0.05297 | 1
4964 | 0 | 0.011362 | 0.96448 | 0 | 1 | 1 | 0 | 0.011362 | 1
4965 | 0 | 0.0010298 | 0.96448 | 0 | 1 | 1 | 0 | 0.0010298 | 1
4966 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4967 | 0 | 0.013138 | 0.96448 | 0 | 0 | 1 | 0 | 0.013138 | 1
4968 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4969 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4970 | 0 | 0.0018955 | 0.96448 | 0 | 0 | 1 | 0 | 0.0018955 | 1
4971 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4972 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4973 | 0 | 0.0030875 | 0.96448 | 0 | 0 | 1 | 0 | 0.0030875 | 1
4974 | 0 | 0.010052 | 0.96448 | 0 | 0 | 1 | 0 | 0.010052 | 1
4975 | 0 | 0.016989 | 0.96448 | 0 | 0 | 1 | 0 | 0.016989 | 1
4976 | 0 | 0.019463 | 0.96448 | 0 | 0 | 1 | 0 | 0.019463 | 1
4977 | 0.052615 | 0.068754 | 0.96448 | 0 | 0 | 1 | 0.052615 | 0.068754 | 1
4978 | 0.21495 | 0.11139 | 0.96448 | 0 | 0 | 1 | 0.21495 | 0.11139 | 1
4979 | 0.29852 | 0.15831 | 0.96448 | 0 | 0 | 1 | 0.29852 | 0.15831 | 1
4980 | 0.32749 | 0.18644 | 0.96448 | 0 | 0 | 1 | 0.32749 | 0.18644 | 1
4981 | 0.34724 | 0.2033 | 0.96448 | 0 | 0 | 1 | 0.34724 | 0.2033 | 1
4982 | 0.36916 | 0.22048 | 0.96448 | 0 | 0 | 1 | 0.36916 | 0.22048 | 1
4983 | 0.31536 | 0.16739 | 0.96448 | 0 | 0 | 1 | 0.31536 | 0.16739 | 1
4984 | 0.22867 | 0.16933 | 0.96448 | 0 | 0 | 1 | 0.22867 | 0.16933 | 1
4985 | 0.10139 | 0.14929 | 0.96448 | 0 | 0 | 1 | 0.10139 | 0.14929 | 1
4986 | 0 | 0.12604 | 0.96448 | 0 | 1 | 1 | 0 | 0.12604 | 1
4987 | 0 | 0.095903 | 0.96448 | 0 | 1 | 1 | 0 | 0.095903 | 1
4988 | 0 | 0.079596 | 0.96448 | 0 | 1 | 1 | 0 | 0.079596 | 1
4989 | 0 | 0.057295 | 0.96448 | 0 | 1 | 1 | 0 | 0.057295 | 1
4990 | 0 | 0.061047 | 0.96448 | 0 | 0 | 1 | 0 | 0.061047 | 1
4991 | 0 | 0.061898 | 0.96448 | 0 | 0 | 1 | 0 | 0.061898 | 1
4992 | 0 | 0.054963 | 0.96448 | 0 | 0 | 1 | 0 | 0.054963 | 1
4993 | 0 | 0 | 0.96448 | 0 | 0 | 1 | 0 | 0 | 1
4994 | 0 | 0.046452 | 0.96448 | 0 | 0 | 1 | 0 | 0.046452 | 1
4995 | 0 | 0.026659 | 0.96448 | 0 | 0 | 1 | 0 | 0.026659 | 1
4996 | 0 | 0.0097674 | 0.96448 | 0 | 0 | 1 | 0 | 0.0097674 | 1
4997 | 0 | 0.027831 | 0.96448 | 0 | 0 | 1 | 0 | 0.027831 | 1
4998 | 0 | 0.043872 | 0.96448 | 0 | 0 | 1 | 0 | 0.043872 | 1
4999 | 0 | 0.055218 | 0.96448 | 0 | 0 | 1 | 0 | 0.055218 | 1
5000 | 0 | 0.061559 | 0.96448 | 0 | 0 | 1 | 0 | 0.061559 | 1
5001 | 0.108 | 0.12441 | 0.96448 | 0 | 0 | 1 | 0.108 | 0.12441 | 1
5002 | 0.31462 | 0.18867 | 0.96448 | 0 | 0 | 1 | 0.31462 | 0.18867 | 1
5003 | 0.39227 | 0.20163 | 0.96448 | 0 | 0 | 1 | 0.39227 | 0.20163 | 1
5004 | 0.38023 | 0.22946 | 0.96448 | 0 | 0 | 1 | 0.38023 | 0.22946 | 1
5005 | 0.36137 | 0.24898 | 0.96448 | 0 | 0 | 1 | 0.36137 | 0.24898 | 1
5006 | 0.36242 | 0.27329 | 0.96448 | 0 | 0 | 1 | 0.36242 | 0.27329 | 1
5007 | 0.3556 | 0.21255 | 0.96448 | 0 | 0 | 1 | 0.3556 | 0.21255 | 1
5008 | 0.21421 | 0.22344 | 0.96448 | 0 | 0 | 1 | 0.21421 | 0.22344 | 1
5009 | 0.10066 | 0.22044 | 0.96448 | 0 | 0 | 1 | 0.10066 | 0.22044 | 1
5010 | 0 | 0.18176 | 0.96448 | 0 | 1 | 1 | 0 | 0.18176 | 1
5011 | 0 | 0.13487 | 0.96448 | 0 | 1 | 1 | 0 | 0.13487 | 1
5012 | 0 | 0.14169 | 0.96448 | 0 | 1 | 1 | 0 | 0.14169 | 1
5013 | 0 | 0.12225 | 0.96448 | 0 | 1 | 1 | 0 | 0.12225 | 1
5014 | 0 | 0.12177 | 0.96448 | 0 | 0 | 1 | 0 | 0.12177 | 1
5015 | 0 | 0.1042 | 0.96448 | 0 | 0 | 1 | 0 | 0.1042 | 1
5016 | 0 | 0.1136 | 0.96448 | 0 | 0 | 1 | 0 | 0.1136 | 1
5017 | 0 | 0.038204 | 1 | 0 | 0 | 1 | 0 | 0.038204 | 1
5018 | 0 | 0.092111 | 1 | 0 | 0 | 1 | 0 | 0.092111 | 1
5019 | 0 | 0.066655 | 1 | 0 | 0 | 1 | 0 | 0.066655 | 1
5020 | 0 | 0.050228 | 1 | 0 | 0 | 1 | 0 | 0.050228 | 1
5021 | 0 | 0.053767 | 1 | 0 | 0 | 1 | 0 | 0.053767 | 1
5022 | 0 | 0.056125 | 1 | 0 | 0 | 1 | 0 | 0.056125 | 1
5023 | 0 | 0.082971 | 1 | 0 | 0 | 1 | 0 | 0.082971 | 1
5024 | 0 | 0.10644 | 1 | 0 | 0 | 1 | 0 | 0.10644 | 1
5025 | 0.076809 | 0.15917 | 1 | 0 | 0 | 1 | 0.076809 | 0.15917 | 1
5026 | 0.28442 | 0.21935 | 1 | 0 | 0 | 1 | 0.28442 | 0.21935 | 1
5027 | 0.33811 | 0.22402 | 1 | 0 | 0 | 1 | 0.33811 | 0.22402 | 1
5028 | 0.38012 | 0.23735 | 1 | 0 | 0 | 1 | 0.38012 | 0.23735 | 1
5029 | 0.39412 | 0.28165 | 1 | 0 | 0 | 1 | 0.39412 | 0.28165 | 1
5030 | 0.39474 | 0.31101 | 1 | 0 | 0 | 1 | 0.39474 | 0.31101 | 1
5031 | 0.33191 | 0.28821 | 1 | 0 | 0 | 1 | 0.33191 | 0.28821 | 1
5032 | 0.28988 | 0.2693 | 1 | 0 | 0 | 1 | 0.28988 | 0.2693 | 1
5033 | 0.13358 | 0.27689 | 1 | 0 | 0 | 1 | 0.13358 | 0.27689 | 1
5034 | 0 | 0.25575 | 1 | 0 | 1 | 1 | 0 | 0.25575 | 1
5035 | 0 | 0.20743 | 1 | 0 | 1 | 1 | 0 | 0.20743 | 1
5036 | 0 | 0.19739 | 1 | 0 | 1 | 1 | 0 | 0.19739 | 1
5037 | 0 | 0.18223 | 1 | 0 | 1 | 1 | 0 | 0.18223 | 1
5038 | 0 | 0.1769 | 1 | 0 | 0 | 1 | 0 | 0.1769 | 1
5039 | 0 | 0.15842 | 1 | 0 | 0 | 1 | 0 | 0.15842 | 1
5040 | 0 | 0.18739 | 1 | 0 | 0 | 1 | 0 | 0.18739 | 1
5041 | 0 | 0.083338 | 0.91183 | 0 | 0 | 1 | 0 | 0.083338 | 1
5042 | 0 | 0.11801 | 0.91183 | 0 | 0 | 1 | 0 | 0.11801 | 1
5043 | 0 | 0.10029 | 0.91183 | 0 | 0 | 1 | 0 | 0.10029 | 1
5044 | 0 | 0.075264 | 0.91183 | 0 | 0 | 1 | 0 | 0.075264 | 1
5045 | 0 | 0.076593 | 0.91183 | 0 | 0 | 1 | 0 | 0.076593 | 1
5046 | 0 | 0.090423 | 0.91183 | 0 | 0 | 1 | 0 | 0.090423 | 1
5047 | 0 | 0.1082 | 0.91183 | 0 | 0 | 1 | 0 | 0.1082 | 1
5048 | 0 | 0.11508 | 0.91183 | 0 | 0 | 1 | 0 | 0.11508 | 1
5049 | 0.085745 | 0.17231 | 0.91183 | 0 | 0 | 1 | 0.085745 | 0.17231 | 1
5050 | 0.27951 | 0.20612 | 0.91183 | 0 | 0 | 1 | 0.27951 | 0.20612 | 1
5051 | 0.30589 | 0.21492 | 0.91183 | 0 | 0 | 1 | 0.30589 | 0.21492 | 1
5052 | 0.32661 | 0.22946 | 0.91183 | 0 | 0 | 1 | 0.32661 | 0.22946 | 1
5053 | 0.4083 | 0.24343 | 0.91183 | 0 | 0 | 1 | 0.4083 | 0.24343 | 1
5054 | 0.41093 | 0.23974 | 0.91183 | 0 | 0 | 1 | 0.41093 | 0.23974 | 1
5055 | 0.2536 | 0.25232 | 0.91183 | 0 | 0 | 1 | 0.2536 | 0.25232 | 1
5056 | 0.21692 | 0.2638 | 0.91183 | 0 | 0 | 1 | 0.21692 | 0.2638 | 1
5057 | 0.087093 | 0.27769 | 0.91183 | 0 | 0 | 1 | 0.087093 | 0.27769 | 1
5058 | 0 | 0.20904 | 0.91183 | 0 | 1 | 1 | 0 | 0.20904 | 1
5059 | 0 | 0.16277 | 0.91183 | 0 | 1 | 1 | 0 | 0.16277 | 1
5060 | 0 | 0.15784 | 0.91183 | 0 | 1 | 1 | 0 | 0.15784 | 1
5061 | 0 | 0.1525 | 0.91183 | 0 | 1 | 1 | 0 | 0.1525 | 1
5062 | 0 | 0.16058 | 0.91183 | 0 | 0 | 1 | 0 | 0.16058 | 1
5063 | 0 | 0.15604 | 0.91183 | 0 | 0 | 1 | 0 | 0.15604 | 1
5064 | 0 | 0.15826 | 0.91183 | 0 | 0 | 1 | 0 | 0.15826 | 1
5065 | 0 | 0.14583 | 0.91183 | 0 | 0 | 1 | 0 | 0.14583 | 1
5066 | 0 | 0.092838 | 0.91183 | 0 | 0 | 1 | 0 | 0.092838 | 1
5067 | 0 | 0.087881 | 0.91183 | 0 | 0 | 1 | 0 | 0.087881 | 1
5068 | 0 | 0.098852 | 0.91183 | 0 | 0 | 1 | 0 | 0.098852 | 1
5069 | 0 | 0.084853 | 0.91183 | 0 | 0 | 1 | 0 | 0.084853 | 1
5070 | 0 | 0.069903 | 0.91183 | 0 | 0 | 1 | 0 | 0.069903 | 1
5071 | 0 | 0.066884 | 0.91183 | 0 | 0 | 1 | 0 | 0.066884 | 1
5072 | 0 | 0.098003 | 0.91183 | 0 | 0 | 1 | 0 | 0.098003 | 1
5073 | 0.00041796 | 0.136 | 0.91183 | 0 | 0 | 1 | 0.00041796 | 0.136 | 1
5074 | 0.12531 | 0.16592 | 0.91183 | 0 | 0 | 1 | 0.12531 | 0.16592 | 1
5075 | 0.15654 | 0.18703 | 0.91183 | 0 | 0 | 1 | 0.15654 | 0.18703 | 1
5076 | 0.2267 | 0.20004 | 0.91183 | 0 | 0 | 1 | 0.2267 | 0.20004 | 1
5077 | 0.25342 | 0.20308 | 0.91183 | 0 | 0 | 1 | 0.25342 | 0.20308 | 1
5078 | 0.27642 | 0.21859 | 0.91183 | 0 | 0 | 1 | 0.27642 | 0.21859 | 1
5079 | 0.18059 | 0.23992 | 0.91183 | 0 | 0 | 1 | 0.18059 | 0.23992 | 1
5080 | 0.17193 | 0.23873 | 0.91183 | 0 | 0 | 1 | 0.17193 | 0.23873 | 1
5081 | 0.068863 | 0.24433 | 0.91183 | 0 | 0 | 1 | 0.068863 | 0.24433 | 1
5082 | 0 | 0.19929 | 0.91183 | 0 | 1 | 1 | 0 | 0.19929 | 1
5083 | 0 | 0.16756 | 0.91183 | 0 | 1 | 1 | 0 | 0.16756 | 1
5084 | 0 | 0.16025 | 0.91183 | 0 | 1 | 1 | 0 | 0.16025 | 1
5085 | 0 | 0.15789 | 0.91183 | 0 | 1 | 1 | 0 | 0.15789 | 1
5086 | 0 | 0.15875 | 0.91183 | 0 | 0 | 1 | 0 | 0.15875 | 1
5087 | 0 | 0.12207 | 0.91183 | 0 | 0 | 1 | 0 | 0.12207 | 1
5088 | 0 | 0.10191 | 0.91183 | 0 | 0 | 1 | 0 | 0.10191 | 1
5089 | 0 | 0.14283 | 0.91183 | 0 | 0 | 1 | 0 | 0.14283 | 1
5090 | 0 | 0.050845 | 0.91183 | 0 | 0 | 1 | 0 | 0.050845 | 1
5091 | 0 | 0.059297 | 0.91183 | 0 | 0 | 1 | 0 | 0.059297 | 1
5092 | 0 | 0.061997 | 0.91183 | 0 | 0 | 1 | 0 | 0.061997 | 1
5093 | 0 | 0.046391 | 0.91183 | 0 | 0 | 1 | 0 | 0.046391 | 1
5094 | 0 | 0.037232 | 0.91183 | 0 | 0 | 1 | 0 | 0.037232 | 1
5095 | 0 | 0.040312 | 0.91183 | 0 | 0 | 1 | 0 | 0.040312 | 1
5096 | 0 | 0.068875 | 0.91183 | 0 | 0 | 1 | 0 | 0.068875 | 1
5097 | 0 | 0.098721 | 0.91183 | 0 | 0 | 1 | 0 | 0.098721 | 1
5098 | 0.084774 | 0.14349 | 0.91183 | 0 | 0 | 1 | 0.084774 | 0.14349 | 1
5099 | 0.1152 | 0.16978 | 0.91183 | 0 | 0 | 1 | 0.1152 | 0.16978 | 1
5100 | 0.16239 | 0.2116 | 0.91183 | 0 | 0 | 1 | 0.16239 | 0.2116 | 1
5101 | 0.16967 | 0.19752 | 0.91183 | 0 | 0 | 1 | 0.16967 | 0.19752 | 1
5102 | 0.18792 | 0.19473 | 0.91183 | 0 | 0 | 1 | 0.18792 | 0.19473 | 1
5103 | 0.12841 | 0.19816 | 0.91183 | 0 | 0 | 1 | 0.12841 | 0.19816 | 1
5104 | 0.092615 | 0.21049 | 0.91183 | 0 | 0 | 1 | 0.092615 | 0.21049 | 1
5105 | 0.0086046 | 0.22987 | 0.91183 | 0 | 0 | 1 | 0.0086046 | 0.22987 | 1
5106 | 0 | 0.17943 | 0.91183 | 0 | 1 | 1 | 0 | 0.17943 | 1
5107 | 0 | 0.15347 | 0.91183 | 0 | 1 | 1 | 0 | 0.15347 | 1
5108 | 0 | 0.17185 | 0.91183 | 0 | 1 | 1 | 0 | 0.17185 | 1
5109 | 0 | 0.16462 | 0.91183 | 0 | 1 | 1 | 0 | 0.16462 | 1
5110 | 0 | 0.15632 | 0.91183 | 0 | 0 | 1 | 0 | 0.15632 | 1
5111 | 0 | 0.11854 | 0.91183 | 0 | 0 | 1 | 0 | 0.11854 | 1
5112 | 0 | 0.090141 | 0.91183 | 0 | 0 | 1 | 0 | 0.090141 | 1
5113 | 0 | 0.1005 | 0.91183 | 0 | 0 | 1 | 0 | 0.1005 | 1
5114 | 0 | 0.060474 | 0.91183 | 0 | 0 | 1 | 0 | 0.060474 | 1
5115 | 0 | 0.028919 | 0.91183 | 0 | 0 | 1 | 0 | 0.028919 | 1
5116 | 0 | 0.039401 | 0.91183 | 0 | 0 | 1 | 0 | 0.039401 | 1
5117 | 0 | 0.039962 | 0.91183 | 0 | 0 | 1 | 0 | 0.039962 | 1
5118 | 0 | 0.034626 | 0.91183 | 0 | 0 | 1 | 0 | 0.034626 | 1
5119 | 0 | 0.045566 | 0.91183 | 0 | 0 | 1 | 0 | 0.045566 | 1
5120 | 0 | 0.067767 | 0.91183 | 0 | 0 | 1 | 0 | 0.067767 | 1
5121 | 0 | 0.081287 | 0.91183 | 0 | 0 | 1 | 0 | 0.081287 | 1
5122 | 0.038425 | 0.12368 | 0.91183 | 0 | 0 | 1 | 0.038425 | 0.12368 | 1
5123 | 0.082785 | 0.1519 | 0.91183 | 0 | 0 | 1 | 0.082785 | 0.1519 | 1
5124 | 0.13653 | 0.19735 | 0.91183 | 0 | 0 | 1 | 0.13653 | 0.19735 | 1
5125 | 0.096092 | 0.19369 | 0.91183 | 0 | 0 | 1 | 0.096092 | 0.19369 | 1
5126 | 0.1304 | 0.20136 | 0.91183 | 0 | 0 | 1 | 0.1304 | 0.20136 | 1
5127 | 0.078084 | 0.19417 | 0.91183 | 0 | 0 | 1 | 0.078084 | 0.19417 | 1
5128 | 0.047162 | 0.20041 | 0.91183 | 0 | 0 | 1 | 0.047162 | 0.20041 | 1
5129 | 0 | 0.21006 | 0.91183 | 0 | 0 | 1 | 0 | 0.21006 | 1
5130 | 0 | 0.16683 | 0.91183 | 0 | 1 | 1 | 0 | 0.16683 | 1
5131 | 0 | 0.16143 | 0.91183 | 0 | 1 | 1 | 0 | 0.16143 | 1
5132 | 0 | 0.14312 | 0.91183 | 0 | 1 | 1 | 0 | 0.14312 | 1
5133 | 0 | 0.15435 | 0.91183 | 0 | 1 | 1 | 0 | 0.15435 | 1
5134 | 0 | 0.13224 | 0.91183 | 0 | 0 | 1 | 0 | 0.13224 | 1
5135 | 0 | 0.097701 | 0.91183 | 0 | 0 | 1 | 0 | 0.097701 | 1
5136 | 0 | 0.071106 | 0.91183 | 0 | 0 | 1 | 0 | 0.071106 | 1
5137 | 0 | 0.096965 | 0.91183 | 0 | 0 | 1 | 0 | 0.096965 | 1
5138 | 0 | 0.063796 | 0.91183 | 0 | 0 | 1 | 0 | 0.063796 | 1
5139 | 0 | 0.022631 | 0.91183 | 0 | 0 | 1 | 0 | 0.022631 | 1
5140 | 0 | 0.025783 | 0.91183 | 0 | 0 | 1 | 0 | 0.025783 | 1
5141 | 0 | 0.024696 | 0.91183 | 0 | 0 | 1 | 0 | 0.024696 | 1
5142 | 0 | 0.019387 | 0.91183 | 0 | 0 | 1 | 0 | 0.019387 | 1
5143 | 0 | 0.050661 | 0.91183 | 0 | 0 | 1 | 0 | 0.050661 | 1
5144 | 0 | 0.058973 | 0.91183 | 0 | 0 | 1 | 0 | 0.058973 | 1
5145 | 0.021725 | 0.064857 | 0.91183 | 0 | 0 | 1 | 0.021725 | 0.064857 | 1
5146 | 0.11076 | 0.11099 | 0.91183 | 0 | 0 | 1 | 0.11076 | 0.11099 | 1
5147 | 0.13752 | 0.14575 | 0.91183 | 0 | 0 | 1 | 0.13752 | 0.14575 | 1
5148 | 0.19082 | 0.19341 | 0.91183 | 0 | 0 | 1 | 0.19082 | 0.19341 | 1
5149 | 0.1644 | 0.21414 | 0.91183 | 0 | 0 | 1 | 0.1644 | 0.21414 | 1
5150 | 0.16925 | 0.20857 | 0.91183 | 0 | 0 | 1 | 0.16925 | 0.20857 | 1
5151 | 0.086059 | 0.20103 | 0.91183 | 0 | 0 | 1 | 0.086059 | 0.20103 | 1
5152 | 0.040922 | 0.21406 | 0.91183 | 0 | 0 | 1 | 0.040922 | 0.21406 | 1
5153 | 0 | 0.21151 | 0.91183 | 0 | 0 | 1 | 0 | 0.21151 | 1
5154 | 0 | 0.15736 | 0.91183 | 0 | 1 | 1 | 0 | 0.15736 | 1
5155 | 0 | 0.1625 | 0.91183 | 0 | 1 | 1 | 0 | 0.1625 | 1
5156 | 0 | 0.15225 | 0.91183 | 0 | 1 | 1 | 0 | 0.15225 | 1
5157 | 0 | 0.16794 | 0.91183 | 0 | 1 | 1 | 0 | 0.16794 | 1
5158 | 0 | 0.14994 | 0.91183 | 0 | 0 | 1 | 0 | 0.14994 | 1
5159 | 0 | 0.13799 | 0.91183 | 0 | 0 | 1 | 0 | 0.13799 | 1
5160 | 0 | 0.13586 | 0.91183 | 0 | 0 | 1 | 0 | 0.13586 | 1
5161 | 0 | 0.077216 | 0.91183 | 0 | 0 | 1 | 0 | 0.077216 | 1
5162 | 0 | 0.12262 | 0.91183 | 0 | 0 | 1 | 0 | 0.12262 | 1
5163 | 0 | 0.068685 | 0.91183 | 0 | 0 | 1 | 0 | 0.068685 | 1
5164 | 0 | 0.07014 | 0.91183 | 0 | 0 | 1 | 0 | 0.07014 | 1
5165 | 0 | 0.069925 | 0.91183 | 0 | 0 | 1 | 0 | 0.069925 | 1
5166 | 0 | 0.065395 | 0.91183 | 0 | 0 | 1 | 0 | 0.065395 | 1
5167 | 0 | 0.085869 | 0.91183 | 0 | 0 | 1 | 0 | 0.085869 | 1
5168 | 0 | 0.086544 | 0.91183 | 0 | 0 | 1 | 0 | 0.086544 | 1
5169 | 0.05022 | 0.11896 | 0.91183 | 0 | 0 | 1 | 0.05022 | 0.11896 | 1
5170 | 0.15903 | 0.13183 | 0.91183 | 0 | 0 | 1 | 0.15903 | 0.13183 | 1
5171 | 0.21065 | 0.19031 | 0.91183 | 0 | 0 | 1 | 0.21065 | 0.19031 | 1
5172 | 0.25809 | 0.22004 | 0.91183 | 0 | 0 | 1 | 0.25809 | 0.22004 | 1
5173 | 0.24353 | 0.23726 | 0.91183 | 0 | 0 | 1 | 0.24353 | 0.23726 | 1
5174 | 0.25901 | 0.24492 | 0.91183 | 0 | 0 | 1 | 0.25901 | 0.24492 | 1
5175 | 0.17785 | 0.23272 | 0.91183 | 0 | 0 | 1 | 0.17785 | 0.23272 | 1
5176 | 0.11599 | 0.23319 | 0.91183 | 0 | 0 | 1 | 0.11599 | 0.23319 | 1
5177 | 0.0035835 | 0.2382 | 0.91183 | 0 | 0 | 1 | 0.0035835 | 0.2382 | 1
5178 | 0 | 0.17022 | 0.91183 | 0 | 1 | 1 | 0 | 0.17022 | 1
5179 | 0 | 0.14005 | 0.91183 | 0 | 1 | 1 | 0 | 0.14005 | 1
5180 | 0 | 0.14763 | 0.91183 | 0 | 1 | 1 | 0 | 0.14763 | 1
5181 | 0 | 0.16432 | 0.91183 | 0 | 1 | 1 | 0 | 0.16432 | 1
5182 | 0 | 0.13921 | 0.91183 | 0 | 0 | 1 | 0 | 0.13921 | 1
5183 | 0 | 0.1472 | 0.91183 | 0 | 0 | 1 | 0 | 0.1472 | 1
5184 | 0 | 0.14611 | 0.91183 | 0 | 0 | 1 | 0 | 0.14611 | 1
5185 | 0 | 0.14552 | 0.94371 | 0 | 0 | 1 | 0 | 0.14552 | 1
5186 | 0 | 0.13473 | 0.94371 | 0 | 0 | 1 | 0 | 0.13473 | 1
5187 | 0 | 0.098714 | 0.94371 | 0 | 0 | 1 | 0 | 0.098714 | 1
5188 | 0 | 0.072962 | 0.94371 | 0 | 0 | 1 | 0 | 0.072962 | 1
5189 | 0 | 0.036865 | 0.94371 | 0 | 0 | 1 | 0 | 0.036865 | 1
5190 | 0 | 0.044731 | 0.94371 | 0 | 0 | 1 | 0 | 0.044731 | 1
5191 | 0 | 0.079338 | 0.94371 | 0 | 0 | 1 | 0 | 0.079338 | 1
5192 | 0 | 0.079343 | 0.94371 | 0 | 0 | 1 | 0 | 0.079343 | 1
5193 | 0.057378 | 0.12928 | 0.94371 | 0 | 0 | 1 | 0.057378 | 0.12928 | 1
5194 | 0.19991 | 0.14511 | 0.94371 | 0 | 0 | 1 | 0.19991 | 0.14511 | 1
5195 | 0.25765 | 0.19142 | 0.94371 | 0 | 0 | 1 | 0.25765 | 0.19142 | 1
5196 | 0.3477 | 0.2272 | 0.94371 | 0 | 0 | 1 | 0.3477 | 0.2272 | 1
5197 | 0.37396 | 0.24434 | 0.94371 | 0 | 0 | 1 | 0.37396 | 0.24434 | 1
5198 | 0.36772 | 0.24269 | 0.94371 | 0 | 0 | 1 | 0.36772 | 0.24269 | 1
5199 | 0.32112 | 0.23357 | 0.94371 | 0 | 0 | 1 | 0.32112 | 0.23357 | 1
5200 | 0.22576 | 0.22508 | 0.94371 | 0 | 0 | 1 | 0.22576 | 0.22508 | 1
5201 | 0.084389 | 0.22574 | 0.94371 | 0 | 0 | 1 | 0.084389 | 0.22574 | 1
5202 | 0 | 0.18782 | 0.94371 | 0 | 1 | 1 | 0 | 0.18782 | 1
5203 | 0 | 0.14784 | 0.94371 | 0 | 1 | 1 | 0 | 0.14784 | 1
5204 | 0 | 0.13596 | 0.94371 | 0 | 1 | 1 | 0 | 0.13596 | 1
5205 | 0 | 0.14268 | 0.94371 | 0 | 1 | 1 | 0 | 0.14268 | 1
5206 | 0 | 0.11125 | 0.94371 | 0 | 0 | 1 | 0 | 0.11125 | 1
5207 | 0 | 0.11244 | 0.94371 | 0 | 0 | 1 | 0 | 0.11244 | 1
5208 | 0 | 0.11885 | 0.94371 | 0 | 0 | 1 | 0 | 0.11885 | 1
5209 | 0 | 0.1566 | 0.94371 | 0 | 0 | 1 | 0 | 0.1566 | 1
5210 | 0 | 0.10626 | 0.94371 | 0 | 0 | 1 | 0 | 0.10626 | 1
5211 | 0 | 0.087659 | 0.94371 | 0 | 0 | 1 | 0 | 0.087659 | 1
5212 | 0 | 0.066543 | 0.94371 | 0 | 0 | 1 | 0 | 0.066543 | 1
5213 | 0 | 0.032142 | 0.94371 | 0 | 0 | 1 | 0 | 0.032142 | 1
5214 | 0 | 0.046796 | 0.94371 | 0 | 0 | 1 | 0 | 0.046796 | 1
5215 | 0 | 0.067653 | 0.94371 | 0 | 0 | 1 | 0 | 0.067653 | 1
5216 | 0 | 0.056533 | 0.94371 | 0 | 0 | 1 | 0 | 0.056533 | 1
5217 | 0.067594 | 0.11596 | 0.94371 | 0 | 0 | 1 | 0.067594 | 0.11596 | 1
5218 | 0.2115 | 0.13423 | 0.94371 | 0 | 0 | 1 | 0.2115 | 0.13423 | 1
5219 | 0.28914 | 0.15934 | 0.94371 | 0 | 0 | 1 | 0.28914 | 0.15934 | 1
5220 | 0.36909 | 0.18081 | 0.94371 | 0 | 0 | 1 | 0.36909 | 0.18081 | 1
5221 | 0.44176 | 0.17714 | 0.94371 | 0 | 0 | 1 | 0.44176 | 0.17714 | 1
5222 | 0.47788 | 0.17266 | 0.94371 | 0 | 0 | 1 | 0.47788 | 0.17266 | 1
5223 | 0.43698 | 0.17688 | 0.94371 | 0 | 0 | 1 | 0.43698 | 0.17688 | 1
5224 | 0.27531 | 0.17212 | 0.94371 | 0 | 0 | 1 | 0.27531 | 0.17212 | 1
5225 | 0.084616 | 0.17983 | 0.94371 | 0 | 0 | 1 | 0.084616 | 0.17983 | 1
5226 | 0 | 0.15581 | 0.94371 | 0 | 1 | 1 | 0 | 0.15581 | 1
5227 | 0 | 0.12684 | 0.94371 | 0 | 1 | 1 | 0 | 0.12684 | 1
5228 | 0 | 0.090927 | 0.94371 | 0 | 1 | 1 | 0 | 0.090927 | 1
5229 | 0 | 0.098788 | 0.94371 | 0 | 1 | 1 | 0 | 0.098788 | 1
5230 | 0 | 0.070731 | 0.94371 | 0 | 0 | 1 | 0 | 0.070731 | 1
5231 | 0 | 0.070199 | 0.94371 | 0 | 0 | 1 | 0 | 0.070199 | 1
5232 | 0 | 0.066532 | 0.94371 | 0 | 0 | 1 | 0 | 0.066532 | 1
5233 | 0 | 0.12735 | 0.94371 | 0 | 0 | 1 | 0 | 0.12735 | 1
5234 | 0 | 0.078275 | 0.94371 | 0 | 0 | 1 | 0 | 0.078275 | 1
5235 | 0 | 0.062055 | 0.94371 | 0 | 0 | 1 | 0 | 0.062055 | 1
5236 | 0 | 0.03545 | 0.94371 | 0 | 0 | 1 | 0 | 0.03545 | 1
5237 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
5238 | 0 | 0.018617 | 0.94371 | 0 | 0 | 1 | 0 | 0.018617 | 1
5239 | 0 | 0.051791 | 0.94371 | 0 | 0 | 1 | 0 | 0.051791 | 1
5240 | 0 | 0.044943 | 0.94371 | 0 | 0 | 1 | 0 | 0.044943 | 1
5241 | 0.051484 | 0.058235 | 0.94371 | 0 | 0 | 1 | 0.051484 | 0.058235 | 1
5242 | 0.17123 | 0.087439 | 0.94371 | 0 | 0 | 1 | 0.17123 | 0.087439 | 1
5243 | 0.26087 | 0.1124 | 0.94371 | 0 | 0 | 1 | 0.26087 | 0.1124 | 1
5244 | 0.37129 | 0.14239 | 0.94371 | 0 | 0 | 1 | 0.37129 | 0.14239 | 1
5245 | 0.4438 | 0.14559 | 0.94371 | 0 | 0 | 1 | 0.4438 | 0.14559 | 1
5246 | 0.4732 | 0.14185 | 0.94371 | 0 | 0 | 1 | 0.4732 | 0.14185 | 1
5247 | 0.44178 | 0.16173 | 0.94371 | 0 | 0 | 1 | 0.44178 | 0.16173 | 1
5248 | 0.26988 | 0.16434 | 0.94371 | 0 | 0 | 1 | 0.26988 | 0.16434 | 1
5249 | 0.087669 | 0.15849 | 0.94371 | 0 | 0 | 1 | 0.087669 | 0.15849 | 1
5250 | 0 | 0.13751 | 0.94371 | 0 | 1 | 1 | 0 | 0.13751 | 1
5251 | 0 | 0.15636 | 0.94371 | 0 | 1 | 1 | 0 | 0.15636 | 1
5252 | 0 | 0.080071 | 0.94371 | 0 | 1 | 1 | 0 | 0.080071 | 1
5253 | 0 | 0.090979 | 0.94371 | 0 | 1 | 1 | 0 | 0.090979 | 1
5254 | 0 | 0.088734 | 0.94371 | 0 | 0 | 1 | 0 | 0.088734 | 1
5255 | 0 | 0.076821 | 0.94371 | 0 | 0 | 1 | 0 | 0.076821 | 1
5256 | 0 | 0.062714 | 0.94371 | 0 | 0 | 1 | 0 | 0.062714 | 1
5257 | 0 | 0.081765 | 0.94371 | 0 | 0 | 1 | 0 | 0.081765 | 1
5258 | 0 | 0.062212 | 0.94371 | 0 | 0 | 1 | 0 | 0.062212 | 1
5259 | 0 | 0.064345 | 0.94371 | 0 | 0 | 1 | 0 | 0.064345 | 1
5260 | 0 | 0.053002 | 0.94371 | 0 | 0 | 1 | 0 | 0.053002 | 1
5261 | 0 | 0.025982 | 0.94371 | 0 | 0 | 1 | 0 | 0.025982 | 1
5262 | 0 | 0.038685 | 0.94371 | 0 | 0 | 1 | 0 | 0.038685 | 1
5263 | 0 | 0.053602 | 0.94371 | 0 | 0 | 1 | 0 | 0.053602 | 1
5264 | 0 | 0.035463 | 0.94371 | 0 | 0 | 1 | 0 | 0.035463 | 1
5265 | 0.014039 | 0.031807 | 0.94371 | 0 | 0 | 1 | 0.014039 | 0.031807 | 1
5266 | 0.13563 | 0.052196 | 0.94371 | 0 | 0 | 1 | 0.13563 | 0.052196 | 1
5267 | 0.22799 | 0.09407 | 0.94371 | 0 | 0 | 1 | 0.22799 | 0.09407 | 1
5268 | 0.31864 | 0.11488 | 0.94371 | 0 | 0 | 1 | 0.31864 | 0.11488 | 1
5269 | 0.3912 | 0.12514 | 0.94371 | 0 | 0 | 1 | 0.3912 | 0.12514 | 1
5270 | 0.39754 | 0.12522 | 0.94371 | 0 | 0 | 1 | 0.39754 | 0.12522 | 1
5271 | 0.37281 | 0.15147 | 0.94371 | 0 | 0 | 1 | 0.37281 | 0.15147 | 1
5272 | 0.23371 | 0.15666 | 0.94371 | 0 | 0 | 1 | 0.23371 | 0.15666 | 1
5273 | 0.039972 | 0.14699 | 0.94371 | 0 | 0 | 1 | 0.039972 | 0.14699 | 1
5274 | 0 | 0.1218 | 0.94371 | 0 | 1 | 1 | 0 | 0.1218 | 1
5275 | 0 | 0.16179 | 0.94371 | 0 | 1 | 1 | 0 | 0.16179 | 1
5276 | 0 | 0.11692 | 0.94371 | 0 | 1 | 1 | 0 | 0.11692 | 1
5277 | 0 | 0.13398 | 0.94371 | 0 | 1 | 1 | 0 | 0.13398 | 1
5278 | 0 | 0.14944 | 0.94371 | 0 | 0 | 1 | 0 | 0.14944 | 1
5279 | 0 | 0.1356 | 0.94371 | 0 | 0 | 1 | 0 | 0.1356 | 1
5280 | 0 | 0.1011 | 0.94371 | 0 | 0 | 1 | 0 | 0.1011 | 1
5281 | 0 | 0.059048 | 1 | 0 | 0 | 1 | 0 | 0.059048 | 1
5282 | 0 | 0.068071 | 1 | 0 | 0 | 1 | 0 | 0.068071 | 1
5283 | 0 | 0.075203 | 1 | 0 | 0 | 1 | 0 | 0.075203 | 1
5284 | 0 | 0.059261 | 1 | 0 | 0 | 1 | 0 | 0.059261 | 1
5285 | 0 | 0.043242 | 1 | 0 | 0 | 1 | 0 | 0.043242 | 1
5286 | 0 | 0.048237 | 1 | 0 | 0 | 1 | 0 | 0.048237 | 1
5287 | 0 | 0.076536 | 1 | 0 | 0 | 1 | 0 | 0.076536 | 1
5288 | 0 | 0.068017 | 1 | 0 | 0 | 1 | 0 | 0.068017 | 1
5289 | 0.017173 | 0.068263 | 1 | 0 | 0 | 1 | 0.017173 | 0.068263 | 1
5290 | 0.14819 | 0.068212 | 1 | 0 | 0 | 1 | 0.14819 | 0.068212 | 1
5291 | 0.25221 | 0.10009 | 1 | 0 | 0 | 1 | 0.25221 | 0.10009 | 1
5292 | 0.33741 | 0.11936 | 1 | 0 | 0 | 1 | 0.33741 | 0.11936 | 1
5293 | 0.41358 | 0.13415 | 1 | 0 | 0 | 1 | 0.41358 | 0.13415 | 1
5294 | 0.38245 | 0.13087 | 1 | 0 | 0 | 1 | 0.38245 | 0.13087 | 1
5295 | 0.34792 | 0.14911 | 1 | 0 | 0 | 1 | 0.34792 | 0.14911 | 1
5296 | 0.19568 | 0.16048 | 1 | 0 | 0 | 1 | 0.19568 | 0.16048 | 1
5297 | 0.05114 | 0.14431 | 1 | 0 | 0 | 1 | 0.05114 | 0.14431 | 1
5298 | 0 | 0.1056 | 1 | 0 | 1 | 1 | 0 | 0.1056 | 1
5299 | 0 | 0.11066 | 1 | 0 | 1 | 1 | 0 | 0.11066 | 1
5300 | 0 | 0.11367 | 1 | 0 | 1 | 1 | 0 | 0.11367 | 1
5301 | 0 | 0.12358 | 1 | 0 | 1 | 1 | 0 | 0.12358 | 1
5302 | 0 | 0.13963 | 1 | 0 | 0 | 1 | 0 | 0.13963 | 1
5303 | 0 | 0.1419 | 1 | 0 | 0 | 1 | 0 | 0.1419 | 1
5304 | 0 | 0.10757 | 1 | 0 | 0 | 1 | 0 | 0.10757 | 1
5305 | 0 | 0.063905 | 1 | 0 | 0 | 1 | 0 | 0.063905 | 1
5306 | 0 | 0.068149 | 1 | 0 | 0 | 1 | 0 | 0.068149 | 1
5307 | 0 | 0.063288 | 1 | 0 | 0 | 1 | 0 | 0.063288 | 1
5308 | 0 | 0.045005 | 1 | 0 | 0 | 1 | 0 | 0.045005 | 1
5309 | 0 | 0.030211 | 1 | 0 | 0 | 1 | 0 | 0.030211 | 1
5310 | 0 | 0.024488 | 1 | 0 | 0 | 1 | 0 | 0.024488 | 1
5311 | 0 | 0.046185 | 1 | 0 | 0 | 1 | 0 | 0.046185 | 1
5312 | 0 | 0.033796 | 1 | 0 | 0 | 1 | 0 | 0.033796 | 1
5313 | 0.046904 | 0.050579 | 1 | 0 | 0 | 1 | 0.046904 | 0.050579 | 1
5314 | 0.20595 | 0.06147 | 1 | 0 | 0 | 1 | 0.20595 | 0.06147 | 1
5315 | 0.27208 | 0.074597 | 1 | 0 | 0 | 1 | 0.27208 | 0.074597 | 1
5316 | 0.35491 | 0.098662 | 1 | 0 | 0 | 1 | 0.35491 | 0.098662 | 1
5317 | 0.3946 | 0.1161 | 1 | 0 | 0 | 1 | 0.3946 | 0.1161 | 1
5318 | 0.3538 | 0.11323 | 1 | 0 | 0 | 1 | 0.3538 | 0.11323 | 1
5319 | 0.31886 | 0.12152 | 1 | 0 | 0 | 1 | 0.31886 | 0.12152 | 1
5320 | 0.14372 | 0.11251 | 1 | 0 | 0 | 1 | 0.14372 | 0.11251 | 1
5321 | 0 | 0.11876 | 1 | 0 | 0 | 1 | 0 | 0.11876 | 1
5322 | 0 | 0.093163 | 1 | 0 | 1 | 1 | 0 | 0.093163 | 1
5323 | 0 | 0.092414 | 1 | 0 | 1 | 1 | 0 | 0.092414 | 1
5324 | 0 | 0.10898 | 1 | 0 | 1 | 1 | 0 | 0.10898 | 1
5325 | 0 | 0.11655 | 1 | 0 | 1 | 1 | 0 | 0.11655 | 1
5326 | 0 | 0.10815 | 1 | 0 | 0 | 1 | 0 | 0.10815 | 1
5327 | 0 | 0.10189 | 1 | 0 | 0 | 1 | 0 | 0.10189 | 1
5328 | 0 | 0.085366 | 1 | 0 | 0 | 1 | 0 | 0.085366 | 1
5329 | 0 | 0.065142 | 1 | 0 | 0 | 1 | 0 | 0.065142 | 1
5330 | 0 | 0.054653 | 1 | 0 | 0 | 1 | 0 | 0.054653 | 1
5331 | 0 | 0.049868 | 1 | 0 | 0 | 1 | 0 | 0.049868 | 1
5332 | 0 | 0.027125 | 1 | 0 | 0 | 1 | 0 | 0.027125 | 1
5333 | 0 | 0.026258 | 1 | 0 | 0 | 1 | 0 | 0.026258 | 1
5334 | 0 | 0.017261 | 1 | 0 | 0 | 1 | 0 | 0.017261 | 1
5335 | 0 | 0.045436 | 1 | 0 | 0 | 1 | 0 | 0.045436 | 1
5336 | 0 | 0.03696 | 1 | 0 | 0 | 1 | 0 | 0.03696 | 1
5337 | 0.071207 | 0.060039 | 1 | 0 | 0 | 1 | 0.071207 | 0.060039 | 1
5338 | 0.24074 | 0.077515 | 1 | 0 | 0 | 1 | 0.24074 | 0.077515 | 1
5339 | 0.28888 | 0.081984 | 1 | 0 | 0 | 1 | 0.28888 | 0.081984 | 1
5340 | 0.33494 | 0.1049 | 1 | 0 | 0 | 1 | 0.33494 | 0.1049 | 1
5341 | 0.38039 | 0.12147 | 1 | 0 | 0 | 1 | 0.38039 | 0.12147 | 1
5342 | 0.36794 | 0.12963 | 1 | 0 | 0 | 1 | 0.36794 | 0.12963 | 1
5343 | 0.33166 | 0.1263 | 1 | 0 | 0 | 1 | 0.33166 | 0.1263 | 1
5344 | 0.11726 | 0.12374 | 1 | 0 | 0 | 1 | 0.11726 | 0.12374 | 1
5345 | 0.0048847 | 0.13797 | 1 | 0 | 0 | 1 | 0.0048847 | 0.13797 | 1
5346 | 0 | 0.11469 | 1 | 0 | 1 | 1 | 0 | 0.11469 | 1
5347 | 0 | 0.08658 | 1 | 0 | 1 | 1 | 0 | 0.08658 | 1
5348 | 0 | 0.085094 | 1 | 0 | 1 | 1 | 0 | 0.085094 | 1
5349 | 0 | 0.077791 | 1 | 0 | 1 | 1 | 0 | 0.077791 | 1
5350 | 0 | 0.06884 | 1 | 0 | 0 | 1 | 0 | 0.06884 | 1
5351 | 0 | 0.072469 | 1 | 0 | 0 | 1 | 0 | 0.072469 | 1
5352 | 0 | 0.073025 | 1 | 0 | 0 | 1 | 0 | 0.073025 | 1
5353 | 0 | 0.0631 | 0.94301 | 0 | 0 | 1 | 0 | 0.0631 | 1
5354 | 0 | 0.064254 | 0.94301 | 0 | 0 | 1 | 0 | 0.064254 | 1
5355 | 0 | 0.05003 | 0.94301 | 0 | 0 | 1 | 0 | 0.05003 | 1
5356 | 0 | 0.024192 | 0.94301 | 0 | 0 | 1 | 0 | 0.024192 | 1
5357 | 0 | 0.023264 | 0.94301 | 0 | 0 | 1 | 0 | 0.023264 | 1
5358 | 0 | 0.013733 | 0.94301 | 0 | 0 | 1 | 0 | 0.013733 | 1
5359 | 0 | 0.0313 | 0.94301 | 0 | 0 | 1 | 0 | 0.0313 | 1
5360 | 0 | 0.041337 | 0.94301 | 0 | 0 | 1 | 0 | 0.041337 | 1
5361 | 0.089825 | 0.072224 | 0.94301 | 0 | 0 | 1 | 0.089825 | 0.072224 | 1
5362 | 0.23065 | 0.12657 | 0.94301 | 0 | 0 | 1 | 0.23065 | 0.12657 | 1
5363 | 0.28672 | 0.12901 | 0.94301 | 0 | 0 | 1 | 0.28672 | 0.12901 | 1
5364 | 0.32447 | 0.16469 | 0.94301 | 0 | 0 | 1 | 0.32447 | 0.16469 | 1
5365 | 0.31153 | 0.18318 | 0.94301 | 0 | 0 | 1 | 0.31153 | 0.18318 | 1
5366 | 0.36132 | 0.18933 | 0.94301 | 0 | 0 | 1 | 0.36132 | 0.18933 | 1
5367 | 0.29777 | 0.17578 | 0.94301 | 0 | 0 | 1 | 0.29777 | 0.17578 | 1
5368 | 0.12922 | 0.17804 | 0.94301 | 0 | 0 | 1 | 0.12922 | 0.17804 | 1
5369 | 0.023069 | 0.1947 | 0.94301 | 0 | 0 | 1 | 0.023069 | 0.1947 | 1
5370 | 0 | 0.16652 | 0.94301 | 0 | 1 | 1 | 0 | 0.16652 | 1
5371 | 0 | 0.15269 | 0.94301 | 0 | 1 | 1 | 0 | 0.15269 | 1
5372 | 0 | 0.12581 | 0.94301 | 0 | 1 | 1 | 0 | 0.12581 | 1
5373 | 0 | 0.12755 | 0.94301 | 0 | 1 | 1 | 0 | 0.12755 | 1
5374 | 0 | 0.10092 | 0.94301 | 0 | 0 | 1 | 0 | 0.10092 | 1
5375 | 0 | 0.10074 | 0.94301 | 0 | 0 | 1 | 0 | 0.10074 | 1
5376 | 0 | 0.10102 | 0.94301 | 0 | 0 | 1 | 0 | 0.10102 | 1
5377 | 0 | 0.078018 | 0.94301 | 0 | 0 | 1 | 0 | 0.078018 | 1
5378 | 0 | 0.079133 | 0.94301 | 0 | 0 | 1 | 0 | 0.079133 | 1
5379 | 0 | 0.069668 | 0.94301 | 0 | 0 | 1 | 0 | 0.069668 | 1
5380 | 0 | 0.065372 | 0.94301 | 0 | 0 | 1 | 0 | 0.065372 | 1
5381 | 0 | 0.075759 | 0.94301 | 0 | 0 | 1 | 0 | 0.075759 | 1
5382 | 0 | 0.059708 | 0.94301 | 0 | 0 | 1 | 0 | 0.059708 | 1
5383 | 0 | 0.08114 | 0.94301 | 0 | 0 | 1 | 0 | 0.08114 | 1
5384 | 0 | 0.09579 | 0.94301 | 0 | 0 | 1 | 0 | 0.09579 | 1
5385 | 0.09781 | 0.10228 | 0.94301 | 0 | 0 | 1 | 0.09781 | 0.10228 | 1
5386 | 0.19183 | 0.16185 | 0.94301 | 0 | 0 | 1 | 0.19183 | 0.16185 | 1
5387 | 0.27131 | 0.18749 | 0.94301 | 0 | 0 | 1 | 0.27131 | 0.18749 | 1
5388 | 0.28782 | 0.22348 | 0.94301 | 0 | 0 | 1 | 0.28782 | 0.22348 | 1
5389 | 0.29795 | 0.21898 | 0.94301 | 0 | 0 | 1 | 0.29795 | 0.21898 | 1
5390 | 0.33733 | 0.23028 | 0.94301 | 0 | 0 | 1 | 0.33733 | 0.23028 | 1
5391 | 0.28929 | 0.21196 | 0.94301 | 0 | 0 | 1 | 0.28929 | 0.21196 | 1
5392 | 0.16503 | 0.22425 | 0.94301 | 0 | 0 | 1 | 0.16503 | 0.22425 | 1
5393 | 0.092326 | 0.21973 | 0.94301 | 0 | 0 | 1 | 0.092326 | 0.21973 | 1
5394 | 0 | 0.17185 | 0.94301 | 0 | 1 | 1 | 0 | 0.17185 | 1
5395 | 0 | 0.14615 | 0.94301 | 0 | 1 | 1 | 0 | 0.14615 | 1
5396 | 0 | 0.1211 | 0.94301 | 0 | 1 | 1 | 0 | 0.1211 | 1
5397 | 0 | 0.10939 | 0.94301 | 0 | 1 | 1 | 0 | 0.10939 | 1
5398 | 0 | 0.09526 | 0.94301 | 0 | 0 | 1 | 0 | 0.09526 | 1
5399 | 0 | 0.095912 | 0.94301 | 0 | 0 | 1 | 0 | 0.095912 | 1
5400 | 0 | 0.07414 | 0.94301 | 0 | 0 | 1 | 0 | 0.07414 | 1
5401 | 0 | 0.096246 | 0.94301 | 0 | 0 | 1 | 0 | 0.096246 | 1
5402 | 0 | 0.072488 | 0.94301 | 0 | 0 | 1 | 0 | 0.072488 | 1
5403 | 0 | 0.065997 | 0.94301 | 0 | 0 | 1 | 0 | 0.065997 | 1
5404 | 0 | 0.071618 | 0.94301 | 0 | 0 | 1 | 0 | 0.071618 | 1
5405 | 0 | 0.086263 | 0.94301 | 0 | 0 | 1 | 0 | 0.086263 | 1
5406 | 0 | 0.061602 | 0.94301 | 0 | 0 | 1 | 0 | 0.061602 | 1
5407 | 0 | 0.082302 | 0.94301 | 0 | 0 | 1 | 0 | 0.082302 | 1
5408 | 0 | 0.10303 | 0.94301 | 0 | 0 | 1 | 0 | 0.10303 | 1
5409 | 0.1538 | 0.11334 | 0.94301 | 0 | 0 | 1 | 0.1538 | 0.11334 | 1
5410 | 0.23919 | 0.17463 | 0.94301 | 0 | 0 | 1 | 0.23919 | 0.17463 | 1
5411 | 0.29469 | 0.21346 | 0.94301 | 0 | 0 | 1 | 0.29469 | 0.21346 | 1
5412 | 0.3249 | 0.26641 | 0.94301 | 0 | 0 | 1 | 0.3249 | 0.26641 | 1
5413 | 0.34765 | 0.24935 | 0.94301 | 0 | 0 | 1 | 0.34765 | 0.24935 | 1
5414 | 0.38971 | 0.25639 | 0.94301 | 0 | 0 | 1 | 0.38971 | 0.25639 | 1
5415 | 0.32261 | 0.23615 | 0.94301 | 0 | 0 | 1 | 0.32261 | 0.23615 | 1
5416 | 0.20919 | 0.25229 | 0.94301 | 0 | 0 | 1 | 0.20919 | 0.25229 | 1
5417 | 0.1006 | 0.2398 | 0.94301 | 0 | 0 | 1 | 0.1006 | 0.2398 | 1
5418 | 0 | 0.16971 | 0.94301 | 0 | 1 | 1 | 0 | 0.16971 | 1
5419 | 0 | 0.16237 | 0.94301 | 0 | 1 | 1 | 0 | 0.16237 | 1
5420 | 0 | 0.16162 | 0.94301 | 0 | 1 | 1 | 0 | 0.16162 | 1
5421 | 0 | 0.15215 | 0.94301 | 0 | 1 | 1 | 0 | 0.15215 | 1
5422 | 0 | 0.13229 | 0.94301 | 0 | 0 | 1 | 0 | 0.13229 | 1
5423 | 0 | 0.11829 | 0.94301 | 0 | 0 | 1 | 0 | 0.11829 | 1
5424 | 0 | 0.077873 | 0.94301 | 0 | 0 | 1 | 0 | 0.077873 | 1
5425 | 0 | 0.062097 | 0.94301 | 0 | 0 | 1 | 0 | 0.062097 | 1
5426 | 0 | 0.066541 | 0.94301 | 0 | 0 | 1 | 0 | 0.066541 | 1
5427 | 0 | 0.054755 | 0.94301 | 0 | 0 | 1 | 0 | 0.054755 | 1
5428 | 0 | 0.060809 | 0.94301 | 0 | 0 | 1 | 0 | 0.060809 | 1
5429 | 0 | 0.071975 | 0.94301 | 0 | 0 | 1 | 0 | 0.071975 | 1
5430 | 0 | 0.058827 | 0.94301 | 0 | 0 | 1 | 0 | 0.058827 | 1
5431 | 0 | 0.065635 | 0.94301 | 0 | 0 | 1 | 0 | 0.065635 | 1
5432 | 0 | 0.071146 | 0.94301 | 0 | 0 | 1 | 0 | 0.071146 | 1
5433 | 0.15831 | 0.084461 | 0.94301 | 0 | 0 | 1 | 0.15831 | 0.084461 | 1
5434 | 0.2617 | 0.12148 | 0.94301 | 0 | 0 | 1 | 0.2617 | 0.12148 | 1
5435 | 0.2608 | 0.16785 | 0.94301 | 0 | 0 | 1 | 0.2608 | 0.16785 | 1
5436 | 0.27779 | 0.20681 | 0.94301 | 0 | 0 | 1 | 0.27779 | 0.20681 | 1
5437 | 0.34062 | 0.19601 | 0.94301 | 0 | 0 | 1 | 0.34062 | 0.19601 | 1
5438 | 0.37037 | 0.21631 | 0.94301 | 0 | 0 | 1 | 0.37037 | 0.21631 | 1
5439 | 0.3068 | 0.20142 | 0.94301 | 0 | 0 | 1 | 0.3068 | 0.20142 | 1
5440 | 0.16817 | 0.2065 | 0.94301 | 0 | 0 | 1 | 0.16817 | 0.2065 | 1
5441 | 0.053118 | 0.19096 | 0.94301 | 0 | 0 | 1 | 0.053118 | 0.19096 | 1
5442 | 0 | 0.11892 | 0.94301 | 0 | 1 | 1 | 0 | 0.11892 | 1
5443 | 0 | 0.11822 | 0.94301 | 0 | 1 | 1 | 0 | 0.11822 | 1
5444 | 0 | 0.12039 | 0.94301 | 0 | 1 | 1 | 0 | 0.12039 | 1
5445 | 0 | 0.10663 | 0.94301 | 0 | 1 | 1 | 0 | 0.10663 | 1
5446 | 0 | 0.097638 | 0.94301 | 0 | 0 | 1 | 0 | 0.097638 | 1
5447 | 0 | 0.065668 | 0.94301 | 0 | 0 | 1 | 0 | 0.065668 | 1
5448 | 0 | 0.026502 | 0.94301 | 0 | 0 | 1 | 0 | 0.026502 | 1
5449 | 0 | 0.068945 | 0.94301 | 0 | 0 | 1 | 0 | 0.068945 | 1
5450 | 0 | 0.025709 | 0.94301 | 0 | 0 | 1 | 0 | 0.025709 | 1
5451 | 0 | 0.020262 | 0.94301 | 0 | 0 | 1 | 0 | 0.020262 | 1
5452 | 0 | 0.018028 | 0.94301 | 0 | 0 | 1 | 0 | 0.018028 | 1
5453 | 0 | 0.021486 | 0.94301 | 0 | 0 | 1 | 0 | 0.021486 | 1
5454 | 0 | 0.002759 | 0.94301 | 0 | 0 | 1 | 0 | 0.002759 | 1
5455 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5456 | 0 | 0.018835 | 0.94301 | 0 | 0 | 1 | 0 | 0.018835 | 1
5457 | 0.11051 | 0.060151 | 0.94301 | 0 | 0 | 1 | 0.11051 | 0.060151 | 1
5458 | 0.24507 | 0.099478 | 0.94301 | 0 | 0 | 1 | 0.24507 | 0.099478 | 1
5459 | 0.2777 | 0.13183 | 0.94301 | 0 | 0 | 1 | 0.2777 | 0.13183 | 1
5460 | 0.26334 | 0.16399 | 0.94301 | 0 | 0 | 1 | 0.26334 | 0.16399 | 1
5461 | 0.36967 | 0.14734 | 0.94301 | 0 | 0 | 1 | 0.36967 | 0.14734 | 1
5462 | 0.39572 | 0.17087 | 0.94301 | 0 | 0 | 1 | 0.39572 | 0.17087 | 1
5463 | 0.30239 | 0.17197 | 0.94301 | 0 | 0 | 1 | 0.30239 | 0.17197 | 1
5464 | 0.18127 | 0.19973 | 0.94301 | 0 | 0 | 1 | 0.18127 | 0.19973 | 1
5465 | 0.06713 | 0.18977 | 0.94301 | 0 | 0 | 1 | 0.06713 | 0.18977 | 1
5466 | 0 | 0.13814 | 0.94301 | 0 | 1 | 1 | 0 | 0.13814 | 1
5467 | 0 | 0.13882 | 0.94301 | 0 | 1 | 1 | 0 | 0.13882 | 1
5468 | 0 | 0.12369 | 0.94301 | 0 | 1 | 1 | 0 | 0.12369 | 1
5469 | 0 | 0.1136 | 0.94301 | 0 | 1 | 1 | 0 | 0.1136 | 1
5470 | 0 | 0.097637 | 0.94301 | 0 | 0 | 1 | 0 | 0.097637 | 1
5471 | 0 | 0.066016 | 0.94301 | 0 | 0 | 1 | 0 | 0.066016 | 1
5472 | 0 | 0.033158 | 0.94301 | 0 | 0 | 1 | 0 | 0.033158 | 1
5473 | 0 | 0.019037 | 0.94301 | 0 | 0 | 1 | 0 | 0.019037 | 1
5474 | 0 | 0.020064 | 0.94301 | 0 | 0 | 1 | 0 | 0.020064 | 1
5475 | 0 | 0.013387 | 0.94301 | 0 | 0 | 1 | 0 | 0.013387 | 1
5476 | 0 | 0.0052234 | 0.94301 | 0 | 0 | 1 | 0 | 0.0052234 | 1
5477 | 0 | 0.0091413 | 0.94301 | 0 | 0 | 1 | 0 | 0.0091413 | 1
5478 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5479 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5480 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5481 | 0.084121 | 0.023599 | 0.94301 | 0 | 0 | 1 | 0.084121 | 0.023599 | 1
5482 | 0.22771 | 0.057458 | 0.94301 | 0 | 0 | 1 | 0.22771 | 0.057458 | 1
5483 | 0.33049 | 0.078152 | 0.94301 | 0 | 0 | 1 | 0.33049 | 0.078152 | 1
5484 | 0.3011 | 0.10293 | 0.94301 | 0 | 0 | 1 | 0.3011 | 0.10293 | 1
5485 | 0.35344 | 0.08911 | 0.94301 | 0 | 0 | 1 | 0.35344 | 0.08911 | 1
5486 | 0.37173 | 0.10767 | 0.94301 | 0 | 0 | 1 | 0.37173 | 0.10767 | 1
5487 | 0.27389 | 0.10572 | 0.94301 | 0 | 0 | 1 | 0.27389 | 0.10572 | 1
5488 | 0.14946 | 0.12718 | 0.94301 | 0 | 0 | 1 | 0.14946 | 0.12718 | 1
5489 | 0.044162 | 0.13814 | 0.94301 | 0 | 0 | 1 | 0.044162 | 0.13814 | 1
5490 | 0 | 0.10285 | 0.94301 | 0 | 1 | 1 | 0 | 0.10285 | 1
5491 | 0 | 0.093046 | 0.94301 | 0 | 1 | 1 | 0 | 0.093046 | 1
5492 | 0 | 0.058012 | 0.94301 | 0 | 1 | 1 | 0 | 0.058012 | 1
5493 | 0 | 0.059676 | 0.94301 | 0 | 1 | 1 | 0 | 0.059676 | 1
5494 | 0 | 0.037658 | 0.94301 | 0 | 0 | 1 | 0 | 0.037658 | 1
5495 | 0 | 0.020606 | 0.94301 | 0 | 0 | 1 | 0 | 0.020606 | 1
5496 | 0 | 0.015492 | 0.94301 | 0 | 0 | 1 | 0 | 0.015492 | 1
5497 | 0 | 0.031612 | 0.94301 | 0 | 0 | 1 | 0 | 0.031612 | 1
5498 | 0 | 0.014228 | 0.94301 | 0 | 0 | 1 | 0 | 0.014228 | 1
5499 | 0 | 0.0098434 | 0.94301 | 0 | 0 | 1 | 0 | 0.0098434 | 1
5500 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5501 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5502 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5503 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5504 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5505 | 0.096583 | 0.011766 | 0.94301 | 0 | 0 | 1 | 0.096583 | 0.011766 | 1
5506 | 0.22934 | 0.048123 | 0.94301 | 0 | 0 | 1 | 0.22934 | 0.048123 | 1
5507 | 0.39746 | 0.077364 | 0.94301 | 0 | 0 | 1 | 0.39746 | 0.077364 | 1
5508 | 0.31204 | 0.10067 | 0.94301 | 0 | 0 | 1 | 0.31204 | 0.10067 | 1
5509 | 0.4046 | 0.10712 | 0.94301 | 0 | 0 | 1 | 0.4046 | 0.10712 | 1
5510 | 0.35222 | 0.11006 | 0.94301 | 0 | 0 | 1 | 0.35222 | 0.11006 | 1
5511 | 0.27702 | 0.10532 | 0.94301 | 0 | 0 | 1 | 0.27702 | 0.10532 | 1
5512 | 0.1934 | 0.12464 | 0.94301 | 0 | 0 | 1 | 0.1934 | 0.12464 | 1
5513 | 0.053928 | 0.11638 | 0.94301 | 0 | 0 | 1 | 0.053928 | 0.11638 | 1
5514 | 0 | 0.090942 | 0.94301 | 0 | 1 | 1 | 0 | 0.090942 | 1
5515 | 0 | 0.064148 | 0.94301 | 0 | 1 | 1 | 0 | 0.064148 | 1
5516 | 0 | 0.022065 | 0.94301 | 0 | 1 | 1 | 0 | 0.022065 | 1
5517 | 0 | 0.027793 | 0.94301 | 0 | 1 | 1 | 0 | 0.027793 | 1
5518 | 0 | 0.0032312 | 0.94301 | 0 | 0 | 1 | 0 | 0.0032312 | 1
5519 | 0 | 0.010275 | 0.94301 | 0 | 0 | 1 | 0 | 0.010275 | 1
5520 | 0 | 0.0034813 | 0.94301 | 0 | 0 | 1 | 0 | 0.0034813 | 1
5521 | 0 | 0.014104 | 0.86762 | 0 | 0 | 1 | 0 | 0.014104 | 1
5522 | 0 | 0.008331 | 0.86762 | 0 | 0 | 1 | 0 | 0.008331 | 1
5523 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5524 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5525 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5526 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5527 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5528 | 0 | 0.00073429 | 0.86762 | 0 | 0 | 1 | 0 | 0.00073429 | 1
5529 | 0.11854 | 0.016651 | 0.86762 | 0 | 0 | 1 | 0.11854 | 0.016651 | 1
5530 | 0.25143 | 0.047761 | 0.86762 | 0 | 0 | 1 | 0.25143 | 0.047761 | 1
5531 | 0.37661 | 0.07015 | 0.86762 | 0 | 0 | 1 | 0.37661 | 0.07015 | 1
5532 | 0.35884 | 0.075441 | 0.86762 | 0 | 0 | 1 | 0.35884 | 0.075441 | 1
5533 | 0.39826 | 0.090297 | 0.86762 | 0 | 0 | 1 | 0.39826 | 0.090297 | 1
5534 | 0.36035 | 0.09652 | 0.86762 | 0 | 0 | 1 | 0.36035 | 0.09652 | 1
5535 | 0.29552 | 0.080856 | 0.86762 | 0 | 0 | 1 | 0.29552 | 0.080856 | 1
5536 | 0.17512 | 0.085757 | 0.86762 | 0 | 0 | 1 | 0.17512 | 0.085757 | 1
5537 | 0.010354 | 0.0925 | 0.86762 | 0 | 0 | 1 | 0.010354 | 0.0925 | 1
5538 | 0 | 0.061098 | 0.86762 | 0 | 1 | 1 | 0 | 0.061098 | 1
5539 | 0 | 0.042053 | 0.86762 | 0 | 1 | 1 | 0 | 0.042053 | 1
5540 | 0 | 0.0079282 | 0.86762 | 0 | 1 | 1 | 0 | 0.0079282 | 1
5541 | 0 | 0.015889 | 0.86762 | 0 | 1 | 1 | 0 | 0.015889 | 1
5542 | 0 | 0.00018213 | 0.86762 | 0 | 0 | 1 | 0 | 0.00018213 | 1
5543 | 0 | 0.011814 | 0.86762 | 0 | 0 | 1 | 0 | 0.011814 | 1
5544 | 0 | 0 | 0.86762 | 0 | 0 | 1 | 0 | 0 | 1
5545 | 0 | 0.0047219 | 0.94301 | 0 | 0 | 1 | 0 | 0.0047219 | 1
5546 | 0 | 0.01396 | 0.94301 | 0 | 0 | 1 | 0 | 0.01396 | 1
5547 | 0 | 0.00046786 | 0.94301 | 0 | 0 | 1 | 0 | 0.00046786 | 1
5548 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5549 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5550 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5551 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5552 | 0 | 0.018428 | 0.94301 | 0 | 0 | 1 | 0 | 0.018428 | 1
5553 | 0.11663 | 0.01111 | 0.94301 | 0 | 0 | 1 | 0.11663 | 0.01111 | 1
5554 | 0.1882 | 0.027894 | 0.94301 | 0 | 0 | 1 | 0.1882 | 0.027894 | 1
5555 | 0.21736 | 0.058275 | 0.94301 | 0 | 0 | 1 | 0.21736 | 0.058275 | 1
5556 | 0.29945 | 0.065423 | 0.94301 | 0 | 0 | 1 | 0.29945 | 0.065423 | 1
5557 | 0.32787 | 0.084108 | 0.94301 | 0 | 0 | 1 | 0.32787 | 0.084108 | 1
5558 | 0.32693 | 0.094929 | 0.94301 | 0 | 0 | 1 | 0.32693 | 0.094929 | 1
5559 | 0.31852 | 0.087181 | 0.94301 | 0 | 0 | 1 | 0.31852 | 0.087181 | 1
5560 | 0.18395 | 0.089628 | 0.94301 | 0 | 0 | 1 | 0.18395 | 0.089628 | 1
5561 | 0.0094506 | 0.087824 | 0.94301 | 0 | 0 | 1 | 0.0094506 | 0.087824 | 1
5562 | 0 | 0.063298 | 0.94301 | 0 | 1 | 1 | 0 | 0.063298 | 1
5563 | 0 | 0.046438 | 0.94301 | 0 | 1 | 1 | 0 | 0.046438 | 1
5564 | 0 | 0.015221 | 0.94301 | 0 | 1 | 1 | 0 | 0.015221 | 1
5565 | 0 | 0.025379 | 0.94301 | 0 | 1 | 1 | 0 | 0.025379 | 1
5566 | 0 | 0.023945 | 0.94301 | 0 | 0 | 1 | 0 | 0.023945 | 1
5567 | 0 | 0.032347 | 0.94301 | 0 | 0 | 1 | 0 | 0.032347 | 1
5568 | 0 | 0.02265 | 0.94301 | 0 | 0 | 1 | 0 | 0.02265 | 1
5569 | 0 | 0.0064049 | 0.94301 | 0 | 0 | 1 | 0 | 0.0064049 | 1
5570 | 0 | 0.030484 | 0.94301 | 0 | 0 | 1 | 0 | 0.030484 | 1
5571 | 0 | 0.014912 | 0.94301 | 0 | 0 | 1 | 0 | 0.014912 | 1
5572 | 0 | 0.0081873 | 0.94301 | 0 | 0 | 1 | 0 | 0.0081873 | 1
5573 | 0 | 0.0023907 | 0.94301 | 0 | 0 | 1 | 0 | 0.0023907 | 1
5574 | 0 | 0.011597 | 0.94301 | 0 | 0 | 1 | 0 | 0.011597 | 1
5575 | 0 | 0.032797 | 0.94301 | 0 | 0 | 1 | 0 | 0.032797 | 1
5576 | 0 | 0.040226 | 0.94301 | 0 | 0 | 1 | 0 | 0.040226 | 1
5577 | 0.076102 | 0.029758 | 0.94301 | 0 | 0 | 1 | 0.076102 | 0.029758 | 1
5578 | 0.17183 | 0.051802 | 0.94301 | 0 | 0 | 1 | 0.17183 | 0.051802 | 1
5579 | 0.21376 | 0.068819 | 0.94301 | 0 | 0 | 1 | 0.21376 | 0.068819 | 1
5580 | 0.34042 | 0.079255 | 0.94301 | 0 | 0 | 1 | 0.34042 | 0.079255 | 1
5581 | 0.25333 | 0.096214 | 0.94301 | 0 | 0 | 1 | 0.25333 | 0.096214 | 1
5582 | 0.2304 | 0.099534 | 0.94301 | 0 | 0 | 1 | 0.2304 | 0.099534 | 1
5583 | 0.30299 | 0.083487 | 0.94301 | 0 | 0 | 1 | 0.30299 | 0.083487 | 1
5584 | 0.16607 | 0.098458 | 0.94301 | 0 | 0 | 1 | 0.16607 | 0.098458 | 1
5585 | 0.0037374 | 0.10473 | 0.94301 | 0 | 0 | 1 | 0.0037374 | 0.10473 | 1
5586 | 0 | 0.083185 | 0.94301 | 0 | 1 | 1 | 0 | 0.083185 | 1
5587 | 0 | 0.059732 | 0.94301 | 0 | 1 | 1 | 0 | 0.059732 | 1
5588 | 0 | 0.039223 | 0.94301 | 0 | 1 | 1 | 0 | 0.039223 | 1
5589 | 0 | 0.049944 | 0.94301 | 0 | 1 | 1 | 0 | 0.049944 | 1
5590 | 0 | 0.074702 | 0.94301 | 0 | 0 | 1 | 0 | 0.074702 | 1
5591 | 0 | 0.064077 | 0.94301 | 0 | 0 | 1 | 0 | 0.064077 | 1
5592 | 0 | 0.056389 | 0.94301 | 0 | 0 | 1 | 0 | 0.056389 | 1
5593 | 0 | 0.026066 | 0.94301 | 0 | 0 | 1 | 0 | 0.026066 | 1
5594 | 0 | 0.041775 | 0.94301 | 0 | 0 | 1 | 0 | 0.041775 | 1
5595 | 0 | 0.029732 | 0.94301 | 0 | 0 | 1 | 0 | 0.029732 | 1
5596 | 0 | 0.01637 | 0.94301 | 0 | 0 | 1 | 0 | 0.01637 | 1
5597 | 0 | 0.0034676 | 0.94301 | 0 | 0 | 1 | 0 | 0.0034676 | 1
5598 | 0 | 0.022176 | 0.94301 | 0 | 0 | 1 | 0 | 0.022176 | 1
5599 | 0 | 0.0058 | 0.94301 | 0 | 0 | 1 | 0 | 0.0058 | 1
5600 | 0 | 0.023556 | 0.94301 | 0 | 0 | 1 | 0 | 0.023556 | 1
5601 | 0 | 0.026527 | 0.94301 | 0 | 0 | 1 | 0 | 0.026527 | 1
5602 | 0.04489 | 0.062257 | 0.94301 | 0 | 0 | 1 | 0.04489 | 0.062257 | 1
5603 | 0.096403 | 0.083831 | 0.94301 | 0 | 0 | 1 | 0.096403 | 0.083831 | 1
5604 | 0.17502 | 0.10176 | 0.94301 | 0 | 0 | 1 | 0.17502 | 0.10176 | 1
5605 | 0.1106 | 0.11373 | 0.94301 | 0 | 0 | 1 | 0.1106 | 0.11373 | 1
5606 | 0.086876 | 0.10522 | 0.94301 | 0 | 0 | 1 | 0.086876 | 0.10522 | 1
5607 | 0.091496 | 0.10404 | 0.94301 | 0 | 0 | 1 | 0.091496 | 0.10404 | 1
5608 | 0.015884 | 0.13012 | 0.94301 | 0 | 0 | 1 | 0.015884 | 0.13012 | 1
5609 | 0 | 0.10826 | 0.94301 | 0 | 0 | 1 | 0 | 0.10826 | 1
5610 | 0 | 0.083353 | 0.94301 | 0 | 1 | 1 | 0 | 0.083353 | 1
5611 | 0 | 0.041175 | 0.94301 | 0 | 1 | 1 | 0 | 0.041175 | 1
5612 | 0 | 0.019432 | 0.94301 | 0 | 1 | 1 | 0 | 0.019432 | 1
5613 | 0 | 0.025277 | 0.94301 | 0 | 1 | 1 | 0 | 0.025277 | 1
5614 | 0 | 0.045902 | 0.94301 | 0 | 0 | 1 | 0 | 0.045902 | 1
5615 | 0 | 0.03401 | 0.94301 | 0 | 0 | 1 | 0 | 0.03401 | 1
5616 | 0 | 0.041532 | 0.94301 | 0 | 0 | 1 | 0 | 0.041532 | 1
5617 | 0 | 0.058166 | 0.94301 | 0 | 0 | 1 | 0 | 0.058166 | 1
5618 | 0 | 0.0070678 | 0.94301 | 0 | 0 | 1 | 0 | 0.0070678 | 1
5619 | 0 | 0.01293 | 0.94301 | 0 | 0 | 1 | 0 | 0.01293 | 1
5620 | 0 | 0.0006535 | 0.94301 | 0 | 0 | 1 | 0 | 0.0006535 | 1
5621 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5622 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5623 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5624 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5625 | 0 | 0.020538 | 0.94301 | 0 | 0 | 1 | 0 | 0.020538 | 1
5626 | 0 | 0.06345 | 0.94301 | 0 | 0 | 1 | 0 | 0.06345 | 1
5627 | 0.030297 | 0.075292 | 0.94301 | 0 | 0 | 1 | 0.030297 | 0.075292 | 1
5628 | 0.084912 | 0.10056 | 0.94301 | 0 | 0 | 1 | 0.084912 | 0.10056 | 1
5629 | 0.065878 | 0.097238 | 0.94301 | 0 | 0 | 1 | 0.065878 | 0.097238 | 1
5630 | 0.02403 | 0.087769 | 0.94301 | 0 | 0 | 1 | 0.02403 | 0.087769 | 1
5631 | 0.023535 | 0.073417 | 0.94301 | 0 | 0 | 1 | 0.023535 | 0.073417 | 1
5632 | 0 | 0.089055 | 0.94301 | 0 | 0 | 1 | 0 | 0.089055 | 1
5633 | 0 | 0.070706 | 0.94301 | 0 | 0 | 1 | 0 | 0.070706 | 1
5634 | 0 | 0.058899 | 0.94301 | 0 | 1 | 1 | 0 | 0.058899 | 1
5635 | 0 | 0.022844 | 0.94301 | 0 | 1 | 1 | 0 | 0.022844 | 1
5636 | 0 | 0.0042837 | 0.94301 | 0 | 1 | 1 | 0 | 0.0042837 | 1
5637 | 0 | 0.0031712 | 0.94301 | 0 | 1 | 1 | 0 | 0.0031712 | 1
5638 | 0 | 0.012031 | 0.94301 | 0 | 0 | 1 | 0 | 0.012031 | 1
5639 | 0 | 0.010299 | 0.94301 | 0 | 0 | 1 | 0 | 0.010299 | 1
5640 | 0 | 0.012252 | 0.94301 | 0 | 0 | 1 | 0 | 0.012252 | 1
5641 | 0 | 0.02833 | 0.94301 | 0 | 0 | 1 | 0 | 0.02833 | 1
5642 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5643 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5644 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5645 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5646 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5647 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5648 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5649 | 0 | 0.019426 | 0.94301 | 0 | 0 | 1 | 0 | 0.019426 | 1
5650 | 0 | 0.043357 | 0.94301 | 0 | 0 | 1 | 0 | 0.043357 | 1
5651 | 0 | 0.046612 | 0.94301 | 0 | 0 | 1 | 0 | 0.046612 | 1
5652 | 0.034287 | 0.063065 | 0.94301 | 0 | 0 | 1 | 0.034287 | 0.063065 | 1
5653 | 0.089337 | 0.05936 | 0.94301 | 0 | 0 | 1 | 0.089337 | 0.05936 | 1
5654 | 0.071724 | 0.058051 | 0.94301 | 0 | 0 | 1 | 0.071724 | 0.058051 | 1
5655 | 0.016269 | 0.059411 | 0.94301 | 0 | 0 | 1 | 0.016269 | 0.059411 | 1
5656 | 0 | 0.039593 | 0.94301 | 0 | 0 | 1 | 0 | 0.039593 | 1
5657 | 0 | 0.040948 | 0.94301 | 0 | 0 | 1 | 0 | 0.040948 | 1
5658 | 0 | 0.029864 | 0.94301 | 0 | 1 | 1 | 0 | 0.029864 | 1
5659 | 0 | 0.011615 | 0.94301 | 0 | 1 | 1 | 0 | 0.011615 | 1
5660 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5661 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5662 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5663 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5664 | 0 | 0.0057408 | 0.94301 | 0 | 0 | 1 | 0 | 0.0057408 | 1
5665 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5666 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5667 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5668 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5669 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5670 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5671 | 0 | 0.0051775 | 0.94301 | 0 | 0 | 1 | 0 | 0.0051775 | 1
5672 | 0 | 0.009899 | 0.94301 | 0 | 0 | 1 | 0 | 0.009899 | 1
5673 | 0 | 0.023315 | 0.94301 | 0 | 0 | 1 | 0 | 0.023315 | 1
5674 | 0 | 0.046279 | 0.94301 | 0 | 0 | 1 | 0 | 0.046279 | 1
5675 | 0.0299 | 0.040401 | 0.94301 | 0 | 0 | 1 | 0.0299 | 0.040401 | 1
5676 | 0.081103 | 0.054236 | 0.94301 | 0 | 0 | 1 | 0.081103 | 0.054236 | 1
5677 | 0.1791 | 0.049798 | 0.94301 | 0 | 0 | 1 | 0.1791 | 0.049798 | 1
5678 | 0.14754 | 0.049484 | 0.94301 | 0 | 0 | 1 | 0.14754 | 0.049484 | 1
5679 | 0.12879 | 0.04126 | 0.94301 | 0 | 0 | 1 | 0.12879 | 0.04126 | 1
5680 | 0.062489 | 0.020685 | 0.94301 | 0 | 0 | 1 | 0.062489 | 0.020685 | 1
5681 | 0 | 0.0364 | 0.94301 | 0 | 0 | 1 | 0 | 0.0364 | 1
5682 | 0 | 0.024607 | 0.94301 | 0 | 1 | 1 | 0 | 0.024607 | 1
5683 | 0 | 0.021948 | 0.94301 | 0 | 1 | 1 | 0 | 0.021948 | 1
5684 | 0 | 0.011287 | 0.94301 | 0 | 1 | 1 | 0 | 0.011287 | 1
5685 | 0 | 0.013066 | 0.94301 | 0 | 1 | 1 | 0 | 0.013066 | 1
5686 | 0 | 0.014801 | 0.94301 | 0 | 0 | 1 | 0 | 0.014801 | 1
5687 | 0 | 0.012882 | 0.94301 | 0 | 0 | 1 | 0 | 0.012882 | 1
5688 | 0 | 0.014779 | 0.94301 | 0 | 0 | 1 | 0 | 0.014779 | 1
5689 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5690 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5691 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5692 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5693 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5694 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5695 | 0 | 0.0046688 | 0.94301 | 0 | 0 | 1 | 0 | 0.0046688 | 1
5696 | 0 | 0.018977 | 0.94301 | 0 | 0 | 1 | 0 | 0.018977 | 1
5697 | 0 | 0.023387 | 0.94301 | 0 | 0 | 1 | 0 | 0.023387 | 1
5698 | 0.078277 | 0.068812 | 0.94301 | 0 | 0 | 1 | 0.078277 | 0.068812 | 1
5699 | 0.10029 | 0.067823 | 0.94301 | 0 | 0 | 1 | 0.10029 | 0.067823 | 1
5700 | 0.11832 | 0.065042 | 0.94301 | 0 | 0 | 1 | 0.11832 | 0.065042 | 1
5701 | 0.21619 | 0.071933 | 0.94301 | 0 | 0 | 1 | 0.21619 | 0.071933 | 1
5702 | 0.16421 | 0.051161 | 0.94301 | 0 | 0 | 1 | 0.16421 | 0.051161 | 1
5703 | 0.11807 | 0.052668 | 0.94301 | 0 | 0 | 1 | 0.11807 | 0.052668 | 1
5704 | 0.042485 | 0.040745 | 0.94301 | 0 | 0 | 1 | 0.042485 | 0.040745 | 1
5705 | 0 | 0.053685 | 0.94301 | 0 | 0 | 1 | 0 | 0.053685 | 1
5706 | 0 | 0.048168 | 0.94301 | 0 | 1 | 1 | 0 | 0.048168 | 1
5707 | 0 | 0.03794 | 0.94301 | 0 | 1 | 1 | 0 | 0.03794 | 1
5708 | 0 | 0.029164 | 0.94301 | 0 | 1 | 1 | 0 | 0.029164 | 1
5709 | 0 | 0.031485 | 0.94301 | 0 | 1 | 1 | 0 | 0.031485 | 1
5710 | 0 | 0.02802 | 0.94301 | 0 | 0 | 1 | 0 | 0.02802 | 1
5711 | 0 | 0.018189 | 0.94301 | 0 | 0 | 1 | 0 | 0.018189 | 1
5712 | 0 | 0.019963 | 0.94301 | 0 | 0 | 1 | 0 | 0.019963 | 1
5713 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5714 | 0 | 0.0012786 | 0.94301 | 0 | 0 | 1 | 0 | 0.0012786 | 1
5715 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5716 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5717 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5718 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5719 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5720 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5721 | 0.0041504 | 0 | 0.94301 | 0 | 0 | 1 | 0.0041504 | 0 | 1
5722 | 0.12436 | 0.024504 | 0.94301 | 0 | 0 | 1 | 0.12436 | 0.024504 | 1
5723 | 0.16303 | 0.037392 | 0.94301 | 0 | 0 | 1 | 0.16303 | 0.037392 | 1
5724 | 0.21 | 0.044741 | 0.94301 | 0 | 0 | 1 | 0.21 | 0.044741 | 1
5725 | 0.19802 | 0.061516 | 0.94301 | 0 | 0 | 1 | 0.19802 | 0.061516 | 1
5726 | 0.15332 | 0.060137 | 0.94301 | 0 | 0 | 1 | 0.15332 | 0.060137 | 1
5727 | 0.07526 | 0.056359 | 0.94301 | 0 | 0 | 1 | 0.07526 | 0.056359 | 1
5728 | 0 | 0.049164 | 0.94301 | 0 | 0 | 1 | 0 | 0.049164 | 1
5729 | 0 | 0.053246 | 0.94301 | 0 | 0 | 1 | 0 | 0.053246 | 1
5730 | 0 | 0.045235 | 0.94301 | 0 | 1 | 1 | 0 | 0.045235 | 1
5731 | 0 | 0.025747 | 0.94301 | 0 | 1 | 1 | 0 | 0.025747 | 1
5732 | 0 | 0.014566 | 0.94301 | 0 | 1 | 1 | 0 | 0.014566 | 1
5733 | 0 | 0.025438 | 0.94301 | 0 | 1 | 1 | 0 | 0.025438 | 1
5734 | 0 | 0.032523 | 0.94301 | 0 | 0 | 1 | 0 | 0.032523 | 1
5735 | 0 | 0.031283 | 0.94301 | 0 | 0 | 1 | 0 | 0.031283 | 1
5736 | 0 | 0.01387 | 0.94301 | 0 | 0 | 1 | 0 | 0.01387 | 1
5737 | 0 | 0.01289 | 0.94301 | 0 | 0 | 1 | 0 | 0.01289 | 1
5738 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5739 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5740 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5741 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5742 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5743 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5744 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5745 | 0.020364 | 0 | 0.94301 | 0 | 0 | 1 | 0.020364 | 0 | 1
5746 | 0.12263 | 0 | 0.94301 | 0 | 0 | 1 | 0.12263 | 0 | 1
5747 | 0.1437 | 0.01665 | 0.94301 | 0 | 0 | 1 | 0.1437 | 0.01665 | 1
5748 | 0.18117 | 0.044176 | 0.94301 | 0 | 0 | 1 | 0.18117 | 0.044176 | 1
5749 | 0.20241 | 0.073302 | 0.94301 | 0 | 0 | 1 | 0.20241 | 0.073302 | 1
5750 | 0.18613 | 0.087465 | 0.94301 | 0 | 0 | 1 | 0.18613 | 0.087465 | 1
5751 | 0.093636 | 0.083869 | 0.94301 | 0 | 0 | 1 | 0.093636 | 0.083869 | 1
5752 | 0 | 0.070517 | 0.94301 | 0 | 0 | 1 | 0 | 0.070517 | 1
5753 | 0 | 0.082776 | 0.94301 | 0 | 0 | 1 | 0 | 0.082776 | 1
5754 | 0 | 0.059685 | 0.94301 | 0 | 1 | 1 | 0 | 0.059685 | 1
5755 | 0 | 0.026493 | 0.94301 | 0 | 1 | 1 | 0 | 0.026493 | 1
5756 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5757 | 0 | 0.018305 | 0.94301 | 0 | 1 | 1 | 0 | 0.018305 | 1
5758 | 0 | 0.0099119 | 0.94301 | 0 | 0 | 1 | 0 | 0.0099119 | 1
5759 | 0 | 0.014694 | 0.94301 | 0 | 0 | 1 | 0 | 0.014694 | 1
5760 | 0 | 0.0030655 | 0.94301 | 0 | 0 | 1 | 0 | 0.0030655 | 1
5761 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5762 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5763 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5764 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5765 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5766 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5767 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5768 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5769 | 0.082525 | 0 | 0.94301 | 0 | 0 | 1 | 0.082525 | 0 | 1
5770 | 0.18836 | 0.00056448 | 0.94301 | 0 | 0 | 1 | 0.18836 | 0.00056448 | 1
5771 | 0.26762 | 0.024695 | 0.94301 | 0 | 0 | 1 | 0.26762 | 0.024695 | 1
5772 | 0.30096 | 0.061221 | 0.94301 | 0 | 0 | 1 | 0.30096 | 0.061221 | 1
5773 | 0.31412 | 0.096468 | 0.94301 | 0 | 0 | 1 | 0.31412 | 0.096468 | 1
5774 | 0.31148 | 0.12195 | 0.94301 | 0 | 0 | 1 | 0.31148 | 0.12195 | 1
5775 | 0.19697 | 0.11359 | 0.94301 | 0 | 0 | 1 | 0.19697 | 0.11359 | 1
5776 | 0.054548 | 0.089356 | 0.94301 | 0 | 0 | 1 | 0.054548 | 0.089356 | 1
5777 | 0.02533 | 0.09803 | 0.94301 | 0 | 0 | 1 | 0.02533 | 0.09803 | 1
5778 | 0 | 0.054798 | 0.94301 | 0 | 1 | 1 | 0 | 0.054798 | 1
5779 | 0 | 0.030037 | 0.94301 | 0 | 1 | 1 | 0 | 0.030037 | 1
5780 | 0 | 0.0086824 | 0.94301 | 0 | 1 | 1 | 0 | 0.0086824 | 1
5781 | 0 | 0.034838 | 0.94301 | 0 | 1 | 1 | 0 | 0.034838 | 1
5782 | 0 | 0.02381 | 0.94301 | 0 | 0 | 1 | 0 | 0.02381 | 1
5783 | 0 | 0.037281 | 0.94301 | 0 | 0 | 1 | 0 | 0.037281 | 1
5784 | 0 | 0.020159 | 0.94301 | 0 | 0 | 1 | 0 | 0.020159 | 1
5785 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5786 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5787 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5788 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5789 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5790 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5791 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5792 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5793 | 0.092062 | 0 | 0.94301 | 0 | 0 | 1 | 0.092062 | 0 | 1
5794 | 0.18019 | 0.0095755 | 0.94301 | 0 | 0 | 1 | 0.18019 | 0.0095755 | 1
5795 | 0.30376 | 0.047123 | 0.94301 | 0 | 0 | 1 | 0.30376 | 0.047123 | 1
5796 | 0.34208 | 0.086607 | 0.94301 | 0 | 0 | 1 | 0.34208 | 0.086607 | 1
5797 | 0.35737 | 0.11315 | 0.94301 | 0 | 0 | 1 | 0.35737 | 0.11315 | 1
5798 | 0.35372 | 0.12038 | 0.94301 | 0 | 0 | 1 | 0.35372 | 0.12038 | 1
5799 | 0.25884 | 0.109 | 0.94301 | 0 | 0 | 1 | 0.25884 | 0.109 | 1
5800 | 0.1218 | 0.096337 | 0.94301 | 0 | 0 | 1 | 0.1218 | 0.096337 | 1
5801 | 0.01214 | 0.10222 | 0.94301 | 0 | 0 | 1 | 0.01214 | 0.10222 | 1
5802 | 0 | 0.046474 | 0.94301 | 0 | 1 | 1 | 0 | 0.046474 | 1
5803 | 0 | 0.011956 | 0.94301 | 0 | 1 | 1 | 0 | 0.011956 | 1
5804 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5805 | 0 | 0.0012076 | 0.94301 | 0 | 1 | 1 | 0 | 0.0012076 | 1
5806 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5807 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5808 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5809 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5810 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5811 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5812 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5813 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5814 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5815 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5816 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5817 | 0.096894 | 0 | 0.94301 | 0 | 0 | 1 | 0.096894 | 0 | 1
5818 | 0.17827 | 0 | 0.94301 | 0 | 0 | 1 | 0.17827 | 0 | 1
5819 | 0.31385 | 0.027323 | 0.94301 | 0 | 0 | 1 | 0.31385 | 0.027323 | 1
5820 | 0.3625 | 0.053084 | 0.94301 | 0 | 0 | 1 | 0.3625 | 0.053084 | 1
5821 | 0.30167 | 0.077644 | 0.94301 | 0 | 0 | 1 | 0.30167 | 0.077644 | 1
5822 | 0.31931 | 0.067783 | 0.94301 | 0 | 0 | 1 | 0.31931 | 0.067783 | 1
5823 | 0.25797 | 0.050183 | 0.94301 | 0 | 0 | 1 | 0.25797 | 0.050183 | 1
5824 | 0.23843 | 0.036004 | 0.94301 | 0 | 0 | 1 | 0.23843 | 0.036004 | 1
5825 | 0.061803 | 0.037559 | 0.94301 | 0 | 0 | 1 | 0.061803 | 0.037559 | 1
5826 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5827 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5828 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5829 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5830 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5831 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5832 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5833 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5834 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5835 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5836 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5837 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5838 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5839 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5840 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5841 | 0.075604 | 0 | 0.94301 | 0 | 0 | 1 | 0.075604 | 0 | 1
5842 | 0.18256 | 0 | 0.94301 | 0 | 0 | 1 | 0.18256 | 0 | 1
5843 | 0.25019 | 0 | 0.94301 | 0 | 0 | 1 | 0.25019 | 0 | 1
5844 | 0.29246 | 0.0046383 | 0.94301 | 0 | 0 | 1 | 0.29246 | 0.0046383 | 1
5845 | 0.23442 | 0.033307 | 0.94301 | 0 | 0 | 1 | 0.23442 | 0.033307 | 1
5846 | 0.24473 | 0.032277 | 0.94301 | 0 | 0 | 1 | 0.24473 | 0.032277 | 1
5847 | 0.17715 | 0.01763 | 0.94301 | 0 | 0 | 1 | 0.17715 | 0.01763 | 1
5848 | 0.15976 | 0.0014204 | 0.94301 | 0 | 0 | 1 | 0.15976 | 0.0014204 | 1
5849 | 0.021756 | 0.0033695 | 0.94301 | 0 | 0 | 1 | 0.021756 | 0.0033695 | 1
5850 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5851 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5852 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5853 | 0 | 0 | 0.94301 | 0 | 1 | 1 | 0 | 0 | 1
5854 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5855 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5856 | 0 | 0 | 0.94301 | 0 | 0 | 1 | 0 | 0 | 1
5857 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5858 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5859 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5860 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5861 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5862 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5863 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5864 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5865 | 0.038563 | 0 | 1 | 0 | 0 | 1 | 0.038563 | 0 | 1
5866 | 0.10977 | 0 | 1 | 0 | 0 | 1 | 0.10977 | 0 | 1
5867 | 0.17373 | 0 | 1 | 0 | 0 | 1 | 0.17373 | 0 | 1
5868 | 0.16839 | 0 | 1 | 0 | 0 | 1 | 0.16839 | 0 | 1
5869 | 0.15603 | 0 | 1 | 0 | 0 | 1 | 0.15603 | 0 | 1
5870 | 0.18673 | 0.003452 | 1 | 0 | 0 | 1 | 0.18673 | 0.003452 | 1
5871 | 0.13898 | 0 | 1 | 0 | 0 | 1 | 0.13898 | 0 | 1
5872 | 0.15928 | 0 | 1 | 0 | 0 | 1 | 0.15928 | 0 | 1
5873 | 0.0022596 | 0 | 1 | 0 | 0 | 1 | 0.0022596 | 0 | 1
5874 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5875 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5876 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5877 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5878 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5879 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5880 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5881 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5882 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5883 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5884 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5885 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5886 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5887 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5888 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5889 | 0.077904 | 0 | 1 | 0 | 0 | 1 | 0.077904 | 0 | 1
5890 | 0.14655 | 0 | 1 | 0 | 0 | 1 | 0.14655 | 0 | 1
5891 | 0.20861 | 0 | 1 | 0 | 0 | 1 | 0.20861 | 0 | 1
5892 | 0.17296 | 0.00096894 | 1 | 0 | 0 | 1 | 0.17296 | 0.00096894 | 1
5893 | 0.19584 | 0.0036393 | 1 | 0 | 0 | 1 | 0.19584 | 0.0036393 | 1
5894 | 0.18384 | 0.018634 | 1 | 0 | 0 | 1 | 0.18384 | 0.018634 | 1
5895 | 0.10585 | 0.031228 | 1 | 0 | 0 | 1 | 0.10585 | 0.031228 | 1
5896 | 0.083989 | 0.014596 | 1 | 0 | 0 | 1 | 0.083989 | 0.014596 | 1
5897 | 0 | 0.015371 | 1 | 0 | 0 | 1 | 0 | 0.015371 | 1
5898 | 0 | 0.0031113 | 1 | 0 | 1 | 1 | 0 | 0.0031113 | 1
5899 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5900 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5901 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
5902 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5903 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5904 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
5905 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5906 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5907 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5908 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5909 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5910 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5911 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5912 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5913 | 0.069003 | 0 | 0.94365 | 0 | 0 | 1 | 0.069003 | 0 | 1
5914 | 0.14589 | 0.0025603 | 0.94365 | 0 | 0 | 1 | 0.14589 | 0.0025603 | 1
5915 | 0.2355 | 0.033557 | 0.94365 | 0 | 0 | 1 | 0.2355 | 0.033557 | 1
5916 | 0.13975 | 0.048899 | 0.94365 | 0 | 0 | 1 | 0.13975 | 0.048899 | 1
5917 | 0.22631 | 0.032309 | 0.94365 | 0 | 0 | 1 | 0.22631 | 0.032309 | 1
5918 | 0.17679 | 0.046413 | 0.94365 | 0 | 0 | 1 | 0.17679 | 0.046413 | 1
5919 | 0.13576 | 0.0513 | 0.94365 | 0 | 0 | 1 | 0.13576 | 0.0513 | 1
5920 | 0.094216 | 0.048993 | 0.94365 | 0 | 0 | 1 | 0.094216 | 0.048993 | 1
5921 | 0 | 0.042851 | 0.94365 | 0 | 0 | 1 | 0 | 0.042851 | 1
5922 | 0 | 0.020825 | 0.94365 | 0 | 1 | 1 | 0 | 0.020825 | 1
5923 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5924 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5925 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5926 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5927 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5928 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5929 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5930 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5931 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5932 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5933 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5934 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5935 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5936 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5937 | 0.1096 | 0 | 0.94365 | 0 | 0 | 1 | 0.1096 | 0 | 1
5938 | 0.23729 | 0 | 0.94365 | 0 | 0 | 1 | 0.23729 | 0 | 1
5939 | 0.36234 | 0.01336 | 0.94365 | 0 | 0 | 1 | 0.36234 | 0.01336 | 1
5940 | 0.27661 | 0.048629 | 0.94365 | 0 | 0 | 1 | 0.27661 | 0.048629 | 1
5941 | 0.36749 | 0.051336 | 0.94365 | 0 | 0 | 1 | 0.36749 | 0.051336 | 1
5942 | 0.23319 | 0.058006 | 0.94365 | 0 | 0 | 1 | 0.23319 | 0.058006 | 1
5943 | 0.19553 | 0.066367 | 0.94365 | 0 | 0 | 1 | 0.19553 | 0.066367 | 1
5944 | 0.096873 | 0.071679 | 0.94365 | 0 | 0 | 1 | 0.096873 | 0.071679 | 1
5945 | 0 | 0.061928 | 0.94365 | 0 | 0 | 1 | 0 | 0.061928 | 1
5946 | 0 | 0.043601 | 0.94365 | 0 | 1 | 1 | 0 | 0.043601 | 1
5947 | 0 | 0.0068268 | 0.94365 | 0 | 1 | 1 | 0 | 0.0068268 | 1
5948 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5949 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5950 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5951 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5952 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5953 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5954 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5955 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5956 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5957 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5958 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5959 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5960 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5961 | 0.050162 | 0 | 0.94365 | 0 | 0 | 1 | 0.050162 | 0 | 1
5962 | 0.2287 | 0 | 0.94365 | 0 | 0 | 1 | 0.2287 | 0 | 1
5963 | 0.32112 | 0.0055883 | 0.94365 | 0 | 0 | 1 | 0.32112 | 0.0055883 | 1
5964 | 0.27473 | 0.027321 | 0.94365 | 0 | 0 | 1 | 0.27473 | 0.027321 | 1
5965 | 0.30751 | 0.048097 | 0.94365 | 0 | 0 | 1 | 0.30751 | 0.048097 | 1
5966 | 0.27514 | 0.063119 | 0.94365 | 0 | 0 | 1 | 0.27514 | 0.063119 | 1
5967 | 0.24654 | 0.060582 | 0.94365 | 0 | 0 | 1 | 0.24654 | 0.060582 | 1
5968 | 0.16789 | 0.061984 | 0.94365 | 0 | 0 | 1 | 0.16789 | 0.061984 | 1
5969 | 0.034337 | 0.053765 | 0.94365 | 0 | 0 | 1 | 0.034337 | 0.053765 | 1
5970 | 0 | 0.034621 | 0.94365 | 0 | 1 | 1 | 0 | 0.034621 | 1
5971 | 0 | 0.014362 | 0.94365 | 0 | 1 | 1 | 0 | 0.014362 | 1
5972 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5973 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5974 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5975 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5976 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5977 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5978 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5979 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5980 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5981 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5982 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5983 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5984 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5985 | 0.069124 | 0 | 0.94365 | 0 | 0 | 1 | 0.069124 | 0 | 1
5986 | 0.24542 | 0 | 0.94365 | 0 | 0 | 1 | 0.24542 | 0 | 1
5987 | 0.28388 | 0.00074549 | 0.94365 | 0 | 0 | 1 | 0.28388 | 0.00074549 | 1
5988 | 0.3381 | 0.01832 | 0.94365 | 0 | 0 | 1 | 0.3381 | 0.01832 | 1
5989 | 0.274 | 0.043584 | 0.94365 | 0 | 0 | 1 | 0.274 | 0.043584 | 1
5990 | 0.21081 | 0.052777 | 0.94365 | 0 | 0 | 1 | 0.21081 | 0.052777 | 1
5991 | 0.21195 | 0.048917 | 0.94365 | 0 | 0 | 1 | 0.21195 | 0.048917 | 1
5992 | 0.15347 | 0.052291 | 0.94365 | 0 | 0 | 1 | 0.15347 | 0.052291 | 1
5993 | 0.02015 | 0.045039 | 0.94365 | 0 | 0 | 1 | 0.02015 | 0.045039 | 1
5994 | 0 | 0.032907 | 0.94365 | 0 | 1 | 1 | 0 | 0.032907 | 1
5995 | 0 | 0.01152 | 0.94365 | 0 | 1 | 1 | 0 | 0.01152 | 1
5996 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5997 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
5998 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
5999 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6000 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6001 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6002 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6003 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6004 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6005 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6006 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6007 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6008 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6009 | 0.033552 | 0 | 0.94365 | 0 | 0 | 1 | 0.033552 | 0 | 1
6010 | 0.19411 | 0.0014273 | 0.94365 | 0 | 0 | 1 | 0.19411 | 0.0014273 | 1
6011 | 0.20087 | 0.014676 | 0.94365 | 0 | 0 | 1 | 0.20087 | 0.014676 | 1
6012 | 0.27726 | 0.023359 | 0.94365 | 0 | 0 | 1 | 0.27726 | 0.023359 | 1
6013 | 0.22682 | 0.046105 | 0.94365 | 0 | 0 | 1 | 0.22682 | 0.046105 | 1
6014 | 0.19249 | 0.053563 | 0.94365 | 0 | 0 | 1 | 0.19249 | 0.053563 | 1
6015 | 0.18278 | 0.052584 | 0.94365 | 0 | 0 | 1 | 0.18278 | 0.052584 | 1
6016 | 0.113 | 0.047857 | 0.94365 | 0 | 0 | 1 | 0.113 | 0.047857 | 1
6017 | 0.011373 | 0.041781 | 0.94365 | 0 | 0 | 1 | 0.011373 | 0.041781 | 1
6018 | 0 | 0.036025 | 0.94365 | 0 | 1 | 1 | 0 | 0.036025 | 1
6019 | 0 | 0.014555 | 0.94365 | 0 | 1 | 1 | 0 | 0.014555 | 1
6020 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6021 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6022 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6023 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6024 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6025 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6026 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6027 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6028 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6029 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6030 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6031 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6032 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6033 | 0.097021 | 0 | 0.94365 | 0 | 0 | 1 | 0.097021 | 0 | 1
6034 | 0.23688 | 0 | 0.94365 | 0 | 0 | 1 | 0.23688 | 0 | 1
6035 | 0.26021 | 0.0069147 | 0.94365 | 0 | 0 | 1 | 0.26021 | 0.0069147 | 1
6036 | 0.31389 | 0.026621 | 0.94365 | 0 | 0 | 1 | 0.31389 | 0.026621 | 1
6037 | 0.22814 | 0.042614 | 0.94365 | 0 | 0 | 1 | 0.22814 | 0.042614 | 1
6038 | 0.21732 | 0.028781 | 0.94365 | 0 | 0 | 1 | 0.21732 | 0.028781 | 1
6039 | 0.19835 | 0.026138 | 0.94365 | 0 | 0 | 1 | 0.19835 | 0.026138 | 1
6040 | 0.11035 | 0.013369 | 0.94365 | 0 | 0 | 1 | 0.11035 | 0.013369 | 1
6041 | 0 | 0.03196 | 0.94365 | 0 | 0 | 1 | 0 | 0.03196 | 1
6042 | 0 | 0.025334 | 0.94365 | 0 | 1 | 1 | 0 | 0.025334 | 1
6043 | 0 | 0.014645 | 0.94365 | 0 | 1 | 1 | 0 | 0.014645 | 1
6044 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6045 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6046 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6047 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6048 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6049 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6050 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6051 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6052 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6053 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6054 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6055 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6056 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6057 | 0.08291 | 0 | 0.94365 | 0 | 0 | 1 | 0.08291 | 0 | 1
6058 | 0.22733 | 0 | 0.94365 | 0 | 0 | 1 | 0.22733 | 0 | 1
6059 | 0.2463 | 0.024945 | 0.94365 | 0 | 0 | 1 | 0.2463 | 0.024945 | 1
6060 | 0.29475 | 0.0539 | 0.94365 | 0 | 0 | 1 | 0.29475 | 0.0539 | 1
6061 | 0.18285 | 0.061996 | 0.94365 | 0 | 0 | 1 | 0.18285 | 0.061996 | 1
6062 | 0.15724 | 0.056044 | 0.94365 | 0 | 0 | 1 | 0.15724 | 0.056044 | 1
6063 | 0.1224 | 0.047735 | 0.94365 | 0 | 0 | 1 | 0.1224 | 0.047735 | 1
6064 | 0.034534 | 0.030349 | 0.94365 | 0 | 0 | 1 | 0.034534 | 0.030349 | 1
6065 | 0 | 0.037791 | 0.94365 | 0 | 0 | 1 | 0 | 0.037791 | 1
6066 | 0 | 0.0315 | 0.94365 | 0 | 1 | 1 | 0 | 0.0315 | 1
6067 | 0 | 0.025821 | 0.94365 | 0 | 1 | 1 | 0 | 0.025821 | 1
6068 | 0 | 0.005754 | 0.94365 | 0 | 1 | 1 | 0 | 0.005754 | 1
6069 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6070 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6071 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6072 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6073 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6074 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6075 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6076 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6077 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6078 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6079 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6080 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6081 | 0.073593 | 0 | 0.94365 | 0 | 0 | 1 | 0.073593 | 0 | 1
6082 | 0.25766 | 0 | 0.94365 | 0 | 0 | 1 | 0.25766 | 0 | 1
6083 | 0.25224 | 0 | 0.94365 | 0 | 0 | 1 | 0.25224 | 0 | 1
6084 | 0.2214 | 0.00055933 | 0.94365 | 0 | 0 | 1 | 0.2214 | 0.00055933 | 1
6085 | 0.13246 | 0 | 0.94365 | 0 | 0 | 1 | 0.13246 | 0 | 1
6086 | 0.089752 | 0 | 0.94365 | 0 | 0 | 1 | 0.089752 | 0 | 1
6087 | 0.086546 | 0 | 0.94365 | 0 | 0 | 1 | 0.086546 | 0 | 1
6088 | 0.0093977 | 0 | 0.94365 | 0 | 0 | 1 | 0.0093977 | 0 | 1
6089 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6090 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6091 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6092 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6093 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6094 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6095 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6096 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6097 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6098 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6099 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6100 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6101 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6102 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6103 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6104 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6105 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6106 | 0.0916 | 0 | 0.94365 | 0 | 0 | 1 | 0.0916 | 0 | 1
6107 | 0.16922 | 0 | 0.94365 | 0 | 0 | 1 | 0.16922 | 0 | 1
6108 | 0.1557 | 0 | 0.94365 | 0 | 0 | 1 | 0.1557 | 0 | 1
6109 | 0.12448 | 0 | 0.94365 | 0 | 0 | 1 | 0.12448 | 0 | 1
6110 | 0.064259 | 0 | 0.94365 | 0 | 0 | 1 | 0.064259 | 0 | 1
6111 | 0.042989 | 0 | 0.94365 | 0 | 0 | 1 | 0.042989 | 0 | 1
6112 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6113 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6114 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6115 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6116 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6117 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6118 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6119 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6120 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6121 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6122 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6123 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6124 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6125 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6126 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6127 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6128 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6129 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6130 | 0.06798 | 0 | 0.94365 | 0 | 0 | 1 | 0.06798 | 0 | 1
6131 | 0.15802 | 0 | 0.94365 | 0 | 0 | 1 | 0.15802 | 0 | 1
6132 | 0.14972 | 0 | 0.94365 | 0 | 0 | 1 | 0.14972 | 0 | 1
6133 | 0.087542 | 0 | 0.94365 | 0 | 0 | 1 | 0.087542 | 0 | 1
6134 | 0.060298 | 0 | 0.94365 | 0 | 0 | 1 | 0.060298 | 0 | 1
6135 | 0.034973 | 0 | 0.94365 | 0 | 0 | 1 | 0.034973 | 0 | 1
6136 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6137 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6138 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6139 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6140 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6141 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6142 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6143 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6144 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6145 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6146 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6147 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6148 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6149 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6150 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6151 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6152 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6153 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6154 | 0.017146 | 0.0049854 | 0.94365 | 0 | 0 | 1 | 0.017146 | 0.0049854 | 1
6155 | 0.19933 | 0.038343 | 0.94365 | 0 | 0 | 1 | 0.19933 | 0.038343 | 1
6156 | 0.22559 | 0.071203 | 0.94365 | 0 | 0 | 1 | 0.22559 | 0.071203 | 1
6157 | 0.1647 | 0.062066 | 0.94365 | 0 | 0 | 1 | 0.1647 | 0.062066 | 1
6158 | 0.16779 | 0.042864 | 0.94365 | 0 | 0 | 1 | 0.16779 | 0.042864 | 1
6159 | 0.10019 | 0.043232 | 0.94365 | 0 | 0 | 1 | 0.10019 | 0.043232 | 1
6160 | 0.010938 | 0.048054 | 0.94365 | 0 | 0 | 1 | 0.010938 | 0.048054 | 1
6161 | 0 | 0.027931 | 0.94365 | 0 | 0 | 1 | 0 | 0.027931 | 1
6162 | 0 | 0.0092193 | 0.94365 | 0 | 1 | 1 | 0 | 0.0092193 | 1
6163 | 0 | 0.0051996 | 0.94365 | 0 | 1 | 1 | 0 | 0.0051996 | 1
6164 | 0 | 0.016462 | 0.94365 | 0 | 1 | 1 | 0 | 0.016462 | 1
6165 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6166 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6167 | 0 | 0.007378 | 0.94365 | 0 | 0 | 1 | 0 | 0.007378 | 1
6168 | 0 | 0.035467 | 0.94365 | 0 | 0 | 1 | 0 | 0.035467 | 1
6169 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6170 | 0 | 0.0058448 | 0.94365 | 0 | 0 | 1 | 0 | 0.0058448 | 1
6171 | 0 | 0.016442 | 0.94365 | 0 | 0 | 1 | 0 | 0.016442 | 1
6172 | 0 | 0.021122 | 0.94365 | 0 | 0 | 1 | 0 | 0.021122 | 1
6173 | 0 | 0.039729 | 0.94365 | 0 | 0 | 1 | 0 | 0.039729 | 1
6174 | 0 | 0.043136 | 0.94365 | 0 | 0 | 1 | 0 | 0.043136 | 1
6175 | 0 | 0.041457 | 0.94365 | 0 | 0 | 1 | 0 | 0.041457 | 1
6176 | 0 | 0.014776 | 0.94365 | 0 | 0 | 1 | 0 | 0.014776 | 1
6177 | 0.012521 | 0.0095538 | 0.94365 | 0 | 0 | 1 | 0.012521 | 0.0095538 | 1
6178 | 0.11897 | 0.052178 | 0.94365 | 0 | 0 | 1 | 0.11897 | 0.052178 | 1
6179 | 0.26286 | 0.076226 | 0.94365 | 0 | 0 | 1 | 0.26286 | 0.076226 | 1
6180 | 0.31088 | 0.087721 | 0.94365 | 0 | 0 | 1 | 0.31088 | 0.087721 | 1
6181 | 0.22499 | 0.066663 | 0.94365 | 0 | 0 | 1 | 0.22499 | 0.066663 | 1
6182 | 0.20286 | 0.058339 | 0.94365 | 0 | 0 | 1 | 0.20286 | 0.058339 | 1
6183 | 0.15535 | 0.064656 | 0.94365 | 0 | 0 | 1 | 0.15535 | 0.064656 | 1
6184 | 0.076123 | 0.060146 | 0.94365 | 0 | 0 | 1 | 0.076123 | 0.060146 | 1
6185 | 0 | 0.052963 | 0.94365 | 0 | 0 | 1 | 0 | 0.052963 | 1
6186 | 0 | 0.040568 | 0.94365 | 0 | 1 | 1 | 0 | 0.040568 | 1
6187 | 0 | 0.045139 | 0.94365 | 0 | 1 | 1 | 0 | 0.045139 | 1
6188 | 0 | 0.038811 | 0.94365 | 0 | 1 | 1 | 0 | 0.038811 | 1
6189 | 0 | 0.010327 | 0.94365 | 0 | 1 | 1 | 0 | 0.010327 | 1
6190 | 0 | 0.020491 | 0.94365 | 0 | 0 | 1 | 0 | 0.020491 | 1
6191 | 0 | 0.027079 | 0.94365 | 0 | 0 | 1 | 0 | 0.027079 | 1
6192 | 0 | 0.052865 | 0.94365 | 0 | 0 | 1 | 0 | 0.052865 | 1
6193 | 0 | 0.029143 | 0.86826 | 0 | 0 | 1 | 0 | 0.029143 | 1
6194 | 0 | 0.00097593 | 0.86826 | 0 | 0 | 1 | 0 | 0.00097593 | 1
6195 | 0 | 0.0082699 | 0.86826 | 0 | 0 | 1 | 0 | 0.0082699 | 1
6196 | 0 | 0.026207 | 0.86826 | 0 | 0 | 1 | 0 | 0.026207 | 1
6197 | 0 | 0.047078 | 0.86826 | 0 | 0 | 1 | 0 | 0.047078 | 1
6198 | 0 | 0.052126 | 0.86826 | 0 | 0 | 1 | 0 | 0.052126 | 1
6199 | 0 | 0.053671 | 0.86826 | 0 | 0 | 1 | 0 | 0.053671 | 1
6200 | 0 | 0.032213 | 0.86826 | 0 | 0 | 1 | 0 | 0.032213 | 1
6201 | 0.042545 | 0.032032 | 0.86826 | 0 | 0 | 1 | 0.042545 | 0.032032 | 1
6202 | 0.1296 | 0.074071 | 0.86826 | 0 | 0 | 1 | 0.1296 | 0.074071 | 1
6203 | 0.30594 | 0.099177 | 0.86826 | 0 | 0 | 1 | 0.30594 | 0.099177 | 1
6204 | 0.33052 | 0.10596 | 0.86826 | 0 | 0 | 1 | 0.33052 | 0.10596 | 1
6205 | 0.29644 | 0.095634 | 0.86826 | 0 | 0 | 1 | 0.29644 | 0.095634 | 1
6206 | 0.23993 | 0.094472 | 0.86826 | 0 | 0 | 1 | 0.23993 | 0.094472 | 1
6207 | 0.24071 | 0.12138 | 0.86826 | 0 | 0 | 1 | 0.24071 | 0.12138 | 1
6208 | 0.10407 | 0.11049 | 0.86826 | 0 | 0 | 1 | 0.10407 | 0.11049 | 1
6209 | 0.020243 | 0.10164 | 0.86826 | 0 | 0 | 1 | 0.020243 | 0.10164 | 1
6210 | 0 | 0.093795 | 0.86826 | 0 | 1 | 1 | 0 | 0.093795 | 1
6211 | 0 | 0.07882 | 0.86826 | 0 | 1 | 1 | 0 | 0.07882 | 1
6212 | 0 | 0.069561 | 0.86826 | 0 | 1 | 1 | 0 | 0.069561 | 1
6213 | 0 | 0.046598 | 0.86826 | 0 | 1 | 1 | 0 | 0.046598 | 1
6214 | 0 | 0.047189 | 0.86826 | 0 | 0 | 1 | 0 | 0.047189 | 1
6215 | 0 | 0.067887 | 0.86826 | 0 | 0 | 1 | 0 | 0.067887 | 1
6216 | 0 | 0.08415 | 0.86826 | 0 | 0 | 1 | 0 | 0.08415 | 1
6217 | 0 | 0.034169 | 0.94365 | 0 | 0 | 1 | 0 | 0.034169 | 1
6218 | 0 | 0.038778 | 0.94365 | 0 | 0 | 1 | 0 | 0.038778 | 1
6219 | 0 | 0.028669 | 0.94365 | 0 | 0 | 1 | 0 | 0.028669 | 1
6220 | 0 | 0.031034 | 0.94365 | 0 | 0 | 1 | 0 | 0.031034 | 1
6221 | 0 | 0.047006 | 0.94365 | 0 | 0 | 1 | 0 | 0.047006 | 1
6222 | 0 | 0.038104 | 0.94365 | 0 | 0 | 1 | 0 | 0.038104 | 1
6223 | 0 | 0.051843 | 0.94365 | 0 | 0 | 1 | 0 | 0.051843 | 1
6224 | 0 | 0.042625 | 0.94365 | 0 | 0 | 1 | 0 | 0.042625 | 1
6225 | 0.12061 | 0.057796 | 0.94365 | 0 | 0 | 1 | 0.12061 | 0.057796 | 1
6226 | 0.20682 | 0.075579 | 0.94365 | 0 | 0 | 1 | 0.20682 | 0.075579 | 1
6227 | 0.32657 | 0.062988 | 0.94365 | 0 | 0 | 1 | 0.32657 | 0.062988 | 1
6228 | 0.36831 | 0.10614 | 0.94365 | 0 | 0 | 1 | 0.36831 | 0.10614 | 1
6229 | 0.27635 | 0.11086 | 0.94365 | 0 | 0 | 1 | 0.27635 | 0.11086 | 1
6230 | 0.22268 | 0.11634 | 0.94365 | 0 | 0 | 1 | 0.22268 | 0.11634 | 1
6231 | 0.16385 | 0.12818 | 0.94365 | 0 | 0 | 1 | 0.16385 | 0.12818 | 1
6232 | 0.081577 | 0.10523 | 0.94365 | 0 | 0 | 1 | 0.081577 | 0.10523 | 1
6233 | 0.0091601 | 0.10284 | 0.94365 | 0 | 0 | 1 | 0.0091601 | 0.10284 | 1
6234 | 0 | 0.088417 | 0.94365 | 0 | 1 | 1 | 0 | 0.088417 | 1
6235 | 0 | 0.05126 | 0.94365 | 0 | 1 | 1 | 0 | 0.05126 | 1
6236 | 0 | 0.044762 | 0.94365 | 0 | 1 | 1 | 0 | 0.044762 | 1
6237 | 0 | 0.039372 | 0.94365 | 0 | 1 | 1 | 0 | 0.039372 | 1
6238 | 0 | 0.055262 | 0.94365 | 0 | 0 | 1 | 0 | 0.055262 | 1
6239 | 0 | 0.051422 | 0.94365 | 0 | 0 | 1 | 0 | 0.051422 | 1
6240 | 0 | 0.045034 | 0.94365 | 0 | 0 | 1 | 0 | 0.045034 | 1
6241 | 0 | 0.058718 | 0.94365 | 0 | 0 | 1 | 0 | 0.058718 | 1
6242 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6243 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6244 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6245 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6246 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6247 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6248 | 0 | 0.026178 | 0.94365 | 0 | 0 | 1 | 0 | 0.026178 | 1
6249 | 0.043469 | 0.037674 | 0.94365 | 0 | 0 | 1 | 0.043469 | 0.037674 | 1
6250 | 0.18423 | 0.052221 | 0.94365 | 0 | 0 | 1 | 0.18423 | 0.052221 | 1
6251 | 0.31686 | 0.050027 | 0.94365 | 0 | 0 | 1 | 0.31686 | 0.050027 | 1
6252 | 0.35634 | 0.09383 | 0.94365 | 0 | 0 | 1 | 0.35634 | 0.09383 | 1
6253 | 0.26654 | 0.10446 | 0.94365 | 0 | 0 | 1 | 0.26654 | 0.10446 | 1
6254 | 0.20213 | 0.10855 | 0.94365 | 0 | 0 | 1 | 0.20213 | 0.10855 | 1
6255 | 0.15545 | 0.10628 | 0.94365 | 0 | 0 | 1 | 0.15545 | 0.10628 | 1
6256 | 0.10354 | 0.08839 | 0.94365 | 0 | 0 | 1 | 0.10354 | 0.08839 | 1
6257 | 0.0030156 | 0.092089 | 0.94365 | 0 | 0 | 1 | 0.0030156 | 0.092089 | 1
6258 | 0 | 0.07192 | 0.94365 | 0 | 1 | 1 | 0 | 0.07192 | 1
6259 | 0 | 0.025461 | 0.94365 | 0 | 1 | 1 | 0 | 0.025461 | 1
6260 | 0 | 0.021451 | 0.94365 | 0 | 1 | 1 | 0 | 0.021451 | 1
6261 | 0 | 0.017989 | 0.94365 | 0 | 1 | 1 | 0 | 0.017989 | 1
6262 | 0 | 0.023303 | 0.94365 | 0 | 0 | 1 | 0 | 0.023303 | 1
6263 | 0 | 0.030366 | 0.94365 | 0 | 0 | 1 | 0 | 0.030366 | 1
6264 | 0 | 0.019778 | 0.94365 | 0 | 0 | 1 | 0 | 0.019778 | 1
6265 | 0 | 0.011592 | 0.94365 | 0 | 0 | 1 | 0 | 0.011592 | 1
6266 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6267 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6268 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6269 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6270 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6271 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6272 | 0 | 0.015642 | 0.94365 | 0 | 0 | 1 | 0 | 0.015642 | 1
6273 | 0.067461 | 0.027967 | 0.94365 | 0 | 0 | 1 | 0.067461 | 0.027967 | 1
6274 | 0.22558 | 0.054851 | 0.94365 | 0 | 0 | 1 | 0.22558 | 0.054851 | 1
6275 | 0.37248 | 0.051885 | 0.94365 | 0 | 0 | 1 | 0.37248 | 0.051885 | 1
6276 | 0.44632 | 0.090602 | 0.94365 | 0 | 0 | 1 | 0.44632 | 0.090602 | 1
6277 | 0.34784 | 0.094544 | 0.94365 | 0 | 0 | 1 | 0.34784 | 0.094544 | 1
6278 | 0.24151 | 0.09473 | 0.94365 | 0 | 0 | 1 | 0.24151 | 0.09473 | 1
6279 | 0.17588 | 0.094184 | 0.94365 | 0 | 0 | 1 | 0.17588 | 0.094184 | 1
6280 | 0.14133 | 0.090633 | 0.94365 | 0 | 0 | 1 | 0.14133 | 0.090633 | 1
6281 | 0.045952 | 0.086187 | 0.94365 | 0 | 0 | 1 | 0.045952 | 0.086187 | 1
6282 | 0 | 0.056237 | 0.94365 | 0 | 1 | 1 | 0 | 0.056237 | 1
6283 | 0 | 0.022294 | 0.94365 | 0 | 1 | 1 | 0 | 0.022294 | 1
6284 | 0 | 0.024284 | 0.94365 | 0 | 1 | 1 | 0 | 0.024284 | 1
6285 | 0 | 0.017628 | 0.94365 | 0 | 1 | 1 | 0 | 0.017628 | 1
6286 | 0 | 0.017272 | 0.94365 | 0 | 0 | 1 | 0 | 0.017272 | 1
6287 | 0 | 0.018536 | 0.94365 | 0 | 0 | 1 | 0 | 0.018536 | 1
6288 | 0 | 0.015956 | 0.94365 | 0 | 0 | 1 | 0 | 0.015956 | 1
6289 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6290 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6291 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6292 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6293 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6294 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6295 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6296 | 0 | 0.018167 | 0.94365 | 0 | 0 | 1 | 0 | 0.018167 | 1
6297 | 0.053951 | 0.015441 | 0.94365 | 0 | 0 | 1 | 0.053951 | 0.015441 | 1
6298 | 0.20033 | 0.059561 | 0.94365 | 0 | 0 | 1 | 0.20033 | 0.059561 | 1
6299 | 0.31561 | 0.088825 | 0.94365 | 0 | 0 | 1 | 0.31561 | 0.088825 | 1
6300 | 0.37582 | 0.095149 | 0.94365 | 0 | 0 | 1 | 0.37582 | 0.095149 | 1
6301 | 0.34253 | 0.10132 | 0.94365 | 0 | 0 | 1 | 0.34253 | 0.10132 | 1
6302 | 0.2276 | 0.093669 | 0.94365 | 0 | 0 | 1 | 0.2276 | 0.093669 | 1
6303 | 0.20948 | 0.099409 | 0.94365 | 0 | 0 | 1 | 0.20948 | 0.099409 | 1
6304 | 0.14601 | 0.090783 | 0.94365 | 0 | 0 | 1 | 0.14601 | 0.090783 | 1
6305 | 0.055333 | 0.076207 | 0.94365 | 0 | 0 | 1 | 0.055333 | 0.076207 | 1
6306 | 0 | 0.050582 | 0.94365 | 0 | 1 | 1 | 0 | 0.050582 | 1
6307 | 0 | 0.044562 | 0.94365 | 0 | 1 | 1 | 0 | 0.044562 | 1
6308 | 0 | 0.047842 | 0.94365 | 0 | 1 | 1 | 0 | 0.047842 | 1
6309 | 0 | 0.054105 | 0.94365 | 0 | 1 | 1 | 0 | 0.054105 | 1
6310 | 0 | 0.047033 | 0.94365 | 0 | 0 | 1 | 0 | 0.047033 | 1
6311 | 0 | 0.049052 | 0.94365 | 0 | 0 | 1 | 0 | 0.049052 | 1
6312 | 0 | 0.047142 | 0.94365 | 0 | 0 | 1 | 0 | 0.047142 | 1
6313 | 0 | 0.011448 | 0.94365 | 0 | 0 | 1 | 0 | 0.011448 | 1
6314 | 0 | 0.0055686 | 0.94365 | 0 | 0 | 1 | 0 | 0.0055686 | 1
6315 | 0 | 0.0091002 | 0.94365 | 0 | 0 | 1 | 0 | 0.0091002 | 1
6316 | 0 | 0.012557 | 0.94365 | 0 | 0 | 1 | 0 | 0.012557 | 1
6317 | 0 | 0.023419 | 0.94365 | 0 | 0 | 1 | 0 | 0.023419 | 1
6318 | 0 | 0.038752 | 0.94365 | 0 | 0 | 1 | 0 | 0.038752 | 1
6319 | 0 | 0.031069 | 0.94365 | 0 | 0 | 1 | 0 | 0.031069 | 1
6320 | 0 | 0.046135 | 0.94365 | 0 | 0 | 1 | 0 | 0.046135 | 1
6321 | 0.14617 | 0.060424 | 0.94365 | 0 | 0 | 1 | 0.14617 | 0.060424 | 1
6322 | 0.27447 | 0.10063 | 0.94365 | 0 | 0 | 1 | 0.27447 | 0.10063 | 1
6323 | 0.38291 | 0.12039 | 0.94365 | 0 | 0 | 1 | 0.38291 | 0.12039 | 1
6324 | 0.41742 | 0.12346 | 0.94365 | 0 | 0 | 1 | 0.41742 | 0.12346 | 1
6325 | 0.40409 | 0.13666 | 0.94365 | 0 | 0 | 1 | 0.40409 | 0.13666 | 1
6326 | 0.31195 | 0.13192 | 0.94365 | 0 | 0 | 1 | 0.31195 | 0.13192 | 1
6327 | 0.30157 | 0.13725 | 0.94365 | 0 | 0 | 1 | 0.30157 | 0.13725 | 1
6328 | 0.17199 | 0.12585 | 0.94365 | 0 | 0 | 1 | 0.17199 | 0.12585 | 1
6329 | 0.084179 | 0.099753 | 0.94365 | 0 | 0 | 1 | 0.084179 | 0.099753 | 1
6330 | 0 | 0.06522 | 0.94365 | 0 | 1 | 1 | 0 | 0.06522 | 1
6331 | 0 | 0.058768 | 0.94365 | 0 | 1 | 1 | 0 | 0.058768 | 1
6332 | 0 | 0.068059 | 0.94365 | 0 | 1 | 1 | 0 | 0.068059 | 1
6333 | 0 | 0.0702 | 0.94365 | 0 | 1 | 1 | 0 | 0.0702 | 1
6334 | 0 | 0.05961 | 0.94365 | 0 | 0 | 1 | 0 | 0.05961 | 1
6335 | 0 | 0.054512 | 0.94365 | 0 | 0 | 1 | 0 | 0.054512 | 1
6336 | 0 | 0.05738 | 0.94365 | 0 | 0 | 1 | 0 | 0.05738 | 1
6337 | 0 | 0.029199 | 0.94365 | 0 | 0 | 1 | 0 | 0.029199 | 1
6338 | 0 | 0.009276 | 0.94365 | 0 | 0 | 1 | 0 | 0.009276 | 1
6339 | 0 | 0.012528 | 0.94365 | 0 | 0 | 1 | 0 | 0.012528 | 1
6340 | 0 | 0.0078909 | 0.94365 | 0 | 0 | 1 | 0 | 0.0078909 | 1
6341 | 0 | 0.027553 | 0.94365 | 0 | 0 | 1 | 0 | 0.027553 | 1
6342 | 0 | 0.031262 | 0.94365 | 0 | 0 | 1 | 0 | 0.031262 | 1
6343 | 0 | 0.043781 | 0.94365 | 0 | 0 | 1 | 0 | 0.043781 | 1
6344 | 0 | 0.057983 | 0.94365 | 0 | 0 | 1 | 0 | 0.057983 | 1
6345 | 0.15701 | 0.056504 | 0.94365 | 0 | 0 | 1 | 0.15701 | 0.056504 | 1
6346 | 0.30893 | 0.074608 | 0.94365 | 0 | 0 | 1 | 0.30893 | 0.074608 | 1
6347 | 0.38261 | 0.097932 | 0.94365 | 0 | 0 | 1 | 0.38261 | 0.097932 | 1
6348 | 0.39986 | 0.12132 | 0.94365 | 0 | 0 | 1 | 0.39986 | 0.12132 | 1
6349 | 0.40993 | 0.12817 | 0.94365 | 0 | 0 | 1 | 0.40993 | 0.12817 | 1
6350 | 0.34459 | 0.11452 | 0.94365 | 0 | 0 | 1 | 0.34459 | 0.11452 | 1
6351 | 0.24842 | 0.11116 | 0.94365 | 0 | 0 | 1 | 0.24842 | 0.11116 | 1
6352 | 0.1315 | 0.099664 | 0.94365 | 0 | 0 | 1 | 0.1315 | 0.099664 | 1
6353 | 0.041193 | 0.080908 | 0.94365 | 0 | 0 | 1 | 0.041193 | 0.080908 | 1
6354 | 0 | 0.052263 | 0.94365 | 0 | 1 | 1 | 0 | 0.052263 | 1
6355 | 0 | 0.036572 | 0.94365 | 0 | 1 | 1 | 0 | 0.036572 | 1
6356 | 0 | 0.043314 | 0.94365 | 0 | 1 | 1 | 0 | 0.043314 | 1
6357 | 0 | 0.044495 | 0.94365 | 0 | 1 | 1 | 0 | 0.044495 | 1
6358 | 0 | 0.036212 | 0.94365 | 0 | 0 | 1 | 0 | 0.036212 | 1
6359 | 0 | 0.027367 | 0.94365 | 0 | 0 | 1 | 0 | 0.027367 | 1
6360 | 0 | 0.027258 | 0.94365 | 0 | 0 | 1 | 0 | 0.027258 | 1
6361 | 0 | 0.039373 | 0.94365 | 0 | 0 | 1 | 0 | 0.039373 | 1
6362 | 0 | 0.0096793 | 0.94365 | 0 | 0 | 1 | 0 | 0.0096793 | 1
6363 | 0 | 0.012695 | 0.94365 | 0 | 0 | 1 | 0 | 0.012695 | 1
6364 | 0 | 0.0038935 | 0.94365 | 0 | 0 | 1 | 0 | 0.0038935 | 1
6365 | 0 | 0.020574 | 0.94365 | 0 | 0 | 1 | 0 | 0.020574 | 1
6366 | 0 | 0.013302 | 0.94365 | 0 | 0 | 1 | 0 | 0.013302 | 1
6367 | 0 | 0.026171 | 0.94365 | 0 | 0 | 1 | 0 | 0.026171 | 1
6368 | 0.01534 | 0.036384 | 0.94365 | 0 | 0 | 1 | 0.01534 | 0.036384 | 1
6369 | 0.21583 | 0.046152 | 0.94365 | 0 | 0 | 1 | 0.21583 | 0.046152 | 1
6370 | 0.40617 | 0.052862 | 0.94365 | 0 | 0 | 1 | 0.40617 | 0.052862 | 1
6371 | 0.42536 | 0.070379 | 0.94365 | 0 | 0 | 1 | 0.42536 | 0.070379 | 1
6372 | 0.42527 | 0.085869 | 0.94365 | 0 | 0 | 1 | 0.42527 | 0.085869 | 1
6373 | 0.46736 | 0.082553 | 0.94365 | 0 | 0 | 1 | 0.46736 | 0.082553 | 1
6374 | 0.38382 | 0.078298 | 0.94365 | 0 | 0 | 1 | 0.38382 | 0.078298 | 1
6375 | 0.30198 | 0.068027 | 0.94365 | 0 | 0 | 1 | 0.30198 | 0.068027 | 1
6376 | 0.19666 | 0.054979 | 0.94365 | 0 | 0 | 1 | 0.19666 | 0.054979 | 1
6377 | 0.066319 | 0.046775 | 0.94365 | 0 | 0 | 1 | 0.066319 | 0.046775 | 1
6378 | 0 | 0.035083 | 0.94365 | 0 | 1 | 1 | 0 | 0.035083 | 1
6379 | 0 | 0.0063254 | 0.94365 | 0 | 1 | 1 | 0 | 0.0063254 | 1
6380 | 0 | 0.011356 | 0.94365 | 0 | 1 | 1 | 0 | 0.011356 | 1
6381 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6382 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6383 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6384 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6385 | 0 | 0.021592 | 0.94365 | 0 | 0 | 1 | 0 | 0.021592 | 1
6386 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6387 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6388 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6389 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6390 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6391 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6392 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6393 | 0.098906 | 0 | 0.94365 | 0 | 0 | 1 | 0.098906 | 0 | 1
6394 | 0.16184 | 0.025527 | 0.94365 | 0 | 0 | 1 | 0.16184 | 0.025527 | 1
6395 | 0.19064 | 0.041873 | 0.94365 | 0 | 0 | 1 | 0.19064 | 0.041873 | 1
6396 | 0.26406 | 0.049018 | 0.94365 | 0 | 0 | 1 | 0.26406 | 0.049018 | 1
6397 | 0.2965 | 0.040973 | 0.94365 | 0 | 0 | 1 | 0.2965 | 0.040973 | 1
6398 | 0.22554 | 0.048504 | 0.94365 | 0 | 0 | 1 | 0.22554 | 0.048504 | 1
6399 | 0.1673 | 0.040633 | 0.94365 | 0 | 0 | 1 | 0.1673 | 0.040633 | 1
6400 | 0.11602 | 0.0282 | 0.94365 | 0 | 0 | 1 | 0.11602 | 0.0282 | 1
6401 | 0.016503 | 0.016508 | 0.94365 | 0 | 0 | 1 | 0.016503 | 0.016508 | 1
6402 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6403 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6404 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6405 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6406 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6407 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6408 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6409 | 0 | 0.0032237 | 0.94365 | 0 | 0 | 1 | 0 | 0.0032237 | 1
6410 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6411 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6412 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6413 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6414 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6415 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6416 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6417 | 0.022299 | 0 | 0.94365 | 0 | 0 | 1 | 0.022299 | 0 | 1
6418 | 0.075357 | 0 | 0.94365 | 0 | 0 | 1 | 0.075357 | 0 | 1
6419 | 0.12479 | 0.0062432 | 0.94365 | 0 | 0 | 1 | 0.12479 | 0.0062432 | 1
6420 | 0.18907 | 0.017309 | 0.94365 | 0 | 0 | 1 | 0.18907 | 0.017309 | 1
6421 | 0.18994 | 0.019688 | 0.94365 | 0 | 0 | 1 | 0.18994 | 0.019688 | 1
6422 | 0.1393 | 0.018586 | 0.94365 | 0 | 0 | 1 | 0.1393 | 0.018586 | 1
6423 | 0.12967 | 0.0072168 | 0.94365 | 0 | 0 | 1 | 0.12967 | 0.0072168 | 1
6424 | 0.10233 | 0 | 0.94365 | 0 | 0 | 1 | 0.10233 | 0 | 1
6425 | 0.018806 | 0 | 0.94365 | 0 | 0 | 1 | 0.018806 | 0 | 1
6426 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6427 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6428 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6429 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6430 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6431 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6432 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6433 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6434 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6435 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6436 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6437 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6438 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6439 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6440 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6441 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6442 | 0.0069314 | 0 | 0.94365 | 0 | 0 | 1 | 0.0069314 | 0 | 1
6443 | 0.034343 | 0 | 0.94365 | 0 | 0 | 1 | 0.034343 | 0 | 1
6444 | 0.044704 | 0.016178 | 0.94365 | 0 | 0 | 1 | 0.044704 | 0.016178 | 1
6445 | 0.061924 | 0.014378 | 0.94365 | 0 | 0 | 1 | 0.061924 | 0.014378 | 1
6446 | 0.053701 | 0.018212 | 0.94365 | 0 | 0 | 1 | 0.053701 | 0.018212 | 1
6447 | 0.028837 | 0.0055991 | 0.94365 | 0 | 0 | 1 | 0.028837 | 0.0055991 | 1
6448 | 0.0058463 | 0 | 0.94365 | 0 | 0 | 1 | 0.0058463 | 0 | 1
6449 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6450 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6451 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6452 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6453 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6454 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6455 | 0 | 0.0012456 | 0.94365 | 0 | 0 | 1 | 0 | 0.0012456 | 1
6456 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6457 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6458 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6459 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6460 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6461 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6462 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6463 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6464 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6465 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6466 | 0.072015 | 0 | 0.94365 | 0 | 0 | 1 | 0.072015 | 0 | 1
6467 | 0.12313 | 0 | 0.94365 | 0 | 0 | 1 | 0.12313 | 0 | 1
6468 | 0.10693 | 0.0081031 | 0.94365 | 0 | 0 | 1 | 0.10693 | 0.0081031 | 1
6469 | 0.11263 | 0.021268 | 0.94365 | 0 | 0 | 1 | 0.11263 | 0.021268 | 1
6470 | 0.1091 | 0.023082 | 0.94365 | 0 | 0 | 1 | 0.1091 | 0.023082 | 1
6471 | 0.044281 | 0.021523 | 0.94365 | 0 | 0 | 1 | 0.044281 | 0.021523 | 1
6472 | 0.020499 | 0 | 0.94365 | 0 | 0 | 1 | 0.020499 | 0 | 1
6473 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6474 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6475 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6476 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6477 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6478 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6479 | 0 | 0.040388 | 0.94365 | 0 | 0 | 1 | 0 | 0.040388 | 1
6480 | 0 | 0.0011018 | 0.94365 | 0 | 0 | 1 | 0 | 0.0011018 | 1
6481 | 0 | 0.000176 | 0.94365 | 0 | 0 | 1 | 0 | 0.000176 | 1
6482 | 0 | 0.0099631 | 0.94365 | 0 | 0 | 1 | 0 | 0.0099631 | 1
6483 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6484 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6485 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6486 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6487 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6488 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6489 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6490 | 0.046289 | 0 | 0.94365 | 0 | 0 | 1 | 0.046289 | 0 | 1
6491 | 0.084573 | 0 | 0.94365 | 0 | 0 | 1 | 0.084573 | 0 | 1
6492 | 0.053973 | 0.0014799 | 0.94365 | 0 | 0 | 1 | 0.053973 | 0.0014799 | 1
6493 | 0.053168 | 0.020712 | 0.94365 | 0 | 0 | 1 | 0.053168 | 0.020712 | 1
6494 | 0.058572 | 0.030912 | 0.94365 | 0 | 0 | 1 | 0.058572 | 0.030912 | 1
6495 | 0.023448 | 0.040834 | 0.94365 | 0 | 0 | 1 | 0.023448 | 0.040834 | 1
6496 | 0 | 0.010141 | 0.94365 | 0 | 0 | 1 | 0 | 0.010141 | 1
6497 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6498 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6499 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6500 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6501 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6502 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6503 | 0 | 0.032296 | 0.94365 | 0 | 0 | 1 | 0 | 0.032296 | 1
6504 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6505 | 0 | 0.013131 | 1 | 0 | 0 | 1 | 0 | 0.013131 | 1
6506 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6507 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6508 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6509 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6510 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6511 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6512 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6513 | 0.024826 | 0 | 1 | 0 | 0 | 1 | 0.024826 | 0 | 1
6514 | 0.12509 | 0 | 1 | 0 | 0 | 1 | 0.12509 | 0 | 1
6515 | 0.25667 | 0 | 1 | 0 | 0 | 1 | 0.25667 | 0 | 1
6516 | 0.21517 | 0 | 1 | 0 | 0 | 1 | 0.21517 | 0 | 1
6517 | 0.15984 | 0.0068131 | 1 | 0 | 0 | 1 | 0.15984 | 0.0068131 | 1
6518 | 0.15617 | 0.014982 | 1 | 0 | 0 | 1 | 0.15617 | 0.014982 | 1
6519 | 0.13366 | 0.03181 | 1 | 0 | 0 | 1 | 0.13366 | 0.03181 | 1
6520 | 0.025015 | 0.0042288 | 1 | 0 | 0 | 1 | 0.025015 | 0.0042288 | 1
6521 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6522 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6523 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6524 | 0 | 0.0014477 | 1 | 0 | 1 | 1 | 0 | 0.0014477 | 1
6525 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6526 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6527 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6528 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6529 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6530 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6531 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6532 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6533 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6534 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6535 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6536 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6537 | 0.098961 | 0 | 1 | 0 | 0 | 1 | 0.098961 | 0 | 1
6538 | 0.19685 | 0 | 1 | 0 | 0 | 1 | 0.19685 | 0 | 1
6539 | 0.30897 | 0 | 1 | 0 | 0 | 1 | 0.30897 | 0 | 1
6540 | 0.24887 | 0 | 1 | 0 | 0 | 1 | 0.24887 | 0 | 1
6541 | 0.19222 | 0 | 1 | 0 | 0 | 1 | 0.19222 | 0 | 1
6542 | 0.20251 | 0 | 1 | 0 | 0 | 1 | 0.20251 | 0 | 1
6543 | 0.1458 | 0 | 1 | 0 | 0 | 1 | 0.1458 | 0 | 1
6544 | 0.014356 | 0 | 1 | 0 | 0 | 1 | 0.014356 | 0 | 1
6545 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6546 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6547 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6548 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6549 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6550 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6551 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6552 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6553 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6554 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6555 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6556 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6557 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6558 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6559 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6560 | 0.014253 | 0 | 0.94365 | 0 | 0 | 1 | 0.014253 | 0 | 1
6561 | 0.12777 | 0 | 0.94365 | 0 | 0 | 1 | 0.12777 | 0 | 1
6562 | 0.32183 | 0 | 0.94365 | 0 | 0 | 1 | 0.32183 | 0 | 1
6563 | 0.50283 | 0 | 0.94365 | 0 | 0 | 1 | 0.50283 | 0 | 1
6564 | 0.41338 | 0 | 0.94365 | 0 | 0 | 1 | 0.41338 | 0 | 1
6565 | 0.39553 | 0 | 0.94365 | 0 | 0 | 1 | 0.39553 | 0 | 1
6566 | 0.28498 | 0 | 0.94365 | 0 | 0 | 1 | 0.28498 | 0 | 1
6567 | 0.18432 | 0 | 0.94365 | 0 | 0 | 1 | 0.18432 | 0 | 1
6568 | 0.065418 | 0 | 0.94365 | 0 | 0 | 1 | 0.065418 | 0 | 1
6569 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6570 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6571 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6572 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6573 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6574 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6575 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6576 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6577 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6578 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6579 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6580 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6581 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6582 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6583 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6584 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6585 | 0.096732 | 0 | 0.94365 | 0 | 0 | 1 | 0.096732 | 0 | 1
6586 | 0.29929 | 0 | 0.94365 | 0 | 0 | 1 | 0.29929 | 0 | 1
6587 | 0.42321 | 0 | 0.94365 | 0 | 0 | 1 | 0.42321 | 0 | 1
6588 | 0.35009 | 0.024563 | 0.94365 | 0 | 0 | 1 | 0.35009 | 0.024563 | 1
6589 | 0.36985 | 0.023123 | 0.94365 | 0 | 0 | 1 | 0.36985 | 0.023123 | 1
6590 | 0.21665 | 0.048495 | 0.94365 | 0 | 0 | 1 | 0.21665 | 0.048495 | 1
6591 | 0.12736 | 0.049339 | 0.94365 | 0 | 0 | 1 | 0.12736 | 0.049339 | 1
6592 | 0.07131 | 0.038374 | 0.94365 | 0 | 0 | 1 | 0.07131 | 0.038374 | 1
6593 | 0.026397 | 0.045324 | 0.94365 | 0 | 0 | 1 | 0.026397 | 0.045324 | 1
6594 | 0 | 0.045195 | 0.94365 | 0 | 1 | 1 | 0 | 0.045195 | 1
6595 | 0 | 0.024122 | 0.94365 | 0 | 1 | 1 | 0 | 0.024122 | 1
6596 | 0 | 0.018192 | 0.94365 | 0 | 1 | 1 | 0 | 0.018192 | 1
6597 | 0 | 0.034938 | 0.94365 | 0 | 1 | 1 | 0 | 0.034938 | 1
6598 | 0 | 0.028692 | 0.94365 | 0 | 0 | 1 | 0 | 0.028692 | 1
6599 | 0 | 0.0088497 | 0.94365 | 0 | 0 | 1 | 0 | 0.0088497 | 1
6600 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6601 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6602 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6603 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6604 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6605 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6606 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6607 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6608 | 0.0088604 | 0 | 0.94365 | 0 | 0 | 1 | 0.0088604 | 0 | 1
6609 | 0.11011 | 0.0068009 | 0.94365 | 0 | 0 | 1 | 0.11011 | 0.0068009 | 1
6610 | 0.32322 | 0.014679 | 0.94365 | 0 | 0 | 1 | 0.32322 | 0.014679 | 1
6611 | 0.41598 | 0.029264 | 0.94365 | 0 | 0 | 1 | 0.41598 | 0.029264 | 1
6612 | 0.30705 | 0.057546 | 0.94365 | 0 | 0 | 1 | 0.30705 | 0.057546 | 1
6613 | 0.35845 | 0.053245 | 0.94365 | 0 | 0 | 1 | 0.35845 | 0.053245 | 1
6614 | 0.17457 | 0.066309 | 0.94365 | 0 | 0 | 1 | 0.17457 | 0.066309 | 1
6615 | 0.15601 | 0.071483 | 0.94365 | 0 | 0 | 1 | 0.15601 | 0.071483 | 1
6616 | 0.078561 | 0.066126 | 0.94365 | 0 | 0 | 1 | 0.078561 | 0.066126 | 1
6617 | 0.031866 | 0.077483 | 0.94365 | 0 | 0 | 1 | 0.031866 | 0.077483 | 1
6618 | 0 | 0.071837 | 0.94365 | 0 | 1 | 1 | 0 | 0.071837 | 1
6619 | 0 | 0.058818 | 0.94365 | 0 | 1 | 1 | 0 | 0.058818 | 1
6620 | 0 | 0.047351 | 0.94365 | 0 | 1 | 1 | 0 | 0.047351 | 1
6621 | 0 | 0.03877 | 0.94365 | 0 | 1 | 1 | 0 | 0.03877 | 1
6622 | 0 | 0.043643 | 0.94365 | 0 | 0 | 1 | 0 | 0.043643 | 1
6623 | 0 | 0.011114 | 0.94365 | 0 | 0 | 1 | 0 | 0.011114 | 1
6624 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6625 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6626 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6627 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6628 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6629 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6630 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6631 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6632 | 0.0060273 | 0.0083077 | 0.94365 | 0 | 0 | 1 | 0.0060273 | 0.0083077 | 1
6633 | 0.14089 | 0.031726 | 0.94365 | 0 | 0 | 1 | 0.14089 | 0.031726 | 1
6634 | 0.31072 | 0.042918 | 0.94365 | 0 | 0 | 1 | 0.31072 | 0.042918 | 1
6635 | 0.36687 | 0.052024 | 0.94365 | 0 | 0 | 1 | 0.36687 | 0.052024 | 1
6636 | 0.25885 | 0.080953 | 0.94365 | 0 | 0 | 1 | 0.25885 | 0.080953 | 1
6637 | 0.30985 | 0.063352 | 0.94365 | 0 | 0 | 1 | 0.30985 | 0.063352 | 1
6638 | 0.23959 | 0.071613 | 0.94365 | 0 | 0 | 1 | 0.23959 | 0.071613 | 1
6639 | 0.23436 | 0.07046 | 0.94365 | 0 | 0 | 1 | 0.23436 | 0.07046 | 1
6640 | 0.13088 | 0.067327 | 0.94365 | 0 | 0 | 1 | 0.13088 | 0.067327 | 1
6641 | 0 | 0.0602 | 0.94365 | 0 | 0 | 1 | 0 | 0.0602 | 1
6642 | 0 | 0.050027 | 0.94365 | 0 | 1 | 1 | 0 | 0.050027 | 1
6643 | 0 | 0.047016 | 0.94365 | 0 | 1 | 1 | 0 | 0.047016 | 1
6644 | 0 | 0.018893 | 0.94365 | 0 | 1 | 1 | 0 | 0.018893 | 1
6645 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6646 | 0 | 0.015228 | 0.94365 | 0 | 0 | 1 | 0 | 0.015228 | 1
6647 | 0 | 0.0088845 | 0.94365 | 0 | 0 | 1 | 0 | 0.0088845 | 1
6648 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6649 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6650 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6651 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6652 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6653 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6654 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6655 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6656 | 0.0071986 | 0.02828 | 0.94365 | 0 | 0 | 1 | 0.0071986 | 0.02828 | 1
6657 | 0.12204 | 0.046054 | 0.94365 | 0 | 0 | 1 | 0.12204 | 0.046054 | 1
6658 | 0.22689 | 0.056837 | 0.94365 | 0 | 0 | 1 | 0.22689 | 0.056837 | 1
6659 | 0.31697 | 0.049219 | 0.94365 | 0 | 0 | 1 | 0.31697 | 0.049219 | 1
6660 | 0.23908 | 0.081094 | 0.94365 | 0 | 0 | 1 | 0.23908 | 0.081094 | 1
6661 | 0.24469 | 0.054452 | 0.94365 | 0 | 0 | 1 | 0.24469 | 0.054452 | 1
6662 | 0.26633 | 0.030563 | 0.94365 | 0 | 0 | 1 | 0.26633 | 0.030563 | 1
6663 | 0.25012 | 0.023234 | 0.94365 | 0 | 0 | 1 | 0.25012 | 0.023234 | 1
6664 | 0.085312 | 0.0079023 | 0.94365 | 0 | 0 | 1 | 0.085312 | 0.0079023 | 1
6665 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6666 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6667 | 0 | 0.0042666 | 0.94365 | 0 | 1 | 1 | 0 | 0.0042666 | 1
6668 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6669 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6670 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6671 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6672 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6673 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6674 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6675 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6676 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6677 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6678 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6679 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6680 | 0.00090752 | 0 | 0.94365 | 0 | 0 | 1 | 0.00090752 | 0 | 1
6681 | 0.13581 | 0 | 0.94365 | 0 | 0 | 1 | 0.13581 | 0 | 1
6682 | 0.23071 | 0 | 0.94365 | 0 | 0 | 1 | 0.23071 | 0 | 1
6683 | 0.22263 | 0.0001847 | 0.94365 | 0 | 0 | 1 | 0.22263 | 0.0001847 | 1
6684 | 0.227 | 0.034519 | 0.94365 | 0 | 0 | 1 | 0.227 | 0.034519 | 1
6685 | 0.22202 | 0.032847 | 0.94365 | 0 | 0 | 1 | 0.22202 | 0.032847 | 1
6686 | 0.22221 | 0.017556 | 0.94365 | 0 | 0 | 1 | 0.22221 | 0.017556 | 1
6687 | 0.15125 | 0.016135 | 0.94365 | 0 | 0 | 1 | 0.15125 | 0.016135 | 1
6688 | 0.014986 | 0.010929 | 0.94365 | 0 | 0 | 1 | 0.014986 | 0.010929 | 1
6689 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6690 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6691 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6692 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6693 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6694 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6695 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6696 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6697 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6698 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6699 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6700 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6701 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6702 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6703 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6704 | 0.0045256 | 0 | 0.94365 | 0 | 0 | 1 | 0.0045256 | 0 | 1
6705 | 0.13258 | 0 | 0.94365 | 0 | 0 | 1 | 0.13258 | 0 | 1
6706 | 0.25637 | 0 | 0.94365 | 0 | 0 | 1 | 0.25637 | 0 | 1
6707 | 0.23421 | 0 | 0.94365 | 0 | 0 | 1 | 0.23421 | 0 | 1
6708 | 0.27836 | 0.016067 | 0.94365 | 0 | 0 | 1 | 0.27836 | 0.016067 | 1
6709 | 0.23181 | 0.030862 | 0.94365 | 0 | 0 | 1 | 0.23181 | 0.030862 | 1
6710 | 0.1796 | 0.022719 | 0.94365 | 0 | 0 | 1 | 0.1796 | 0.022719 | 1
6711 | 0.095905 | 0.021125 | 0.94365 | 0 | 0 | 1 | 0.095905 | 0.021125 | 1
6712 | 0 | 0.027054 | 0.94365 | 0 | 0 | 1 | 0 | 0.027054 | 1
6713 | 0 | 0.019814 | 0.94365 | 0 | 0 | 1 | 0 | 0.019814 | 1
6714 | 0 | 0.018433 | 0.94365 | 0 | 1 | 1 | 0 | 0.018433 | 1
6715 | 0 | 0.0021589 | 0.94365 | 0 | 1 | 1 | 0 | 0.0021589 | 1
6716 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6717 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6718 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6719 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6720 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6721 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6722 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6723 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6724 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6725 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6726 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6727 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6728 | 0.0085252 | 0 | 0.94365 | 0 | 0 | 1 | 0.0085252 | 0 | 1
6729 | 0.17456 | 0 | 0.94365 | 0 | 0 | 1 | 0.17456 | 0 | 1
6730 | 0.33805 | 0 | 0.94365 | 0 | 0 | 1 | 0.33805 | 0 | 1
6731 | 0.25532 | 0.0026098 | 0.94365 | 0 | 0 | 1 | 0.25532 | 0.0026098 | 1
6732 | 0.31465 | 0.02823 | 0.94365 | 0 | 0 | 1 | 0.31465 | 0.02823 | 1
6733 | 0.3259 | 0.047056 | 0.94365 | 0 | 0 | 1 | 0.3259 | 0.047056 | 1
6734 | 0.14843 | 0.049302 | 0.94365 | 0 | 0 | 1 | 0.14843 | 0.049302 | 1
6735 | 0.02831 | 0.046551 | 0.94365 | 0 | 0 | 1 | 0.02831 | 0.046551 | 1
6736 | 0 | 0.054708 | 0.94365 | 0 | 0 | 1 | 0 | 0.054708 | 1
6737 | 0 | 0.050847 | 0.94365 | 0 | 0 | 1 | 0 | 0.050847 | 1
6738 | 0 | 0.025786 | 0.94365 | 0 | 1 | 1 | 0 | 0.025786 | 1
6739 | 0 | 0.0065922 | 0.94365 | 0 | 1 | 1 | 0 | 0.0065922 | 1
6740 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6741 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6742 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6743 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6744 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6745 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6746 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6747 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6748 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6749 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6750 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6751 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6752 | 0.014559 | 0 | 0.94365 | 0 | 0 | 1 | 0.014559 | 0 | 1
6753 | 0.1589 | 0 | 0.94365 | 0 | 0 | 1 | 0.1589 | 0 | 1
6754 | 0.24584 | 0 | 0.94365 | 0 | 0 | 1 | 0.24584 | 0 | 1
6755 | 0.28246 | 0 | 0.94365 | 0 | 0 | 1 | 0.28246 | 0 | 1
6756 | 0.29427 | 0.036948 | 0.94365 | 0 | 0 | 1 | 0.29427 | 0.036948 | 1
6757 | 0.25502 | 0.076947 | 0.94365 | 0 | 0 | 1 | 0.25502 | 0.076947 | 1
6758 | 0.14414 | 0.081883 | 0.94365 | 0 | 0 | 1 | 0.14414 | 0.081883 | 1
6759 | 0.087091 | 0.077404 | 0.94365 | 0 | 0 | 1 | 0.087091 | 0.077404 | 1
6760 | 0.0089531 | 0.078817 | 0.94365 | 0 | 0 | 1 | 0.0089531 | 0.078817 | 1
6761 | 0 | 0.077965 | 0.94365 | 0 | 0 | 1 | 0 | 0.077965 | 1
6762 | 0 | 0.052918 | 0.94365 | 0 | 1 | 1 | 0 | 0.052918 | 1
6763 | 0 | 0.026303 | 0.94365 | 0 | 1 | 1 | 0 | 0.026303 | 1
6764 | 0 | 0.024221 | 0.94365 | 0 | 1 | 1 | 0 | 0.024221 | 1
6765 | 0 | 0.0069288 | 0.94365 | 0 | 1 | 1 | 0 | 0.0069288 | 1
6766 | 0 | 0.0086938 | 0.94365 | 0 | 0 | 1 | 0 | 0.0086938 | 1
6767 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6768 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6769 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6770 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6771 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6772 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6773 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6774 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6775 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6776 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6777 | 0.10338 | 0 | 0.94365 | 0 | 0 | 1 | 0.10338 | 0 | 1
6778 | 0.1405 | 0 | 0.94365 | 0 | 0 | 1 | 0.1405 | 0 | 1
6779 | 0.18003 | 0.0024028 | 0.94365 | 0 | 0 | 1 | 0.18003 | 0.0024028 | 1
6780 | 0.23425 | 0.047632 | 0.94365 | 0 | 0 | 1 | 0.23425 | 0.047632 | 1
6781 | 0.20521 | 0.08812 | 0.94365 | 0 | 0 | 1 | 0.20521 | 0.08812 | 1
6782 | 0.14519 | 0.091559 | 0.94365 | 0 | 0 | 1 | 0.14519 | 0.091559 | 1
6783 | 0.096235 | 0.092 | 0.94365 | 0 | 0 | 1 | 0.096235 | 0.092 | 1
6784 | 0.047118 | 0.087655 | 0.94365 | 0 | 0 | 1 | 0.047118 | 0.087655 | 1
6785 | 0 | 0.073333 | 0.94365 | 0 | 0 | 1 | 0 | 0.073333 | 1
6786 | 0 | 0.046955 | 0.94365 | 0 | 1 | 1 | 0 | 0.046955 | 1
6787 | 0 | 0.032814 | 0.94365 | 0 | 1 | 1 | 0 | 0.032814 | 1
6788 | 0 | 0.027304 | 0.94365 | 0 | 1 | 1 | 0 | 0.027304 | 1
6789 | 0 | 0.0038561 | 0.94365 | 0 | 1 | 1 | 0 | 0.0038561 | 1
6790 | 0 | 0.007258 | 0.94365 | 0 | 0 | 1 | 0 | 0.007258 | 1
6791 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6792 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6793 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6794 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6795 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6796 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6797 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6798 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6799 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6800 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6801 | 0.10688 | 0 | 0.94365 | 0 | 0 | 1 | 0.10688 | 0 | 1
6802 | 0.14743 | 0 | 0.94365 | 0 | 0 | 1 | 0.14743 | 0 | 1
6803 | 0.19358 | 0 | 0.94365 | 0 | 0 | 1 | 0.19358 | 0 | 1
6804 | 0.2281 | 0.018697 | 0.94365 | 0 | 0 | 1 | 0.2281 | 0.018697 | 1
6805 | 0.10491 | 0.045018 | 0.94365 | 0 | 0 | 1 | 0.10491 | 0.045018 | 1
6806 | 0.11158 | 0.055172 | 0.94365 | 0 | 0 | 1 | 0.11158 | 0.055172 | 1
6807 | 0.077048 | 0.057382 | 0.94365 | 0 | 0 | 1 | 0.077048 | 0.057382 | 1
6808 | 0 | 0.041077 | 0.94365 | 0 | 0 | 1 | 0 | 0.041077 | 1
6809 | 0 | 0.022533 | 0.94365 | 0 | 0 | 1 | 0 | 0.022533 | 1
6810 | 0 | 0.017277 | 0.94365 | 0 | 1 | 1 | 0 | 0.017277 | 1
6811 | 0 | 0.004211 | 0.94365 | 0 | 1 | 1 | 0 | 0.004211 | 1
6812 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6813 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6814 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6815 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6816 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6817 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6818 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6819 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6820 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6821 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6822 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6823 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6824 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6825 | 0.037368 | 0 | 0.94365 | 0 | 0 | 1 | 0.037368 | 0 | 1
6826 | 0.11083 | 0 | 0.94365 | 0 | 0 | 1 | 0.11083 | 0 | 1
6827 | 0.1959 | 0 | 0.94365 | 0 | 0 | 1 | 0.1959 | 0 | 1
6828 | 0.2245 | 0.0025338 | 0.94365 | 0 | 0 | 1 | 0.2245 | 0.0025338 | 1
6829 | 0.12617 | 0.012879 | 0.94365 | 0 | 0 | 1 | 0.12617 | 0.012879 | 1
6830 | 0.13697 | 0.012149 | 0.94365 | 0 | 0 | 1 | 0.13697 | 0.012149 | 1
6831 | 0.065229 | 0.023733 | 0.94365 | 0 | 0 | 1 | 0.065229 | 0.023733 | 1
6832 | 0 | 0.010209 | 0.94365 | 0 | 0 | 1 | 0 | 0.010209 | 1
6833 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6834 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6835 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6836 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6837 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6838 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6839 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6840 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6841 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6842 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6843 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6844 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6845 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6846 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6847 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6848 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6849 | 0.054675 | 0 | 0.94365 | 0 | 0 | 1 | 0.054675 | 0 | 1
6850 | 0.14751 | 0 | 0.94365 | 0 | 0 | 1 | 0.14751 | 0 | 1
6851 | 0.23661 | 0 | 0.94365 | 0 | 0 | 1 | 0.23661 | 0 | 1
6852 | 0.2057 | 0.0086076 | 0.94365 | 0 | 0 | 1 | 0.2057 | 0.0086076 | 1
6853 | 0.11887 | 0.016519 | 0.94365 | 0 | 0 | 1 | 0.11887 | 0.016519 | 1
6854 | 0.089075 | 0.016696 | 0.94365 | 0 | 0 | 1 | 0.089075 | 0.016696 | 1
6855 | 0.027123 | 0.022657 | 0.94365 | 0 | 0 | 1 | 0.027123 | 0.022657 | 1
6856 | 0 | 0.019825 | 0.94365 | 0 | 0 | 1 | 0 | 0.019825 | 1
6857 | 0 | 0.0061207 | 0.94365 | 0 | 0 | 1 | 0 | 0.0061207 | 1
6858 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6859 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6860 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6861 | 0 | 0 | 0.94365 | 0 | 1 | 1 | 0 | 0 | 1
6862 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6863 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6864 | 0 | 0 | 0.94365 | 0 | 0 | 1 | 0 | 0 | 1
6865 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6866 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6867 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6868 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6869 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6870 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6871 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6872 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6873 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6874 | 0.12095 | 0 | 1 | 0 | 0 | 1 | 0.12095 | 0 | 1
6875 | 0.20746 | 0.0056816 | 1 | 0 | 0 | 1 | 0.20746 | 0.0056816 | 1
6876 | 0.20868 | 0.03249 | 1 | 0 | 0 | 1 | 0.20868 | 0.03249 | 1
6877 | 0.15876 | 0.041112 | 1 | 0 | 0 | 1 | 0.15876 | 0.041112 | 1
6878 | 0.08264 | 0.03367 | 1 | 0 | 0 | 1 | 0.08264 | 0.03367 | 1
6879 | 0.081505 | 0.042053 | 1 | 0 | 0 | 1 | 0.081505 | 0.042053 | 1
6880 | 0.013298 | 0.047767 | 1 | 0 | 0 | 1 | 0.013298 | 0.047767 | 1
6881 | 0 | 0.052637 | 1 | 0 | 0 | 1 | 0 | 0.052637 | 1
6882 | 0 | 0.038952 | 1 | 0 | 1 | 1 | 0 | 0.038952 | 1
6883 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6884 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6885 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6886 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6887 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6888 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6889 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6890 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6891 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6892 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6893 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6894 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6895 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6896 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6897 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6898 | 0.17905 | 0 | 1 | 0 | 0 | 1 | 0.17905 | 0 | 1
6899 | 0.23432 | 0.027438 | 1 | 0 | 0 | 1 | 0.23432 | 0.027438 | 1
6900 | 0.24443 | 0.044931 | 1 | 0 | 0 | 1 | 0.24443 | 0.044931 | 1
6901 | 0.20108 | 0.054037 | 1 | 0 | 0 | 1 | 0.20108 | 0.054037 | 1
6902 | 0.11395 | 0.055499 | 1 | 0 | 0 | 1 | 0.11395 | 0.055499 | 1
6903 | 0.10159 | 0.064406 | 1 | 0 | 0 | 1 | 0.10159 | 0.064406 | 1
6904 | 0.02703 | 0.078752 | 1 | 0 | 0 | 1 | 0.02703 | 0.078752 | 1
6905 | 0 | 0.08021 | 1 | 0 | 0 | 1 | 0 | 0.08021 | 1
6906 | 0 | 0.071236 | 1 | 0 | 1 | 1 | 0 | 0.071236 | 1
6907 | 0 | 0.019012 | 1 | 0 | 1 | 1 | 0 | 0.019012 | 1
6908 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6909 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
6910 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6911 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6912 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6913 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6914 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6915 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6916 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6917 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6918 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6919 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6920 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6921 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6922 | 0.13044 | 0.0075976 | 1 | 0 | 0 | 1 | 0.13044 | 0.0075976 | 1
6923 | 0.23576 | 0.036973 | 1 | 0 | 0 | 1 | 0.23576 | 0.036973 | 1
6924 | 0.26141 | 0.044532 | 1 | 0 | 0 | 1 | 0.26141 | 0.044532 | 1
6925 | 0.21845 | 0.062399 | 1 | 0 | 0 | 1 | 0.21845 | 0.062399 | 1
6926 | 0.15286 | 0.048148 | 1 | 0 | 0 | 1 | 0.15286 | 0.048148 | 1
6927 | 0.096108 | 0.065241 | 1 | 0 | 0 | 1 | 0.096108 | 0.065241 | 1
6928 | 0.044754 | 0.08846 | 1 | 0 | 0 | 1 | 0.044754 | 0.08846 | 1
6929 | 0 | 0.090426 | 1 | 0 | 0 | 1 | 0 | 0.090426 | 1
6930 | 0 | 0.08199 | 1 | 0 | 1 | 1 | 0 | 0.08199 | 1
6931 | 0 | 0.053566 | 1 | 0 | 1 | 1 | 0 | 0.053566 | 1
6932 | 0 | 0.027902 | 1 | 0 | 1 | 1 | 0 | 0.027902 | 1
6933 | 0 | 0.025065 | 1 | 0 | 1 | 1 | 0 | 0.025065 | 1
6934 | 0 | 0.02951 | 1 | 0 | 0 | 1 | 0 | 0.02951 | 1
6935 | 0 | 0.033753 | 1 | 0 | 0 | 1 | 0 | 0.033753 | 1
6936 | 0 | 0.038644 | 1 | 0 | 0 | 1 | 0 | 0.038644 | 1
6937 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6938 | 0 | 0.012147 | 1 | 0 | 0 | 1 | 0 | 0.012147 | 1
6939 | 0 | 0.0063299 | 1 | 0 | 0 | 1 | 0 | 0.0063299 | 1
6940 | 0 | 0.015107 | 1 | 0 | 0 | 1 | 0 | 0.015107 | 1
6941 | 0 | 0.0059973 | 1 | 0 | 0 | 1 | 0 | 0.0059973 | 1
6942 | 0 | 0.019854 | 1 | 0 | 0 | 1 | 0 | 0.019854 | 1
6943 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6944 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6945 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6946 | 0.052362 | 0.013399 | 1 | 0 | 0 | 1 | 0.052362 | 0.013399 | 1
6947 | 0.082992 | 0.045188 | 1 | 0 | 0 | 1 | 0.082992 | 0.045188 | 1
6948 | 0.13248 | 0.050555 | 1 | 0 | 0 | 1 | 0.13248 | 0.050555 | 1
6949 | 0.13418 | 0.063005 | 1 | 0 | 0 | 1 | 0.13418 | 0.063005 | 1
6950 | 0.084113 | 0.030797 | 1 | 0 | 0 | 1 | 0.084113 | 0.030797 | 1
6951 | 0.029448 | 0.055513 | 1 | 0 | 0 | 1 | 0.029448 | 0.055513 | 1
6952 | 0 | 0.082505 | 1 | 0 | 0 | 1 | 0 | 0.082505 | 1
6953 | 0 | 0.079676 | 1 | 0 | 0 | 1 | 0 | 0.079676 | 1
6954 | 0 | 0.073953 | 1 | 0 | 1 | 1 | 0 | 0.073953 | 1
6955 | 0 | 0.054284 | 1 | 0 | 1 | 1 | 0 | 0.054284 | 1
6956 | 0 | 0.041226 | 1 | 0 | 1 | 1 | 0 | 0.041226 | 1
6957 | 0 | 0.040812 | 1 | 0 | 1 | 1 | 0 | 0.040812 | 1
6958 | 0 | 0.054056 | 1 | 0 | 0 | 1 | 0 | 0.054056 | 1
6959 | 0 | 0.034806 | 1 | 0 | 0 | 1 | 0 | 0.034806 | 1
6960 | 0 | 0.022303 | 1 | 0 | 0 | 1 | 0 | 0.022303 | 1
6961 | 0 | 0.024319 | 1 | 0 | 0 | 1 | 0 | 0.024319 | 1
6962 | 0 | 0.0087674 | 1 | 0 | 0 | 1 | 0 | 0.0087674 | 1
6963 | 0 | 0.0035312 | 1 | 0 | 0 | 1 | 0 | 0.0035312 | 1
6964 | 0 | 0.0053819 | 1 | 0 | 0 | 1 | 0 | 0.0053819 | 1
6965 | 0 | 0.012617 | 1 | 0 | 0 | 1 | 0 | 0.012617 | 1
6966 | 0 | 0.025511 | 1 | 0 | 0 | 1 | 0 | 0.025511 | 1
6967 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6968 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6969 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6970 | 0 | 0.0062517 | 1 | 0 | 0 | 1 | 0 | 0.0062517 | 1
6971 | 0 | 0.022974 | 1 | 0 | 0 | 1 | 0 | 0.022974 | 1
6972 | 0 | 0.027648 | 1 | 0 | 0 | 1 | 0 | 0.027648 | 1
6973 | 0 | 0.025747 | 1 | 0 | 0 | 1 | 0 | 0.025747 | 1
6974 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6975 | 0 | 0.011361 | 1 | 0 | 0 | 1 | 0 | 0.011361 | 1
6976 | 0 | 0.035872 | 1 | 0 | 0 | 1 | 0 | 0.035872 | 1
6977 | 0 | 0.053478 | 1 | 0 | 0 | 1 | 0 | 0.053478 | 1
6978 | 0 | 0.039598 | 1 | 0 | 1 | 1 | 0 | 0.039598 | 1
6979 | 0 | 0.030199 | 1 | 0 | 1 | 1 | 0 | 0.030199 | 1
6980 | 0 | 0.036656 | 1 | 0 | 1 | 1 | 0 | 0.036656 | 1
6981 | 0 | 0.056389 | 1 | 0 | 1 | 1 | 0 | 0.056389 | 1
6982 | 0 | 0.057211 | 1 | 0 | 0 | 1 | 0 | 0.057211 | 1
6983 | 0 | 0.034405 | 1 | 0 | 0 | 1 | 0 | 0.034405 | 1
6984 | 0 | 0.014926 | 1 | 0 | 0 | 1 | 0 | 0.014926 | 1
6985 | 0 | 0.015698 | 1 | 0 | 0 | 1 | 0 | 0.015698 | 1
6986 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6987 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6988 | 0 | 0.01046 | 1 | 0 | 0 | 1 | 0 | 0.01046 | 1
6989 | 0 | 0.0056987 | 1 | 0 | 0 | 1 | 0 | 0.0056987 | 1
6990 | 0 | 0.0068157 | 1 | 0 | 0 | 1 | 0 | 0.0068157 | 1
6991 | 0 | 0.0022029 | 1 | 0 | 0 | 1 | 0 | 0.0022029 | 1
6992 | 0 | 0.016846 | 1 | 0 | 0 | 1 | 0 | 0.016846 | 1
6993 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
6994 | 0 | 0.0092301 | 1 | 0 | 0 | 1 | 0 | 0.0092301 | 1
6995 | 0 | 0.039405 | 1 | 0 | 0 | 1 | 0 | 0.039405 | 1
6996 | 0 | 0.054019 | 1 | 0 | 0 | 1 | 0 | 0.054019 | 1
6997 | 0.0050138 | 0.033763 | 1 | 0 | 0 | 1 | 0.0050138 | 0.033763 | 1
6998 | 0 | 0.017156 | 1 | 0 | 0 | 1 | 0 | 0.017156 | 1
6999 | 0 | 0.022796 | 1 | 0 | 0 | 1 | 0 | 0.022796 | 1
7000 | 0 | 0.01439 | 1 | 0 | 0 | 1 | 0 | 0.01439 | 1
7001 | 0 | 0.043983 | 1 | 0 | 0 | 1 | 0 | 0.043983 | 1
7002 | 0 | 0.046304 | 1 | 0 | 1 | 1 | 0 | 0.046304 | 1
7003 | 0 | 0.036731 | 1 | 0 | 1 | 1 | 0 | 0.036731 | 1
7004 | 0 | 0.043316 | 1 | 0 | 1 | 1 | 0 | 0.043316 | 1
7005 | 0 | 0.058615 | 1 | 0 | 1 | 1 | 0 | 0.058615 | 1
7006 | 0 | 0.043274 | 1 | 0 | 0 | 1 | 0 | 0.043274 | 1
7007 | 0 | 0.023549 | 1 | 0 | 0 | 1 | 0 | 0.023549 | 1
7008 | 0 | 0.0065176 | 1 | 0 | 0 | 1 | 0 | 0.0065176 | 1
7009 | 0 | 0.021598 | 1 | 0 | 0 | 1 | 0 | 0.021598 | 1
7010 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7011 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7012 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7013 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7014 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7015 | 0 | 0.017922 | 1 | 0 | 0 | 1 | 0 | 0.017922 | 1
7016 | 0 | 0.013346 | 1 | 0 | 0 | 1 | 0 | 0.013346 | 1
7017 | 0.016203 | 0 | 1 | 0 | 0 | 1 | 0.016203 | 0 | 1
7018 | 0.092688 | 0.013722 | 1 | 0 | 0 | 1 | 0.092688 | 0.013722 | 1
7019 | 0.095542 | 0.045962 | 1 | 0 | 0 | 1 | 0.095542 | 0.045962 | 1
7020 | 0.08641 | 0.065809 | 1 | 0 | 0 | 1 | 0.08641 | 0.065809 | 1
7021 | 0.090817 | 0.042208 | 1 | 0 | 0 | 1 | 0.090817 | 0.042208 | 1
7022 | 0.054128 | 0.061027 | 1 | 0 | 0 | 1 | 0.054128 | 0.061027 | 1
7023 | 0.032749 | 0.06074 | 1 | 0 | 0 | 1 | 0.032749 | 0.06074 | 1
7024 | 0.0085179 | 0.027598 | 1 | 0 | 0 | 1 | 0.0085179 | 0.027598 | 1
7025 | 0 | 0.0479 | 1 | 0 | 0 | 1 | 0 | 0.0479 | 1
7026 | 0 | 0.044247 | 1 | 0 | 1 | 1 | 0 | 0.044247 | 1
7027 | 0 | 0.02145 | 1 | 0 | 1 | 1 | 0 | 0.02145 | 1
7028 | 0 | 0.027268 | 1 | 0 | 1 | 1 | 0 | 0.027268 | 1
7029 | 0 | 0.052242 | 1 | 0 | 1 | 1 | 0 | 0.052242 | 1
7030 | 0 | 0.037909 | 1 | 0 | 0 | 1 | 0 | 0.037909 | 1
7031 | 0 | 0.030017 | 1 | 0 | 0 | 1 | 0 | 0.030017 | 1
7032 | 0 | 0.011382 | 1 | 0 | 0 | 1 | 0 | 0.011382 | 1
7033 | 0 | 0.0083857 | 1 | 0 | 0 | 1 | 0 | 0.0083857 | 1
7034 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7035 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7036 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7037 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7038 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7039 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7040 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7041 | 0.1076 | 0 | 1 | 0 | 0 | 1 | 0.1076 | 0 | 1
7042 | 0.25142 | 0.0002384 | 1 | 0 | 0 | 1 | 0.25142 | 0.0002384 | 1
7043 | 0.30723 | 0.033708 | 1 | 0 | 0 | 1 | 0.30723 | 0.033708 | 1
7044 | 0.28613 | 0.04436 | 1 | 0 | 0 | 1 | 0.28613 | 0.04436 | 1
7045 | 0.24548 | 0.045475 | 1 | 0 | 0 | 1 | 0.24548 | 0.045475 | 1
7046 | 0.2414 | 0.061305 | 1 | 0 | 0 | 1 | 0.2414 | 0.061305 | 1
7047 | 0.19155 | 0.071346 | 1 | 0 | 0 | 1 | 0.19155 | 0.071346 | 1
7048 | 0.093931 | 0.031462 | 1 | 0 | 0 | 1 | 0.093931 | 0.031462 | 1
7049 | 0 | 0.031183 | 1 | 0 | 0 | 1 | 0 | 0.031183 | 1
7050 | 0 | 0.025257 | 1 | 0 | 1 | 1 | 0 | 0.025257 | 1
7051 | 0 | 0.00091595 | 1 | 0 | 1 | 1 | 0 | 0.00091595 | 1
7052 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
7053 | 0 | 0.0042516 | 1 | 0 | 1 | 1 | 0 | 0.0042516 | 1
7054 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7055 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7056 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7057 | 0 | 0.0021884 | 1 | 0 | 0 | 1 | 0 | 0.0021884 | 1
7058 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7059 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7060 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7061 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7062 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7063 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7064 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7065 | 0.085248 | 0 | 1 | 0 | 0 | 1 | 0.085248 | 0 | 1
7066 | 0.20773 | 0 | 1 | 0 | 0 | 1 | 0.20773 | 0 | 1
7067 | 0.19216 | 0.0053965 | 1 | 0 | 0 | 1 | 0.19216 | 0.0053965 | 1
7068 | 0.18127 | 0.013038 | 1 | 0 | 0 | 1 | 0.18127 | 0.013038 | 1
7069 | 0.074039 | 0.022181 | 1 | 0 | 0 | 1 | 0.074039 | 0.022181 | 1
7070 | 0.084359 | 0.035971 | 1 | 0 | 0 | 1 | 0.084359 | 0.035971 | 1
7071 | 0.07159 | 0.051993 | 1 | 0 | 0 | 1 | 0.07159 | 0.051993 | 1
7072 | 0 | 0.043171 | 1 | 0 | 0 | 1 | 0 | 0.043171 | 1
7073 | 0 | 0.026671 | 1 | 0 | 0 | 1 | 0 | 0.026671 | 1
7074 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
7075 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
7076 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
7077 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1
7078 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7079 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7080 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
7081 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7082 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7083 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7084 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7085 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7086 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7087 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7088 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7089 | 0.040716 | 0 | 0.94371 | 0 | 0 | 1 | 0.040716 | 0 | 1
7090 | 0.18068 | 0 | 0.94371 | 0 | 0 | 1 | 0.18068 | 0 | 1
7091 | 0.16891 | 0 | 0.94371 | 0 | 0 | 1 | 0.16891 | 0 | 1
7092 | 0.17504 | 0.0049148 | 0.94371 | 0 | 0 | 1 | 0.17504 | 0.0049148 | 1
7093 | 0.094996 | 0.0086617 | 0.94371 | 0 | 0 | 1 | 0.094996 | 0.0086617 | 1
7094 | 0.10517 | 0.0056974 | 0.94371 | 0 | 0 | 1 | 0.10517 | 0.0056974 | 1
7095 | 0.037123 | 0.014458 | 0.94371 | 0 | 0 | 1 | 0.037123 | 0.014458 | 1
7096 | 0 | 0.019293 | 0.94371 | 0 | 0 | 1 | 0 | 0.019293 | 1
7097 | 0 | 0.0083321 | 0.94371 | 0 | 0 | 1 | 0 | 0.0083321 | 1
7098 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7099 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7100 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7101 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7102 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7103 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7104 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7105 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7106 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7107 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7108 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7109 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7110 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7111 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7112 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7113 | 0.023939 | 0 | 0.94371 | 0 | 0 | 1 | 0.023939 | 0 | 1
7114 | 0.20812 | 0 | 0.94371 | 0 | 0 | 1 | 0.20812 | 0 | 1
7115 | 0.16021 | 0 | 0.94371 | 0 | 0 | 1 | 0.16021 | 0 | 1
7116 | 0.11505 | 0.022699 | 0.94371 | 0 | 0 | 1 | 0.11505 | 0.022699 | 1
7117 | 0.11024 | 0.021637 | 0.94371 | 0 | 0 | 1 | 0.11024 | 0.021637 | 1
7118 | 0.080381 | 0.021188 | 0.94371 | 0 | 0 | 1 | 0.080381 | 0.021188 | 1
7119 | 0.025482 | 0.029956 | 0.94371 | 0 | 0 | 1 | 0.025482 | 0.029956 | 1
7120 | 0 | 0.039082 | 0.94371 | 0 | 0 | 1 | 0 | 0.039082 | 1
7121 | 0 | 0.029794 | 0.94371 | 0 | 0 | 1 | 0 | 0.029794 | 1
7122 | 0 | 0.024762 | 0.94371 | 0 | 1 | 1 | 0 | 0.024762 | 1
7123 | 0 | 0.01199 | 0.94371 | 0 | 1 | 1 | 0 | 0.01199 | 1
7124 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7125 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7126 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7127 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7128 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7129 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7130 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7131 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7132 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7133 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7134 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7135 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7136 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7137 | 0.050543 | 0 | 0.94371 | 0 | 0 | 1 | 0.050543 | 0 | 1
7138 | 0.27575 | 0 | 0.94371 | 0 | 0 | 1 | 0.27575 | 0 | 1
7139 | 0.28772 | 0 | 0.94371 | 0 | 0 | 1 | 0.28772 | 0 | 1
7140 | 0.24772 | 0.0038817 | 0.94371 | 0 | 0 | 1 | 0.24772 | 0.0038817 | 1
7141 | 0.29616 | 0 | 0.94371 | 0 | 0 | 1 | 0.29616 | 0 | 1
7142 | 0.20929 | 0 | 0.94371 | 0 | 0 | 1 | 0.20929 | 0 | 1
7143 | 0.14572 | 0 | 0.94371 | 0 | 0 | 1 | 0.14572 | 0 | 1
7144 | 0.0146 | 0.021634 | 0.94371 | 0 | 0 | 1 | 0.0146 | 0.021634 | 1
7145 | 0 | 0.01877 | 0.94371 | 0 | 0 | 1 | 0 | 0.01877 | 1
7146 | 0 | 0.014434 | 0.94371 | 0 | 1 | 1 | 0 | 0.014434 | 1
7147 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7148 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7149 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7150 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7151 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7152 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7153 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7154 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7155 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7156 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7157 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7158 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7159 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7160 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7161 | 0.059546 | 0 | 0.94371 | 0 | 0 | 1 | 0.059546 | 0 | 1
7162 | 0.24333 | 0 | 0.94371 | 0 | 0 | 1 | 0.24333 | 0 | 1
7163 | 0.24393 | 0 | 0.94371 | 0 | 0 | 1 | 0.24393 | 0 | 1
7164 | 0.16668 | 0 | 0.94371 | 0 | 0 | 1 | 0.16668 | 0 | 1
7165 | 0.26466 | 0 | 0.94371 | 0 | 0 | 1 | 0.26466 | 0 | 1
7166 | 0.14884 | 0 | 0.94371 | 0 | 0 | 1 | 0.14884 | 0 | 1
7167 | 0.11425 | 0 | 0.94371 | 0 | 0 | 1 | 0.11425 | 0 | 1
7168 | 0.0074556 | 0.012524 | 0.94371 | 0 | 0 | 1 | 0.0074556 | 0.012524 | 1
7169 | 0 | 0.015993 | 0.94371 | 0 | 0 | 1 | 0 | 0.015993 | 1
7170 | 0 | 0.012093 | 0.94371 | 0 | 1 | 1 | 0 | 0.012093 | 1
7171 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7172 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7173 | 0 | 0 | 0.94371 | 0 | 1 | 1 | 0 | 0 | 1
7174 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7175 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7176 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7177 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7178 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7179 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7180 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7181 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7182 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7183 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7184 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7185 | 0.067209 | 0 | 0.94371 | 0 | 0 | 1 | 0.067209 | 0 | 1
7186 | 0.18116 | 0 | 0.94371 | 0 | 0 | 1 | 0.18116 | 0 | 1
7187 | 0.25189 | 0 | 0.94371 | 0 | 0 | 1 | 0.25189 | 0 | 1
7188 | 0.24727 | 0.0031003 | 0.94371 | 0 | 0 | 1 | 0.24727 | 0.0031003 | 1
7189 | 0.28711 | 0.019643 | 0.94371 | 0 | 0 | 1 | 0.28711 | 0.019643 | 1
7190 | 0.13372 | 0 | 0.94371 | 0 | 0 | 1 | 0.13372 | 0 | 1
7191 | 0.033525 | 0.016872 | 0.94371 | 0 | 0 | 1 | 0.033525 | 0.016872 | 1
7192 | 0 | 0.025152 | 0.94371 | 0 | 0 | 1 | 0 | 0.025152 | 1
7193 | 0 | 0.047886 | 0.94371 | 0 | 0 | 1 | 0 | 0.047886 | 1
7194 | 0 | 0.046228 | 0.94371 | 0 | 1 | 1 | 0 | 0.046228 | 1
7195 | 0 | 0.0096504 | 0.94371 | 0 | 1 | 1 | 0 | 0.0096504 | 1
7196 | 0 | 0.0092316 | 0.94371 | 0 | 1 | 1 | 0 | 0.0092316 | 1
7197 | 0 | 0.016149 | 0.94371 | 0 | 1 | 1 | 0 | 0.016149 | 1
7198 | 0 | 0.0027018 | 0.94371 | 0 | 0 | 1 | 0 | 0.0027018 | 1
7199 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7200 | 0 | 0 | 0.94371 | 0 | 0 | 1 | 0 | 0 | 1
7201 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7202 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7203 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7204 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7205 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7206 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7207 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7208 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7209 | 0.0012356 | 0 | 0.92838 | 0 | 0 | 1 | 0.0012356 | 0 | 1
7210 | 0.075111 | 0 | 0.92838 | 0 | 0 | 1 | 0.075111 | 0 | 1
7211 | 0.15367 | 0.00099146 | 0.92838 | 0 | 0 | 1 | 0.15367 | 0.00099146 | 1
7212 | 0.14319 | 0.0098904 | 0.92838 | 0 | 0 | 1 | 0.14319 | 0.0098904 | 1
7213 | 0.1847 | 0.030489 | 0.92838 | 0 | 0 | 1 | 0.1847 | 0.030489 | 1
7214 | 0.099693 | 0.016855 | 0.92838 | 0 | 0 | 1 | 0.099693 | 0.016855 | 1
7215 | 0 | 0.042401 | 0.92838 | 0 | 0 | 1 | 0 | 0.042401 | 1
7216 | 0 | 0.024811 | 0.92838 | 0 | 0 | 1 | 0 | 0.024811 | 1
7217 | 0 | 0.031825 | 0.92838 | 0 | 0 | 1 | 0 | 0.031825 | 1
7218 | 0 | 0.02654 | 0.92838 | 0 | 1 | 1 | 0 | 0.02654 | 1
7219 | 0 | 0.0016691 | 0.92838 | 0 | 1 | 1 | 0 | 0.0016691 | 1
7220 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7221 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7222 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7223 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7224 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7225 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7226 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7227 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7228 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7229 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7230 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7231 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7232 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7233 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7234 | 0.012623 | 0 | 0.92838 | 0 | 0 | 1 | 0.012623 | 0 | 1
7235 | 0.12042 | 0 | 0.92838 | 0 | 0 | 1 | 0.12042 | 0 | 1
7236 | 0.12841 | 0 | 0.92838 | 0 | 0 | 1 | 0.12841 | 0 | 1
7237 | 0.097343 | 0.0019348 | 0.92838 | 0 | 0 | 1 | 0.097343 | 0.0019348 | 1
7238 | 0.039467 | 0 | 0.92838 | 0 | 0 | 1 | 0.039467 | 0 | 1
7239 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7240 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7241 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7242 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7243 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7244 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7245 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7246 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7247 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7248 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7249 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7250 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7251 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7252 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7253 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7254 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7255 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7256 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7257 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7258 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7259 | 0.081965 | 0 | 0.92838 | 0 | 0 | 1 | 0.081965 | 0 | 1
7260 | 0.094389 | 0 | 0.92838 | 0 | 0 | 1 | 0.094389 | 0 | 1
7261 | 0.073664 | 0 | 0.92838 | 0 | 0 | 1 | 0.073664 | 0 | 1
7262 | 0.041289 | 0 | 0.92838 | 0 | 0 | 1 | 0.041289 | 0 | 1
7263 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7264 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7265 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7266 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7267 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7268 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7269 | 0 | 0 | 0.92838 | 0 | 1 | 1 | 0 | 0 | 1
7270 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7271 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7272 | 0 | 0 | 0.92838 | 0 | 0 | 1 | 0 | 0 | 1
7273 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7274 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7275 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7276 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7277 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7278 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7279 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7280 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7281 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7282 | 0.072889 | 0 | 0.98467 | 0 | 0 | 1 | 0.072889 | 0 | 1
7283 | 0.1755 | 0 | 0.98467 | 0 | 0 | 1 | 0.1755 | 0 | 1
7284 | 0.21291 | 0 | 0.98467 | 0 | 0 | 1 | 0.21291 | 0 | 1
7285 | 0.18301 | 0 | 0.98467 | 0 | 0 | 1 | 0.18301 | 0 | 1
7286 | 0.10652 | 0 | 0.98467 | 0 | 0 | 1 | 0.10652 | 0 | 1
7287 | 0.046477 | 0 | 0.98467 | 0 | 0 | 1 | 0.046477 | 0 | 1
7288 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7289 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7290 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7291 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7292 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7293 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7294 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7295 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7296 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7297 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7298 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7299 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7300 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7301 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7302 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7303 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7304 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7305 | 0.049173 | 0 | 0.98467 | 0 | 0 | 1 | 0.049173 | 0 | 1
7306 | 0.18398 | 0 | 0.98467 | 0 | 0 | 1 | 0.18398 | 0 | 1
7307 | 0.24314 | 0 | 0.98467 | 0 | 0 | 1 | 0.24314 | 0 | 1
7308 | 0.35561 | 0.0070096 | 0.98467 | 0 | 0 | 1 | 0.35561 | 0.0070096 | 1
7309 | 0.3636 | 0.027845 | 0.98467 | 0 | 0 | 1 | 0.3636 | 0.027845 | 1
7310 | 0.26975 | 0.017541 | 0.98467 | 0 | 0 | 1 | 0.26975 | 0.017541 | 1
7311 | 0.17385 | 0 | 0.98467 | 0 | 0 | 1 | 0.17385 | 0 | 1
7312 | 0.059285 | 0 | 0.98467 | 0 | 0 | 1 | 0.059285 | 0 | 1
7313 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7314 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7315 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7316 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7317 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7318 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7319 | 0 | 0.011555 | 0.98467 | 0 | 0 | 1 | 0 | 0.011555 | 1
7320 | 0 | 0.0017427 | 0.98467 | 0 | 0 | 1 | 0 | 0.0017427 | 1
7321 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7322 | 0 | 0.010789 | 0.98467 | 0 | 0 | 1 | 0 | 0.010789 | 1
7323 | 0 | 0.0077106 | 0.98467 | 0 | 0 | 1 | 0 | 0.0077106 | 1
7324 | 0 | 0.006485 | 0.98467 | 0 | 0 | 1 | 0 | 0.006485 | 1
7325 | 0 | 0.014164 | 0.98467 | 0 | 0 | 1 | 0 | 0.014164 | 1
7326 | 0 | 0.0052329 | 0.98467 | 0 | 0 | 1 | 0 | 0.0052329 | 1
7327 | 0 | 0.0072483 | 0.98467 | 0 | 0 | 1 | 0 | 0.0072483 | 1
7328 | 0 | 0.031743 | 0.98467 | 0 | 0 | 1 | 0 | 0.031743 | 1
7329 | 0.078683 | 0.036587 | 0.98467 | 0 | 0 | 1 | 0.078683 | 0.036587 | 1
7330 | 0.21213 | 0.040395 | 0.98467 | 0 | 0 | 1 | 0.21213 | 0.040395 | 1
7331 | 0.24193 | 0.055952 | 0.98467 | 0 | 0 | 1 | 0.24193 | 0.055952 | 1
7332 | 0.32501 | 0.061203 | 0.98467 | 0 | 0 | 1 | 0.32501 | 0.061203 | 1
7333 | 0.30191 | 0.071061 | 0.98467 | 0 | 0 | 1 | 0.30191 | 0.071061 | 1
7334 | 0.25519 | 0.064705 | 0.98467 | 0 | 0 | 1 | 0.25519 | 0.064705 | 1
7335 | 0.23478 | 0.065922 | 0.98467 | 0 | 0 | 1 | 0.23478 | 0.065922 | 1
7336 | 0.083087 | 0.045089 | 0.98467 | 0 | 0 | 1 | 0.083087 | 0.045089 | 1
7337 | 0 | 0.026611 | 0.98467 | 0 | 0 | 1 | 0 | 0.026611 | 1
7338 | 0 | 0.020566 | 0.98467 | 0 | 1 | 1 | 0 | 0.020566 | 1
7339 | 0 | 0 | 0.98467 | 0 | 1 | 1 | 0 | 0 | 1
7340 | 0 | 0.015434 | 0.98467 | 0 | 1 | 1 | 0 | 0.015434 | 1
7341 | 0 | 0.013596 | 0.98467 | 0 | 1 | 1 | 0 | 0.013596 | 1
7342 | 0 | 0.029703 | 0.98467 | 0 | 0 | 1 | 0 | 0.029703 | 1
7343 | 0 | 0.043268 | 0.98467 | 0 | 0 | 1 | 0 | 0.043268 | 1
7344 | 0 | 0.032594 | 0.98467 | 0 | 0 | 1 | 0 | 0.032594 | 1
7345 | 0 | 0.014749 | 0.98467 | 0 | 0 | 1 | 0 | 0.014749 | 1
7346 | 0 | 0.010058 | 0.98467 | 0 | 0 | 1 | 0 | 0.010058 | 1
7347 | 0 | 0 | 0.98467 | 0 | 0 | 1 | 0 | 0 | 1
7348 | 0 | 0.014626 | 0.98467 | 0 | 0 | 1 | 0 | 0.014626 | 1
7349 | 0 | 0.019367 | 0.98467 | 0 | 0 | 1 | 0 | 0.019367 | 1
7350 | 0 | 0.020039 | 0.98467 | 0 | 0 | 1 | 0 | 0.020039 | 1
7351 | 0 | 0.045867 | 0.98467 | 0 | 0 | 1 | 0 | 0.045867 | 1
7352 | 0 | 0.06652 | 0.98467 | 0 | 0 | 1 | 0 | 0.06652 | 1
7353 | 0.039612 | 0.067438 | 0.98467 | 0 | 0 | 1 | 0.039612 | 0.067438 | 1
7354 | 0.16295 | 0.071112 | 0.98467 | 0 | 0 | 1 | 0.16295 | 0.071112 | 1
7355 | 0.17459 | 0.094429 | 0.98467 | 0 | 0 | 1 | 0.17459 | 0.094429 | 1
7356 | 0.26362 | 0.09651 | 0.98467 | 0 | 0 | 1 | 0.26362 | 0.09651 | 1
7357 | 0.26066 | 0.11433 | 0.98467 | 0 | 0 | 1 | 0.26066 | 0.11433 | 1
7358 | 0.2555 | 0.10911 | 0.98467 | 0 | 0 | 1 | 0.2555 | 0.10911 | 1
7359 | 0.26165 | 0.11014 | 0.98467 | 0 | 0 | 1 | 0.26165 | 0.11014 | 1
7360 | 0.14046 | 0.08866 | 0.98467 | 0 | 0 | 1 | 0.14046 | 0.08866 | 1
7361 | 0 | 0.067016 | 0.98467 | 0 | 0 | 1 | 0 | 0.067016 | 1
7362 | 0 | 0.058805 | 0.98467 | 0 | 1 | 1 | 0 | 0.058805 | 1
7363 | 0 | 0.036269 | 0.98467 | 0 | 1 | 1 | 0 | 0.036269 | 1
7364 | 0 | 0.043944 | 0.98467 | 0 | 1 | 1 | 0 | 0.043944 | 1
7365 | 0 | 0.036131 | 0.98467 | 0 | 1 | 1 | 0 | 0.036131 | 1
7366 | 0 | 0.05671 | 0.98467 | 0 | 0 | 1 | 0 | 0.05671 | 1
7367 | 0 | 0.058488 | 0.98467 | 0 | 0 | 1 | 0 | 0.058488 | 1
7368 | 0 | 0.063277 | 0.98467 | 0 | 0 | 1 | 0 | 0.063277 | 1
7369 | 0 | 0.026706 | 0.89861 | 0 | 0 | 1 | 0 | 0.026706 | 1
7370 | 0 | 0.047593 | 0.89861 | 0 | 0 | 1 | 0 | 0.047593 | 1
7371 | 0 | 0.026943 | 0.89861 | 0 | 0 | 1 | 0 | 0.026943 | 1
7372 | 0 | 0.028876 | 0.89861 | 0 | 0 | 1 | 0 | 0.028876 | 1
7373 | 0 | 0.038277 | 0.89861 | 0 | 0 | 1 | 0 | 0.038277 | 1
7374 | 0 | 0.03551 | 0.89861 | 0 | 0 | 1 | 0 | 0.03551 | 1
7375 | 0 | 0.065605 | 0.89861 | 0 | 0 | 1 | 0 | 0.065605 | 1
7376 | 0 | 0.0813 | 0.89861 | 0 | 0 | 1 | 0 | 0.0813 | 1
7377 | 0.021569 | 0.093599 | 0.89861 | 0 | 0 | 1 | 0.021569 | 0.093599 | 1
7378 | 0.14191 | 0.11147 | 0.89861 | 0 | 0 | 1 | 0.14191 | 0.11147 | 1
7379 | 0.19617 | 0.12784 | 0.89861 | 0 | 0 | 1 | 0.19617 | 0.12784 | 1
7380 | 0.2432 | 0.14143 | 0.89861 | 0 | 0 | 1 | 0.2432 | 0.14143 | 1
7381 | 0.21619 | 0.16498 | 0.89861 | 0 | 0 | 1 | 0.21619 | 0.16498 | 1
7382 | 0.24049 | 0.16324 | 0.89861 | 0 | 0 | 1 | 0.24049 | 0.16324 | 1
7383 | 0.22978 | 0.14759 | 0.89861 | 0 | 0 | 1 | 0.22978 | 0.14759 | 1
7384 | 0.10792 | 0.1294 | 0.89861 | 0 | 0 | 1 | 0.10792 | 0.1294 | 1
7385 | 0 | 0.11857 | 0.89861 | 0 | 0 | 1 | 0 | 0.11857 | 1
7386 | 0 | 0.093907 | 0.89861 | 0 | 1 | 1 | 0 | 0.093907 | 1
7387 | 0 | 0.065552 | 0.89861 | 0 | 1 | 1 | 0 | 0.065552 | 1
7388 | 0 | 0.071612 | 0.89861 | 0 | 1 | 1 | 0 | 0.071612 | 1
7389 | 0 | 0.072461 | 0.89861 | 0 | 1 | 1 | 0 | 0.072461 | 1
7390 | 0 | 0.08583 | 0.89861 | 0 | 0 | 1 | 0 | 0.08583 | 1
7391 | 0 | 0.059518 | 0.89861 | 0 | 0 | 1 | 0 | 0.059518 | 1
7392 | 0 | 0.050754 | 0.89861 | 0 | 0 | 1 | 0 | 0.050754 | 1
7393 | 0 | 0.050008 | 0.89861 | 0 | 0 | 1 | 0 | 0.050008 | 1
7394 | 0 | 0.026587 | 0.89861 | 0 | 0 | 1 | 0 | 0.026587 | 1
7395 | 0 | 0.0088295 | 0.89861 | 0 | 0 | 1 | 0 | 0.0088295 | 1
7396 | 0 | 0.002702 | 0.89861 | 0 | 0 | 1 | 0 | 0.002702 | 1
7397 | 0 | 0.0090614 | 0.89861 | 0 | 0 | 1 | 0 | 0.0090614 | 1
7398 | 0 | 0.0066551 | 0.89861 | 0 | 0 | 1 | 0 | 0.0066551 | 1
7399 | 0 | 0.022967 | 0.89861 | 0 | 0 | 1 | 0 | 0.022967 | 1
7400 | 0 | 0.03903 | 0.89861 | 0 | 0 | 1 | 0 | 0.03903 | 1
7401 | 0.058011 | 0.039572 | 0.89861 | 0 | 0 | 1 | 0.058011 | 0.039572 | 1
7402 | 0.18625 | 0.054635 | 0.89861 | 0 | 0 | 1 | 0.18625 | 0.054635 | 1
7403 | 0.25965 | 0.062486 | 0.89861 | 0 | 0 | 1 | 0.25965 | 0.062486 | 1
7404 | 0.30567 | 0.079047 | 0.89861 | 0 | 0 | 1 | 0.30567 | 0.079047 | 1
7405 | 0.31767 | 0.097446 | 0.89861 | 0 | 0 | 1 | 0.31767 | 0.097446 | 1
7406 | 0.34385 | 0.095482 | 0.89861 | 0 | 0 | 1 | 0.34385 | 0.095482 | 1
7407 | 0.27553 | 0.073057 | 0.89861 | 0 | 0 | 1 | 0.27553 | 0.073057 | 1
7408 | 0.13918 | 0.055696 | 0.89861 | 0 | 0 | 1 | 0.13918 | 0.055696 | 1
7409 | 0 | 0.060891 | 0.89861 | 0 | 0 | 1 | 0 | 0.060891 | 1
7410 | 0 | 0.033904 | 0.89861 | 0 | 1 | 1 | 0 | 0.033904 | 1
7411 | 0 | 0.017345 | 0.89861 | 0 | 1 | 1 | 0 | 0.017345 | 1
7412 | 0 | 0.012121 | 0.89861 | 0 | 1 | 1 | 0 | 0.012121 | 1
7413 | 0 | 0.0021539 | 0.89861 | 0 | 1 | 1 | 0 | 0.0021539 | 1
7414 | 0 | 0.014403 | 0.89861 | 0 | 0 | 1 | 0 | 0.014403 | 1
7415 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7416 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7417 | 0 | 0.034327 | 0.89861 | 0 | 0 | 1 | 0 | 0.034327 | 1
7418 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7419 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7420 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7421 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7422 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7423 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7424 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7425 | 0.087085 | 0 | 0.89861 | 0 | 0 | 1 | 0.087085 | 0 | 1
7426 | 0.23301 | 0 | 0.89861 | 0 | 0 | 1 | 0.23301 | 0 | 1
7427 | 0.28345 | 0 | 0.89861 | 0 | 0 | 1 | 0.28345 | 0 | 1
7428 | 0.28171 | 0.017958 | 0.89861 | 0 | 0 | 1 | 0.28171 | 0.017958 | 1
7429 | 0.25282 | 0.043484 | 0.89861 | 0 | 0 | 1 | 0.25282 | 0.043484 | 1
7430 | 0.27848 | 0.053736 | 0.89861 | 0 | 0 | 1 | 0.27848 | 0.053736 | 1
7431 | 0.17641 | 0.023076 | 0.89861 | 0 | 0 | 1 | 0.17641 | 0.023076 | 1
7432 | 0.018698 | 0.006122 | 0.89861 | 0 | 0 | 1 | 0.018698 | 0.006122 | 1
7433 | 0 | 0.017822 | 0.89861 | 0 | 0 | 1 | 0 | 0.017822 | 1
7434 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7435 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7436 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7437 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7438 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7439 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7440 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7441 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7442 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7443 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7444 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7445 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7446 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7447 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7448 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7449 | 0.12621 | 0 | 0.89861 | 0 | 0 | 1 | 0.12621 | 0 | 1
7450 | 0.28353 | 0 | 0.89861 | 0 | 0 | 1 | 0.28353 | 0 | 1
7451 | 0.30858 | 0 | 0.89861 | 0 | 0 | 1 | 0.30858 | 0 | 1
7452 | 0.32351 | 0 | 0.89861 | 0 | 0 | 1 | 0.32351 | 0 | 1
7453 | 0.26534 | 0 | 0.89861 | 0 | 0 | 1 | 0.26534 | 0 | 1
7454 | 0.25333 | 0.0068466 | 0.89861 | 0 | 0 | 1 | 0.25333 | 0.0068466 | 1
7455 | 0.15646 | 0 | 0.89861 | 0 | 0 | 1 | 0.15646 | 0 | 1
7456 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7457 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7458 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7459 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7460 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7461 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7462 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7463 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7464 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7465 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7466 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7467 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7468 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7469 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7470 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7471 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7472 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7473 | 0.12437 | 0 | 0.89861 | 0 | 0 | 1 | 0.12437 | 0 | 1
7474 | 0.29242 | 0 | 0.89861 | 0 | 0 | 1 | 0.29242 | 0 | 1
7475 | 0.30979 | 0 | 0.89861 | 0 | 0 | 1 | 0.30979 | 0 | 1
7476 | 0.29869 | 0 | 0.89861 | 0 | 0 | 1 | 0.29869 | 0 | 1
7477 | 0.20619 | 0 | 0.89861 | 0 | 0 | 1 | 0.20619 | 0 | 1
7478 | 0.25479 | 0.0035937 | 0.89861 | 0 | 0 | 1 | 0.25479 | 0.0035937 | 1
7479 | 0.12531 | 0 | 0.89861 | 0 | 0 | 1 | 0.12531 | 0 | 1
7480 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7481 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7482 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7483 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7484 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7485 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7486 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7487 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7488 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7489 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7490 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7491 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7492 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7493 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7494 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7495 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7496 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7497 | 0.077225 | 0 | 0.89861 | 0 | 0 | 1 | 0.077225 | 0 | 1
7498 | 0.23694 | 0 | 0.89861 | 0 | 0 | 1 | 0.23694 | 0 | 1
7499 | 0.33441 | 0 | 0.89861 | 0 | 0 | 1 | 0.33441 | 0 | 1
7500 | 0.40046 | 0 | 0.89861 | 0 | 0 | 1 | 0.40046 | 0 | 1
7501 | 0.30412 | 0 | 0.89861 | 0 | 0 | 1 | 0.30412 | 0 | 1
7502 | 0.34016 | 0 | 0.89861 | 0 | 0 | 1 | 0.34016 | 0 | 1
7503 | 0.19703 | 0 | 0.89861 | 0 | 0 | 1 | 0.19703 | 0 | 1
7504 | 0.04659 | 0 | 0.89861 | 0 | 0 | 1 | 0.04659 | 0 | 1
7505 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7506 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7507 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7508 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7509 | 0 | 0 | 0.89861 | 0 | 1 | 1 | 0 | 0 | 1
7510 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7511 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7512 | 0 | 0 | 0.89861 | 0 | 0 | 1 | 0 | 0 | 1
7513 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7514 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7515 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7516 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7517 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7518 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7519 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7520 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7521 | 0.066393 | 0 | 0.86372 | 0 | 0 | 1 | 0.066393 | 0 | 1
7522 | 0.19417 | 0 | 0.86372 | 0 | 0 | 1 | 0.19417 | 0 | 1
7523 | 0.27893 | 0 | 0.86372 | 0 | 0 | 1 | 0.27893 | 0 | 1
7524 | 0.27949 | 0 | 0.86372 | 0 | 0 | 1 | 0.27949 | 0 | 1
7525 | 0.24068 | 0 | 0.86372 | 0 | 0 | 1 | 0.24068 | 0 | 1
7526 | 0.2658 | 0 | 0.86372 | 0 | 0 | 1 | 0.2658 | 0 | 1
7527 | 0.18556 | 0.0062104 | 0.86372 | 0 | 0 | 1 | 0.18556 | 0.0062104 | 1
7528 | 0.067164 | 0 | 0.86372 | 0 | 0 | 1 | 0.067164 | 0 | 1
7529 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7530 | 0 | 0 | 0.86372 | 0 | 1 | 1 | 0 | 0 | 1
7531 | 0 | 0 | 0.86372 | 0 | 1 | 1 | 0 | 0 | 1
7532 | 0 | 0 | 0.86372 | 0 | 1 | 1 | 0 | 0 | 1
7533 | 0 | 0 | 0.86372 | 0 | 1 | 1 | 0 | 0 | 1
7534 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7535 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7536 | 0 | 0 | 0.86372 | 0 | 0 | 1 | 0 | 0 | 1
7537 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7538 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7539 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7540 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7541 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7542 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7543 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7544 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7545 | 0.068735 | 0 | 0.87906 | 0 | 0 | 1 | 0.068735 | 0 | 1
7546 | 0.19073 | 0 | 0.87906 | 0 | 0 | 1 | 0.19073 | 0 | 1
7547 | 0.26288 | 0 | 0.87906 | 0 | 0 | 1 | 0.26288 | 0 | 1
7548 | 0.27501 | 0 | 0.87906 | 0 | 0 | 1 | 0.27501 | 0 | 1
7549 | 0.29741 | 0 | 0.87906 | 0 | 0 | 1 | 0.29741 | 0 | 1
7550 | 0.21685 | 0 | 0.87906 | 0 | 0 | 1 | 0.21685 | 0 | 1
7551 | 0.21741 | 0.0082376 | 0.87906 | 0 | 0 | 1 | 0.21741 | 0.0082376 | 1
7552 | 0.10427 | 0 | 0.87906 | 0 | 0 | 1 | 0.10427 | 0 | 1
7553 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7554 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7555 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7556 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7557 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7558 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7559 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7560 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7561 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7562 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7563 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7564 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7565 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7566 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7567 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7568 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7569 | 0.10304 | 0 | 0.87906 | 0 | 0 | 1 | 0.10304 | 0 | 1
7570 | 0.19728 | 0 | 0.87906 | 0 | 0 | 1 | 0.19728 | 0 | 1
7571 | 0.31233 | 0 | 0.87906 | 0 | 0 | 1 | 0.31233 | 0 | 1
7572 | 0.25463 | 0 | 0.87906 | 0 | 0 | 1 | 0.25463 | 0 | 1
7573 | 0.25538 | 0 | 0.87906 | 0 | 0 | 1 | 0.25538 | 0 | 1
7574 | 0.21636 | 0 | 0.87906 | 0 | 0 | 1 | 0.21636 | 0 | 1
7575 | 0.26646 | 0.011152 | 0.87906 | 0 | 0 | 1 | 0.26646 | 0.011152 | 1
7576 | 0.13669 | 0 | 0.87906 | 0 | 0 | 1 | 0.13669 | 0 | 1
7577 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7578 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7579 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7580 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7581 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7582 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7583 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7584 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7585 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7586 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7587 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7588 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7589 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7590 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7591 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7592 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7593 | 0.036848 | 0 | 0.87906 | 0 | 0 | 1 | 0.036848 | 0 | 1
7594 | 0.1784 | 0 | 0.87906 | 0 | 0 | 1 | 0.1784 | 0 | 1
7595 | 0.29508 | 0 | 0.87906 | 0 | 0 | 1 | 0.29508 | 0 | 1
7596 | 0.32048 | 0 | 0.87906 | 0 | 0 | 1 | 0.32048 | 0 | 1
7597 | 0.26879 | 0 | 0.87906 | 0 | 0 | 1 | 0.26879 | 0 | 1
7598 | 0.26606 | 0 | 0.87906 | 0 | 0 | 1 | 0.26606 | 0 | 1
7599 | 0.25484 | 0 | 0.87906 | 0 | 0 | 1 | 0.25484 | 0 | 1
7600 | 0.094398 | 0 | 0.87906 | 0 | 0 | 1 | 0.094398 | 0 | 1
7601 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7602 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7603 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7604 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7605 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7606 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7607 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7608 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7609 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7610 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7611 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7612 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7613 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7614 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7615 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7616 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7617 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7618 | 0.13248 | 0 | 0.87906 | 0 | 0 | 1 | 0.13248 | 0 | 1
7619 | 0.24325 | 0 | 0.87906 | 0 | 0 | 1 | 0.24325 | 0 | 1
7620 | 0.25797 | 0 | 0.87906 | 0 | 0 | 1 | 0.25797 | 0 | 1
7621 | 0.21809 | 0 | 0.87906 | 0 | 0 | 1 | 0.21809 | 0 | 1
7622 | 0.24499 | 0 | 0.87906 | 0 | 0 | 1 | 0.24499 | 0 | 1
7623 | 0.1413 | 0 | 0.87906 | 0 | 0 | 1 | 0.1413 | 0 | 1
7624 | 0.041 | 0 | 0.87906 | 0 | 0 | 1 | 0.041 | 0 | 1
7625 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7626 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7627 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7628 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7629 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7630 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7631 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7632 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7633 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7634 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7635 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7636 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7637 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7638 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7639 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7640 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7641 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7642 | 0.078024 | 0 | 0.87906 | 0 | 0 | 1 | 0.078024 | 0 | 1
7643 | 0.15052 | 0 | 0.87906 | 0 | 0 | 1 | 0.15052 | 0 | 1
7644 | 0.14443 | 0.012724 | 0.87906 | 0 | 0 | 1 | 0.14443 | 0.012724 | 1
7645 | 0.13936 | 0.028856 | 0.87906 | 0 | 0 | 1 | 0.13936 | 0.028856 | 1
7646 | 0.11663 | 0.039441 | 0.87906 | 0 | 0 | 1 | 0.11663 | 0.039441 | 1
7647 | 0.029836 | 0.029589 | 0.87906 | 0 | 0 | 1 | 0.029836 | 0.029589 | 1
7648 | 0.0012426 | 0.023732 | 0.87906 | 0 | 0 | 1 | 0.0012426 | 0.023732 | 1
7649 | 0 | 0.0077879 | 0.87906 | 0 | 0 | 1 | 0 | 0.0077879 | 1
7650 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7651 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7652 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7653 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7654 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7655 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7656 | 0 | 0.0067822 | 0.87906 | 0 | 0 | 1 | 0 | 0.0067822 | 1
7657 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7658 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7659 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7660 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7661 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7662 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7663 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7664 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7665 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7666 | 0.051184 | 0 | 0.87906 | 0 | 0 | 1 | 0.051184 | 0 | 1
7667 | 0.11341 | 0.011886 | 0.87906 | 0 | 0 | 1 | 0.11341 | 0.011886 | 1
7668 | 0.10116 | 0.019704 | 0.87906 | 0 | 0 | 1 | 0.10116 | 0.019704 | 1
7669 | 0.13283 | 0.041848 | 0.87906 | 0 | 0 | 1 | 0.13283 | 0.041848 | 1
7670 | 0.086632 | 0.063673 | 0.87906 | 0 | 0 | 1 | 0.086632 | 0.063673 | 1
7671 | 0.018178 | 0.059228 | 0.87906 | 0 | 0 | 1 | 0.018178 | 0.059228 | 1
7672 | 0.011593 | 0.061523 | 0.87906 | 0 | 0 | 1 | 0.011593 | 0.061523 | 1
7673 | 0 | 0.049145 | 0.87906 | 0 | 0 | 1 | 0 | 0.049145 | 1
7674 | 0 | 0.0094832 | 0.87906 | 0 | 1 | 1 | 0 | 0.0094832 | 1
7675 | 0 | 0.0024156 | 0.87906 | 0 | 1 | 1 | 0 | 0.0024156 | 1
7676 | 0 | 0.0026929 | 0.87906 | 0 | 1 | 1 | 0 | 0.0026929 | 1
7677 | 0 | 0.0012599 | 0.87906 | 0 | 1 | 1 | 0 | 0.0012599 | 1
7678 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7679 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7680 | 0 | 0.016036 | 0.87906 | 0 | 0 | 1 | 0 | 0.016036 | 1
7681 | 0 | 0.0089206 | 0.87906 | 0 | 0 | 1 | 0 | 0.0089206 | 1
7682 | 0 | 0.0027481 | 0.87906 | 0 | 0 | 1 | 0 | 0.0027481 | 1
7683 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7684 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7685 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7686 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7687 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7688 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7689 | 0.0086665 | 0 | 0.87906 | 0 | 0 | 1 | 0.0086665 | 0 | 1
7690 | 0.069091 | 0 | 0.87906 | 0 | 0 | 1 | 0.069091 | 0 | 1
7691 | 0.14671 | 0.028679 | 0.87906 | 0 | 0 | 1 | 0.14671 | 0.028679 | 1
7692 | 0.13807 | 0.046439 | 0.87906 | 0 | 0 | 1 | 0.13807 | 0.046439 | 1
7693 | 0.15695 | 0.052443 | 0.87906 | 0 | 0 | 1 | 0.15695 | 0.052443 | 1
7694 | 0.11359 | 0.061372 | 0.87906 | 0 | 0 | 1 | 0.11359 | 0.061372 | 1
7695 | 0.036612 | 0.066551 | 0.87906 | 0 | 0 | 1 | 0.036612 | 0.066551 | 1
7696 | 0.038412 | 0.068922 | 0.87906 | 0 | 0 | 1 | 0.038412 | 0.068922 | 1
7697 | 0 | 0.054717 | 0.87906 | 0 | 0 | 1 | 0 | 0.054717 | 1
7698 | 0 | 0.020908 | 0.87906 | 0 | 1 | 1 | 0 | 0.020908 | 1
7699 | 0 | 0.012903 | 0.87906 | 0 | 1 | 1 | 0 | 0.012903 | 1
7700 | 0 | 0.010178 | 0.87906 | 0 | 1 | 1 | 0 | 0.010178 | 1
7701 | 0 | 0.00055478 | 0.87906 | 0 | 1 | 1 | 0 | 0.00055478 | 1
7702 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7703 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7704 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7705 | 0 | 0.015227 | 0.87906 | 0 | 0 | 1 | 0 | 0.015227 | 1
7706 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7707 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7708 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7709 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7710 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7711 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7712 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7713 | 0.05074 | 0 | 0.87906 | 0 | 0 | 1 | 0.05074 | 0 | 1
7714 | 0.12934 | 0 | 0.87906 | 0 | 0 | 1 | 0.12934 | 0 | 1
7715 | 0.22375 | 0.011747 | 0.87906 | 0 | 0 | 1 | 0.22375 | 0.011747 | 1
7716 | 0.23247 | 0.033601 | 0.87906 | 0 | 0 | 1 | 0.23247 | 0.033601 | 1
7717 | 0.2356 | 0.041321 | 0.87906 | 0 | 0 | 1 | 0.2356 | 0.041321 | 1
7718 | 0.20254 | 0.056883 | 0.87906 | 0 | 0 | 1 | 0.20254 | 0.056883 | 1
7719 | 0.072853 | 0.05308 | 0.87906 | 0 | 0 | 1 | 0.072853 | 0.05308 | 1
7720 | 0.023501 | 0.045039 | 0.87906 | 0 | 0 | 1 | 0.023501 | 0.045039 | 1
7721 | 0 | 0.030249 | 0.87906 | 0 | 0 | 1 | 0 | 0.030249 | 1
7722 | 0 | 0.0061038 | 0.87906 | 0 | 1 | 1 | 0 | 0.0061038 | 1
7723 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7724 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7725 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7726 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7727 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7728 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7729 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7730 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7731 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7732 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7733 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7734 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7735 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7736 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7737 | 0.054149 | 0.0032226 | 0.87906 | 0 | 0 | 1 | 0.054149 | 0.0032226 | 1
7738 | 0.15556 | 0.0024684 | 0.87906 | 0 | 0 | 1 | 0.15556 | 0.0024684 | 1
7739 | 0.20624 | 0.005262 | 0.87906 | 0 | 0 | 1 | 0.20624 | 0.005262 | 1
7740 | 0.1772 | 0.037244 | 0.87906 | 0 | 0 | 1 | 0.1772 | 0.037244 | 1
7741 | 0.19564 | 0.037465 | 0.87906 | 0 | 0 | 1 | 0.19564 | 0.037465 | 1
7742 | 0.20133 | 0.042637 | 0.87906 | 0 | 0 | 1 | 0.20133 | 0.042637 | 1
7743 | 0.047321 | 0.038712 | 0.87906 | 0 | 0 | 1 | 0.047321 | 0.038712 | 1
7744 | 0 | 0.027617 | 0.87906 | 0 | 0 | 1 | 0 | 0.027617 | 1
7745 | 0 | 0.0057637 | 0.87906 | 0 | 0 | 1 | 0 | 0.0057637 | 1
7746 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7747 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7748 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7749 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7750 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7751 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7752 | 0 | 0.006935 | 0.87906 | 0 | 0 | 1 | 0 | 0.006935 | 1
7753 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7754 | 0 | 0.0073247 | 0.87906 | 0 | 0 | 1 | 0 | 0.0073247 | 1
7755 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7756 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7757 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7758 | 0 | 0.0031683 | 0.87906 | 0 | 0 | 1 | 0 | 0.0031683 | 1
7759 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7760 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7761 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7762 | 0.086073 | 0.0042251 | 0.87906 | 0 | 0 | 1 | 0.086073 | 0.0042251 | 1
7763 | 0.098361 | 0.0074983 | 0.87906 | 0 | 0 | 1 | 0.098361 | 0.0074983 | 1
7764 | 0.14022 | 0.029516 | 0.87906 | 0 | 0 | 1 | 0.14022 | 0.029516 | 1
7765 | 0.15814 | 0.010398 | 0.87906 | 0 | 0 | 1 | 0.15814 | 0.010398 | 1
7766 | 0.17299 | 0.013852 | 0.87906 | 0 | 0 | 1 | 0.17299 | 0.013852 | 1
7767 | 0.082383 | 0.025561 | 0.87906 | 0 | 0 | 1 | 0.082383 | 0.025561 | 1
7768 | 0 | 0.0032174 | 0.87906 | 0 | 0 | 1 | 0 | 0.0032174 | 1
7769 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7770 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7771 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7772 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7773 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7774 | 0 | 0.0019255 | 0.87906 | 0 | 0 | 1 | 0 | 0.0019255 | 1
7775 | 0 | 0.014388 | 0.87906 | 0 | 0 | 1 | 0 | 0.014388 | 1
7776 | 0 | 0.021237 | 0.87906 | 0 | 0 | 1 | 0 | 0.021237 | 1
7777 | 0 | 0.013714 | 0.87906 | 0 | 0 | 1 | 0 | 0.013714 | 1
7778 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7779 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7780 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7781 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7782 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7783 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7784 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7785 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7786 | 0.061672 | 0 | 0.87906 | 0 | 0 | 1 | 0.061672 | 0 | 1
7787 | 0.099689 | 0 | 0.87906 | 0 | 0 | 1 | 0.099689 | 0 | 1
7788 | 0.14445 | 0 | 0.87906 | 0 | 0 | 1 | 0.14445 | 0 | 1
7789 | 0.15737 | 0 | 0.87906 | 0 | 0 | 1 | 0.15737 | 0 | 1
7790 | 0.20101 | 0 | 0.87906 | 0 | 0 | 1 | 0.20101 | 0 | 1
7791 | 0.11323 | 0.0031877 | 0.87906 | 0 | 0 | 1 | 0.11323 | 0.0031877 | 1
7792 | 0.011259 | 0 | 0.87906 | 0 | 0 | 1 | 0.011259 | 0 | 1
7793 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7794 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7795 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7796 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7797 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7798 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7799 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7800 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7801 | 0 | 0.0097985 | 0.87906 | 0 | 0 | 1 | 0 | 0.0097985 | 1
7802 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7803 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7804 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7805 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7806 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7807 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7808 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7809 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7810 | 0.056526 | 0 | 0.87906 | 0 | 0 | 1 | 0.056526 | 0 | 1
7811 | 0.15263 | 0 | 0.87906 | 0 | 0 | 1 | 0.15263 | 0 | 1
7812 | 0.23013 | 0 | 0.87906 | 0 | 0 | 1 | 0.23013 | 0 | 1
7813 | 0.22805 | 0 | 0.87906 | 0 | 0 | 1 | 0.22805 | 0 | 1
7814 | 0.21336 | 0 | 0.87906 | 0 | 0 | 1 | 0.21336 | 0 | 1
7815 | 0.18897 | 0 | 0.87906 | 0 | 0 | 1 | 0.18897 | 0 | 1
7816 | 0.023854 | 0 | 0.87906 | 0 | 0 | 1 | 0.023854 | 0 | 1
7817 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7818 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7819 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7820 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7821 | 0 | 0 | 0.87906 | 0 | 1 | 1 | 0 | 0 | 1
7822 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7823 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7824 | 0 | 0 | 0.87906 | 0 | 0 | 1 | 0 | 0 | 1
7825 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7826 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7827 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7828 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7829 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7830 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7831 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7832 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7833 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7834 | 0.13136 | 0 | 0.91394 | 0 | 0 | 1 | 0.13136 | 0 | 1
7835 | 0.26512 | 0 | 0.91394 | 0 | 0 | 1 | 0.26512 | 0 | 1
7836 | 0.27415 | 0 | 0.91394 | 0 | 0 | 1 | 0.27415 | 0 | 1
7837 | 0.23253 | 0 | 0.91394 | 0 | 0 | 1 | 0.23253 | 0 | 1
7838 | 0.19207 | 0 | 0.91394 | 0 | 0 | 1 | 0.19207 | 0 | 1
7839 | 0.14148 | 0 | 0.91394 | 0 | 0 | 1 | 0.14148 | 0 | 1
7840 | 0.017561 | 0 | 0.91394 | 0 | 0 | 1 | 0.017561 | 0 | 1
7841 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7842 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7843 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7844 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7845 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7846 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7847 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7848 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7849 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7850 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7851 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7852 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7853 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7854 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7855 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7856 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7857 | 0.017975 | 0 | 0.91394 | 0 | 0 | 1 | 0.017975 | 0 | 1
7858 | 0.1724 | 0 | 0.91394 | 0 | 0 | 1 | 0.1724 | 0 | 1
7859 | 0.25739 | 0 | 0.91394 | 0 | 0 | 1 | 0.25739 | 0 | 1
7860 | 0.26103 | 0 | 0.91394 | 0 | 0 | 1 | 0.26103 | 0 | 1
7861 | 0.23596 | 0 | 0.91394 | 0 | 0 | 1 | 0.23596 | 0 | 1
7862 | 0.19205 | 0 | 0.91394 | 0 | 0 | 1 | 0.19205 | 0 | 1
7863 | 0.1542 | 0 | 0.91394 | 0 | 0 | 1 | 0.1542 | 0 | 1
7864 | 0.0078975 | 0 | 0.91394 | 0 | 0 | 1 | 0.0078975 | 0 | 1
7865 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7866 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7867 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7868 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7869 | 0 | 0 | 0.91394 | 0 | 1 | 1 | 0 | 0 | 1
7870 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7871 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7872 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7873 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7874 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7875 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7876 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7877 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7878 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7879 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7880 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7881 | 0.0090112 | 0 | 0.91394 | 0 | 0 | 1 | 0.0090112 | 0 | 1
7882 | 0.13837 | 0.0068525 | 0.91394 | 0 | 0 | 1 | 0.13837 | 0.0068525 | 1
7883 | 0.24598 | 0.017366 | 0.91394 | 0 | 0 | 1 | 0.24598 | 0.017366 | 1
7884 | 0.24556 | 0.052772 | 0.91394 | 0 | 0 | 1 | 0.24556 | 0.052772 | 1
7885 | 0.21673 | 0.055793 | 0.91394 | 0 | 0 | 1 | 0.21673 | 0.055793 | 1
7886 | 0.19803 | 0.056691 | 0.91394 | 0 | 0 | 1 | 0.19803 | 0.056691 | 1
7887 | 0.16973 | 0.064197 | 0.91394 | 0 | 0 | 1 | 0.16973 | 0.064197 | 1
7888 | 0.049873 | 0.067294 | 0.91394 | 0 | 0 | 1 | 0.049873 | 0.067294 | 1
7889 | 0.0033728 | 0.058267 | 0.91394 | 0 | 0 | 1 | 0.0033728 | 0.058267 | 1
7890 | 0 | 0.0079314 | 0.91394 | 0 | 1 | 1 | 0 | 0.0079314 | 1
7891 | 0 | 0.018148 | 0.91394 | 0 | 1 | 1 | 0 | 0.018148 | 1
7892 | 0 | 0.027115 | 0.91394 | 0 | 1 | 1 | 0 | 0.027115 | 1
7893 | 0 | 0.025473 | 0.91394 | 0 | 1 | 1 | 0 | 0.025473 | 1
7894 | 0 | 0.030683 | 0.91394 | 0 | 0 | 1 | 0 | 0.030683 | 1
7895 | 0 | 0.032225 | 0.91394 | 0 | 0 | 1 | 0 | 0.032225 | 1
7896 | 0 | 0.013153 | 0.91394 | 0 | 0 | 1 | 0 | 0.013153 | 1
7897 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7898 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7899 | 0 | 0.004407 | 0.91394 | 0 | 0 | 1 | 0 | 0.004407 | 1
7900 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7901 | 0 | 0.01683 | 0.91394 | 0 | 0 | 1 | 0 | 0.01683 | 1
7902 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7903 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7904 | 0 | 0.011913 | 0.91394 | 0 | 0 | 1 | 0 | 0.011913 | 1
7905 | 0 | 0.040782 | 0.91394 | 0 | 0 | 1 | 0 | 0.040782 | 1
7906 | 0.053493 | 0.056385 | 0.91394 | 0 | 0 | 1 | 0.053493 | 0.056385 | 1
7907 | 0.16749 | 0.0747 | 0.91394 | 0 | 0 | 1 | 0.16749 | 0.0747 | 1
7908 | 0.20762 | 0.10772 | 0.91394 | 0 | 0 | 1 | 0.20762 | 0.10772 | 1
7909 | 0.23343 | 0.12298 | 0.91394 | 0 | 0 | 1 | 0.23343 | 0.12298 | 1
7910 | 0.22063 | 0.12517 | 0.91394 | 0 | 0 | 1 | 0.22063 | 0.12517 | 1
7911 | 0.22081 | 0.12041 | 0.91394 | 0 | 0 | 1 | 0.22081 | 0.12041 | 1
7912 | 0.085196 | 0.111 | 0.91394 | 0 | 0 | 1 | 0.085196 | 0.111 | 1
7913 | 0 | 0.090755 | 0.91394 | 0 | 0 | 1 | 0 | 0.090755 | 1
7914 | 0 | 0.054076 | 0.91394 | 0 | 1 | 1 | 0 | 0.054076 | 1
7915 | 0 | 0.087974 | 0.91394 | 0 | 1 | 1 | 0 | 0.087974 | 1
7916 | 0 | 0.088893 | 0.91394 | 0 | 1 | 1 | 0 | 0.088893 | 1
7917 | 0 | 0.083602 | 0.91394 | 0 | 1 | 1 | 0 | 0.083602 | 1
7918 | 0 | 0.094707 | 0.91394 | 0 | 0 | 1 | 0 | 0.094707 | 1
7919 | 0 | 0.095954 | 0.91394 | 0 | 0 | 1 | 0 | 0.095954 | 1
7920 | 0 | 0.069953 | 0.91394 | 0 | 0 | 1 | 0 | 0.069953 | 1
7921 | 0 | 0 | 0.91394 | 0 | 0 | 1 | 0 | 0 | 1
7922 | 0 | 0.062348 | 0.91394 | 0 | 0 | 1 | 0 | 0.062348 | 1
7923 | 0 | 0.068182 | 0.91394 | 0 | 0 | 1 | 0 | 0.068182 | 1
7924 | 0 | 0.075304 | 0.91394 | 0 | 0 | 1 | 0 | 0.075304 | 1
7925 | 0 | 0.075542 | 0.91394 | 0 | 0 | 1 | 0 | 0.075542 | 1
7926 | 0 | 0.0671 | 0.91394 | 0 | 0 | 1 | 0 | 0.0671 | 1
7927 | 0 | 0.078195 | 0.91394 | 0 | 0 | 1 | 0 | 0.078195 | 1
7928 | 0 | 0.093422 | 0.91394 | 0 | 0 | 1 | 0 | 0.093422 | 1
7929 | 0 | 0.10609 | 0.91394 | 0 | 0 | 1 | 0 | 0.10609 | 1
7930 | 0.034958 | 0.11653 | 0.91394 | 0 | 0 | 1 | 0.034958 | 0.11653 | 1
7931 | 0.14436 | 0.13436 | 0.91394 | 0 | 0 | 1 | 0.14436 | 0.13436 | 1
7932 | 0.18446 | 0.15403 | 0.91394 | 0 | 0 | 1 | 0.18446 | 0.15403 | 1
7933 | 0.23292 | 0.16888 | 0.91394 | 0 | 0 | 1 | 0.23292 | 0.16888 | 1
7934 | 0.18318 | 0.15973 | 0.91394 | 0 | 0 | 1 | 0.18318 | 0.15973 | 1
7935 | 0.20112 | 0.14611 | 0.91394 | 0 | 0 | 1 | 0.20112 | 0.14611 | 1
7936 | 0.093357 | 0.11963 | 0.91394 | 0 | 0 | 1 | 0.093357 | 0.11963 | 1
7937 | 0 | 0.093021 | 0.91394 | 0 | 0 | 1 | 0 | 0.093021 | 1
7938 | 0 | 0.098111 | 0.91394 | 0 | 1 | 1 | 0 | 0.098111 | 1
7939 | 0 | 0.1069 | 0.91394 | 0 | 1 | 1 | 0 | 0.1069 | 1
7940 | 0 | 0.092554 | 0.91394 | 0 | 1 | 1 | 0 | 0.092554 | 1
7941 | 0 | 0.093044 | 0.91394 | 0 | 1 | 1 | 0 | 0.093044 | 1
7942 | 0 | 0.10888 | 0.91394 | 0 | 0 | 1 | 0 | 0.10888 | 1
7943 | 0 | 0.089066 | 0.91394 | 0 | 0 | 1 | 0 | 0.089066 | 1
7944 | 0 | 0.087416 | 0.91394 | 0 | 0 | 1 | 0 | 0.087416 | 1
7945 | 0 | 0.046675 | 0.91394 | 0 | 0 | 1 | 0 | 0.046675 | 1
7946 | 0 | 0.081821 | 0.91394 | 0 | 0 | 1 | 0 | 0.081821 | 1
7947 | 0 | 0.089343 | 0.91394 | 0 | 0 | 1 | 0 | 0.089343 | 1
7948 | 0 | 0.10227 | 0.91394 | 0 | 0 | 1 | 0 | 0.10227 | 1
7949 | 0 | 0.11324 | 0.91394 | 0 | 0 | 1 | 0 | 0.11324 | 1
7950 | 0 | 0.097571 | 0.91394 | 0 | 0 | 1 | 0 | 0.097571 | 1
7951 | 0 | 0.10915 | 0.91394 | 0 | 0 | 1 | 0 | 0.10915 | 1
7952 | 0 | 0.10443 | 0.91394 | 0 | 0 | 1 | 0 | 0.10443 | 1
7953 | 0 | 0.10236 | 0.91394 | 0 | 0 | 1 | 0 | 0.10236 | 1
7954 | 0.085666 | 0.1015 | 0.91394 | 0 | 0 | 1 | 0.085666 | 0.1015 | 1
7955 | 0.13455 | 0.11257 | 0.91394 | 0 | 0 | 1 | 0.13455 | 0.11257 | 1
7956 | 0.14524 | 0.12061 | 0.91394 | 0 | 0 | 1 | 0.14524 | 0.12061 | 1
7957 | 0.1992 | 0.13039 | 0.91394 | 0 | 0 | 1 | 0.1992 | 0.13039 | 1
7958 | 0.15666 | 0.10434 | 0.91394 | 0 | 0 | 1 | 0.15666 | 0.10434 | 1
7959 | 0.15124 | 0.088728 | 0.91394 | 0 | 0 | 1 | 0.15124 | 0.088728 | 1
7960 | 0.048082 | 0.061504 | 0.91394 | 0 | 0 | 1 | 0.048082 | 0.061504 | 1
7961 | 0 | 0.035253 | 0.91394 | 0 | 0 | 1 | 0 | 0.035253 | 1
7962 | 0 | 0.048757 | 0.91394 | 0 | 1 | 1 | 0 | 0.048757 | 1
7963 | 0 | 0.058398 | 0.91394 | 0 | 1 | 1 | 0 | 0.058398 | 1
7964 | 0 | 0.065054 | 0.91394 | 0 | 1 | 1 | 0 | 0.065054 | 1
7965 | 0 | 0.066815 | 0.91394 | 0 | 1 | 1 | 0 | 0.066815 | 1
7966 | 0 | 0.085936 | 0.91394 | 0 | 0 | 1 | 0 | 0.085936 | 1
7967 | 0 | 0.071849 | 0.91394 | 0 | 0 | 1 | 0 | 0.071849 | 1
7968 | 0 | 0.10179 | 0.91394 | 0 | 0 | 1 | 0 | 0.10179 | 1
7969 | 0 | 0.081666 | 0.91394 | 0 | 0 | 1 | 0 | 0.081666 | 1
7970 | 0 | 0.090097 | 0.91394 | 0 | 0 | 1 | 0 | 0.090097 | 1
7971 | 0 | 0.11192 | 0.91394 | 0 | 0 | 1 | 0 | 0.11192 | 1
7972 | 0 | 0.12099 | 0.91394 | 0 | 0 | 1 | 0 | 0.12099 | 1
7973 | 0 | 0.12951 | 0.91394 | 0 | 0 | 1 | 0 | 0.12951 | 1
7974 | 0 | 0.13238 | 0.91394 | 0 | 0 | 1 | 0 | 0.13238 | 1
7975 | 0 | 0.12998 | 0.91394 | 0 | 0 | 1 | 0 | 0.12998 | 1
7976 | 0 | 0.13077 | 0.91394 | 0 | 0 | 1 | 0 | 0.13077 | 1
7977 | 0.017943 | 0.082553 | 0.91394 | 0 | 0 | 1 | 0.017943 | 0.082553 | 1
7978 | 0.12169 | 0.09429 | 0.91394 | 0 | 0 | 1 | 0.12169 | 0.09429 | 1
7979 | 0.20608 | 0.1041 | 0.91394 | 0 | 0 | 1 | 0.20608 | 0.1041 | 1
7980 | 0.19334 | 0.10808 | 0.91394 | 0 | 0 | 1 | 0.19334 | 0.10808 | 1
7981 | 0.20818 | 0.11254 | 0.91394 | 0 | 0 | 1 | 0.20818 | 0.11254 | 1
7982 | 0.14089 | 0.088928 | 0.91394 | 0 | 0 | 1 | 0.14089 | 0.088928 | 1
7983 | 0.15288 | 0.083987 | 0.91394 | 0 | 0 | 1 | 0.15288 | 0.083987 | 1
7984 | 0.026583 | 0.061498 | 0.91394 | 0 | 0 | 1 | 0.026583 | 0.061498 | 1
7985 | 0 | 0.03258 | 0.91394 | 0 | 0 | 1 | 0 | 0.03258 | 1
7986 | 0 | 0.029899 | 0.91394 | 0 | 1 | 1 | 0 | 0.029899 | 1
7987 | 0 | 0.039407 | 0.91394 | 0 | 1 | 1 | 0 | 0.039407 | 1
7988 | 0 | 0.029132 | 0.91394 | 0 | 1 | 1 | 0 | 0.029132 | 1
7989 | 0 | 0.032402 | 0.91394 | 0 | 1 | 1 | 0 | 0.032402 | 1
7990 | 0 | 0.059005 | 0.91394 | 0 | 0 | 1 | 0 | 0.059005 | 1
7991 | 0 | 0.045252 | 0.91394 | 0 | 0 | 1 | 0 | 0.045252 | 1
7992 | 0 | 0.060476 | 0.91394 | 0 | 0 | 1 | 0 | 0.060476 | 1
7993 | 0 | 0.099353 | 0.91394 | 0 | 0 | 1 | 0 | 0.099353 | 1
7994 | 0 | 0.061464 | 0.91394 | 0 | 0 | 1 | 0 | 0.061464 | 1
7995 | 0 | 0.07908 | 0.91394 | 0 | 0 | 1 | 0 | 0.07908 | 1
7996 | 0 | 0.078282 | 0.91394 | 0 | 0 | 1 | 0 | 0.078282 | 1
7997 | 0 | 0.08643 | 0.91394 | 0 | 0 | 1 | 0 | 0.08643 | 1
7998 | 0 | 0.075236 | 0.91394 | 0 | 0 | 1 | 0 | 0.075236 | 1
7999 | 0 | 0.070304 | 0.91394 | 0 | 0 | 1 | 0 | 0.070304 | 1
8000 | 0 | 0.096498 | 0.91394 | 0 | 0 | 1 | 0 | 0.096498 | 1
8001 | 0 | 0.066299 | 0.91394 | 0 | 0 | 1 | 0 | 0.066299 | 1
8002 | 0.049247 | 0.054451 | 0.91394 | 0 | 0 | 1 | 0.049247 | 0.054451 | 1
8003 | 0.08169 | 0.06007 | 0.91394 | 0 | 0 | 1 | 0.08169 | 0.06007 | 1
8004 | 0.11026 | 0.076593 | 0.91394 | 0 | 0 | 1 | 0.11026 | 0.076593 | 1
8005 | 0.11558 | 0.078858 | 0.91394 | 0 | 0 | 1 | 0.11558 | 0.078858 | 1
8006 | 0.064052 | 0.06314 | 0.91394 | 0 | 0 | 1 | 0.064052 | 0.06314 | 1
8007 | 0.03551 | 0.051686 | 0.91394 | 0 | 0 | 1 | 0.03551 | 0.051686 | 1
8008 | 0 | 0.043832 | 0.91394 | 0 | 0 | 1 | 0 | 0.043832 | 1
8009 | 0 | 0.028318 | 0.91394 | 0 | 0 | 1 | 0 | 0.028318 | 1
8010 | 0 | 0.027534 | 0.91394 | 0 | 1 | 1 | 0 | 0.027534 | 1
8011 | 0 | 0.03307 | 0.91394 | 0 | 1 | 1 | 0 | 0.03307 | 1
8012 | 0 | 0.022044 | 0.91394 | 0 | 1 | 1 | 0 | 0.022044 | 1
8013 | 0 | 0.030897 | 0.91394 | 0 | 1 | 1 | 0 | 0.030897 | 1
8014 | 0 | 0.040915 | 0.91394 | 0 | 0 | 1 | 0 | 0.040915 | 1
8015 | 0 | 0.037147 | 0.91394 | 0 | 0 | 1 | 0 | 0.037147 | 1
8016 | 0 | 0.061595 | 0.91394 | 0 | 0 | 1 | 0 | 0.061595 | 1
8017 | 0 | 0.083139 | 1 | 0 | 0 | 1 | 0 | 0.083139 | 1
8018 | 0 | 0.050242 | 1 | 0 | 0 | 1 | 0 | 0.050242 | 1
8019 | 0 | 0.05058 | 1 | 0 | 0 | 1 | 0 | 0.05058 | 1
8020 | 0 | 0.058575 | 1 | 0 | 0 | 1 | 0 | 0.058575 | 1
8021 | 0 | 0.05451 | 1 | 0 | 0 | 1 | 0 | 0.05451 | 1
8022 | 0 | 0.052326 | 1 | 0 | 0 | 1 | 0 | 0.052326 | 1
8023 | 0 | 0.054439 | 1 | 0 | 0 | 1 | 0 | 0.054439 | 1
8024 | 0 | 0.050242 | 1 | 0 | 0 | 1 | 0 | 0.050242 | 1
8025 | 0 | 0.042481 | 1 | 0 | 0 | 1 | 0 | 0.042481 | 1
8026 | 0 | 0.056034 | 1 | 0 | 0 | 1 | 0 | 0.056034 | 1
8027 | 0.008721 | 0.064883 | 1 | 0 | 0 | 1 | 0.008721 | 0.064883 | 1
8028 | 0.078909 | 0.073747 | 1 | 0 | 0 | 1 | 0.078909 | 0.073747 | 1
8029 | 0.091845 | 0.068368 | 1 | 0 | 0 | 1 | 0.091845 | 0.068368 | 1
8030 | 0.049491 | 0.058695 | 1 | 0 | 0 | 1 | 0.049491 | 0.058695 | 1
8031 | 0.0040451 | 0.046851 | 1 | 0 | 0 | 1 | 0.0040451 | 0.046851 | 1
8032 | 0 | 0.040532 | 1 | 0 | 0 | 1 | 0 | 0.040532 | 1
8033 | 0 | 0.024083 | 1 | 0 | 0 | 1 | 0 | 0.024083 | 1
8034 | 0 | 0.026689 | 1 | 0 | 1 | 1 | 0 | 0.026689 | 1
8035 | 0 | 0.040871 | 1 | 0 | 1 | 1 | 0 | 0.040871 | 1
8036 | 0 | 0.014052 | 1 | 0 | 1 | 1 | 0 | 0.014052 | 1
8037 | 0 | 0.0088785 | 1 | 0 | 1 | 1 | 0 | 0.0088785 | 1
8038 | 0 | 0.016127 | 1 | 0 | 0 | 1 | 0 | 0.016127 | 1
8039 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
8040 | 0 | 0.017745 | 1 | 0 | 0 | 1 | 0 | 0.017745 | 1
8041 | 0 | 0.060151 | 0.94486 | 0 | 0 | 1 | 0 | 0.060151 | 1
8042 | 0 | 0.0078551 | 0.94486 | 0 | 0 | 1 | 0 | 0.0078551 | 1
8043 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8044 | 0 | 0.00019364 | 0.94486 | 0 | 0 | 1 | 0 | 0.00019364 | 1
8045 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8046 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8047 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8048 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8049 | 0 | 0.0092978 | 0.94486 | 0 | 0 | 1 | 0 | 0.0092978 | 1
8050 | 0 | 0.015567 | 0.94486 | 0 | 0 | 1 | 0 | 0.015567 | 1
8051 | 0 | 0.035826 | 0.94486 | 0 | 0 | 1 | 0 | 0.035826 | 1
8052 | 0.033216 | 0.051009 | 0.94486 | 0 | 0 | 1 | 0.033216 | 0.051009 | 1
8053 | 0.085834 | 0.037515 | 0.94486 | 0 | 0 | 1 | 0.085834 | 0.037515 | 1
8054 | 0.06812 | 0.038182 | 0.94486 | 0 | 0 | 1 | 0.06812 | 0.038182 | 1
8055 | 0 | 0.01898 | 0.94486 | 0 | 0 | 1 | 0 | 0.01898 | 1
8056 | 0 | 0.027122 | 0.94486 | 0 | 0 | 1 | 0 | 0.027122 | 1
8057 | 0 | 0.00052381 | 0.94486 | 0 | 0 | 1 | 0 | 0.00052381 | 1
8058 | 0 | 0 | 0.94486 | 0 | 1 | 1 | 0 | 0 | 1
8059 | 0 | 0 | 0.94486 | 0 | 1 | 1 | 0 | 0 | 1
8060 | 0 | 0 | 0.94486 | 0 | 1 | 1 | 0 | 0 | 1
8061 | 0 | 0 | 0.94486 | 0 | 1 | 1 | 0 | 0 | 1
8062 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8063 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8064 | 0 | 0 | 0.94486 | 0 | 0 | 1 | 0 | 0 | 1
8065 | 0 | 0.020728 | 0.85931 | 0 | 0 | 1 | 0 | 0.020728 | 1
8066 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8067 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8068 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8069 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8070 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8071 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8072 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8073 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8074 | 0.027787 | 0 | 0.85931 | 0 | 0 | 1 | 0.027787 | 0 | 1
8075 | 0.074998 | 0.018397 | 0.85931 | 0 | 0 | 1 | 0.074998 | 0.018397 | 1
8076 | 0.053348 | 0.016031 | 0.85931 | 0 | 0 | 1 | 0.053348 | 0.016031 | 1
8077 | 0.13063 | 0.0056099 | 0.85931 | 0 | 0 | 1 | 0.13063 | 0.0056099 | 1
8078 | 0.090391 | 0.01108 | 0.85931 | 0 | 0 | 1 | 0.090391 | 0.01108 | 1
8079 | 0.0060272 | 0.0079229 | 0.85931 | 0 | 0 | 1 | 0.0060272 | 0.0079229 | 1
8080 | 0 | 0.0090655 | 0.85931 | 0 | 0 | 1 | 0 | 0.0090655 | 1
8081 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8082 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8083 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8084 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8085 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8086 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8087 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8088 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8089 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8090 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8091 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8092 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8093 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8094 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8095 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8096 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8097 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8098 | 0.12554 | 0 | 0.85931 | 0 | 0 | 1 | 0.12554 | 0 | 1
8099 | 0.18343 | 0 | 0.85931 | 0 | 0 | 1 | 0.18343 | 0 | 1
8100 | 0.11031 | 0 | 0.85931 | 0 | 0 | 1 | 0.11031 | 0 | 1
8101 | 0.15003 | 0 | 0.85931 | 0 | 0 | 1 | 0.15003 | 0 | 1
8102 | 0.10662 | 0 | 0.85931 | 0 | 0 | 1 | 0.10662 | 0 | 1
8103 | 0.020824 | 0 | 0.85931 | 0 | 0 | 1 | 0.020824 | 0 | 1
8104 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8105 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8106 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8107 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8108 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8109 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8110 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8111 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8112 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8113 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8114 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8115 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8116 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8117 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8118 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8119 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8120 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8121 | 0.011844 | 0 | 0.85931 | 0 | 0 | 1 | 0.011844 | 0 | 1
8122 | 0.13262 | 0 | 0.85931 | 0 | 0 | 1 | 0.13262 | 0 | 1
8123 | 0.20815 | 0 | 0.85931 | 0 | 0 | 1 | 0.20815 | 0 | 1
8124 | 0.14087 | 0 | 0.85931 | 0 | 0 | 1 | 0.14087 | 0 | 1
8125 | 0.16334 | 0 | 0.85931 | 0 | 0 | 1 | 0.16334 | 0 | 1
8126 | 0.10387 | 0 | 0.85931 | 0 | 0 | 1 | 0.10387 | 0 | 1
8127 | 0.0088716 | 0.0034702 | 0.85931 | 0 | 0 | 1 | 0.0088716 | 0.0034702 | 1
8128 | 0 | 0.0015967 | 0.85931 | 0 | 0 | 1 | 0 | 0.0015967 | 1
8129 | 0 | 0.0053742 | 0.85931 | 0 | 0 | 1 | 0 | 0.0053742 | 1
8130 | 0 | 0.0014427 | 0.85931 | 0 | 1 | 1 | 0 | 0.0014427 | 1
8131 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8132 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8133 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8134 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8135 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8136 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8137 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8138 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8139 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8140 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8141 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8142 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8143 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8144 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8145 | 0.058206 | 0 | 0.85931 | 0 | 0 | 1 | 0.058206 | 0 | 1
8146 | 0.22268 | 0 | 0.85931 | 0 | 0 | 1 | 0.22268 | 0 | 1
8147 | 0.35269 | 0 | 0.85931 | 0 | 0 | 1 | 0.35269 | 0 | 1
8148 | 0.25258 | 0 | 0.85931 | 0 | 0 | 1 | 0.25258 | 0 | 1
8149 | 0.23633 | 0 | 0.85931 | 0 | 0 | 1 | 0.23633 | 0 | 1
8150 | 0.16982 | 0 | 0.85931 | 0 | 0 | 1 | 0.16982 | 0 | 1
8151 | 0.071612 | 0 | 0.85931 | 0 | 0 | 1 | 0.071612 | 0 | 1
8152 | 0.0030664 | 0 | 0.85931 | 0 | 0 | 1 | 0.0030664 | 0 | 1
8153 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8154 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8155 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8156 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8157 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8158 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8159 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8160 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8161 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8162 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8163 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8164 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8165 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8166 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8167 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8168 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8169 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8170 | 0.11637 | 0 | 0.85931 | 0 | 0 | 1 | 0.11637 | 0 | 1
8171 | 0.22456 | 0 | 0.85931 | 0 | 0 | 1 | 0.22456 | 0 | 1
8172 | 0.1544 | 0 | 0.85931 | 0 | 0 | 1 | 0.1544 | 0 | 1
8173 | 0.22696 | 0 | 0.85931 | 0 | 0 | 1 | 0.22696 | 0 | 1
8174 | 0.1439 | 0 | 0.85931 | 0 | 0 | 1 | 0.1439 | 0 | 1
8175 | 0.081024 | 0 | 0.85931 | 0 | 0 | 1 | 0.081024 | 0 | 1
8176 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8177 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8178 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8179 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8180 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8181 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8182 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8183 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8184 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8185 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8186 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8187 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8188 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8189 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8190 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8191 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8192 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8193 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8194 | 0.069002 | 0 | 0.85931 | 0 | 0 | 1 | 0.069002 | 0 | 1
8195 | 0.17015 | 0 | 0.85931 | 0 | 0 | 1 | 0.17015 | 0 | 1
8196 | 0.14306 | 0 | 0.85931 | 0 | 0 | 1 | 0.14306 | 0 | 1
8197 | 0.19879 | 0 | 0.85931 | 0 | 0 | 1 | 0.19879 | 0 | 1
8198 | 0.13199 | 0 | 0.85931 | 0 | 0 | 1 | 0.13199 | 0 | 1
8199 | 0.088008 | 0 | 0.85931 | 0 | 0 | 1 | 0.088008 | 0 | 1
8200 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8201 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8202 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8203 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8204 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8205 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8206 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8207 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8208 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8209 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8210 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8211 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8212 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8213 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8214 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8215 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8216 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8217 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8218 | 0.052082 | 0 | 0.85931 | 0 | 0 | 1 | 0.052082 | 0 | 1
8219 | 0.14905 | 0 | 0.85931 | 0 | 0 | 1 | 0.14905 | 0 | 1
8220 | 0.15163 | 0 | 0.85931 | 0 | 0 | 1 | 0.15163 | 0 | 1
8221 | 0.14745 | 0 | 0.85931 | 0 | 0 | 1 | 0.14745 | 0 | 1
8222 | 0.10356 | 0 | 0.85931 | 0 | 0 | 1 | 0.10356 | 0 | 1
8223 | 0.063517 | 0 | 0.85931 | 0 | 0 | 1 | 0.063517 | 0 | 1
8224 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8225 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8226 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8227 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8228 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8229 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8230 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8231 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8232 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8233 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8234 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8235 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8236 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8237 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8238 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8239 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8240 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8241 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8242 | 0.14206 | 0 | 0.85931 | 0 | 0 | 1 | 0.14206 | 0 | 1
8243 | 0.27573 | 0 | 0.85931 | 0 | 0 | 1 | 0.27573 | 0 | 1
8244 | 0.28445 | 0 | 0.85931 | 0 | 0 | 1 | 0.28445 | 0 | 1
8245 | 0.20639 | 0 | 0.85931 | 0 | 0 | 1 | 0.20639 | 0 | 1
8246 | 0.19955 | 0 | 0.85931 | 0 | 0 | 1 | 0.19955 | 0 | 1
8247 | 0.14404 | 0 | 0.85931 | 0 | 0 | 1 | 0.14404 | 0 | 1
8248 | 0.010317 | 0 | 0.85931 | 0 | 0 | 1 | 0.010317 | 0 | 1
8249 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8250 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8251 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8252 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8253 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8254 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8255 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8256 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8257 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8258 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8259 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8260 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8261 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8262 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8263 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8264 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8265 | 0.00050924 | 0 | 0.85931 | 0 | 0 | 1 | 0.00050924 | 0 | 1
8266 | 0.11016 | 0 | 0.85931 | 0 | 0 | 1 | 0.11016 | 0 | 1
8267 | 0.23914 | 0 | 0.85931 | 0 | 0 | 1 | 0.23914 | 0 | 1
8268 | 0.21334 | 0 | 0.85931 | 0 | 0 | 1 | 0.21334 | 0 | 1
8269 | 0.11408 | 0 | 0.85931 | 0 | 0 | 1 | 0.11408 | 0 | 1
8270 | 0.18601 | 0 | 0.85931 | 0 | 0 | 1 | 0.18601 | 0 | 1
8271 | 0.14364 | 0 | 0.85931 | 0 | 0 | 1 | 0.14364 | 0 | 1
8272 | 0.06772 | 0 | 0.85931 | 0 | 0 | 1 | 0.06772 | 0 | 1
8273 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8274 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8275 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8276 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8277 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8278 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8279 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8280 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8281 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8282 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8283 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8284 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8285 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8286 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8287 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8288 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8289 | 0.0079127 | 0 | 0.85931 | 0 | 0 | 1 | 0.0079127 | 0 | 1
8290 | 0.092097 | 0 | 0.85931 | 0 | 0 | 1 | 0.092097 | 0 | 1
8291 | 0.18148 | 0 | 0.85931 | 0 | 0 | 1 | 0.18148 | 0 | 1
8292 | 0.21478 | 0 | 0.85931 | 0 | 0 | 1 | 0.21478 | 0 | 1
8293 | 0.14462 | 0 | 0.85931 | 0 | 0 | 1 | 0.14462 | 0 | 1
8294 | 0.24266 | 0 | 0.85931 | 0 | 0 | 1 | 0.24266 | 0 | 1
8295 | 0.2197 | 0 | 0.85931 | 0 | 0 | 1 | 0.2197 | 0 | 1
8296 | 0.16869 | 0 | 0.85931 | 0 | 0 | 1 | 0.16869 | 0 | 1
8297 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8298 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8299 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8300 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8301 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8302 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8303 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8304 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8305 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8306 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8307 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8308 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8309 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8310 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8311 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8312 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8313 | 0.020695 | 0 | 0.85931 | 0 | 0 | 1 | 0.020695 | 0 | 1
8314 | 0.10768 | 0 | 0.85931 | 0 | 0 | 1 | 0.10768 | 0 | 1
8315 | 0.16493 | 0 | 0.85931 | 0 | 0 | 1 | 0.16493 | 0 | 1
8316 | 0.21197 | 0 | 0.85931 | 0 | 0 | 1 | 0.21197 | 0 | 1
8317 | 0.15352 | 0 | 0.85931 | 0 | 0 | 1 | 0.15352 | 0 | 1
8318 | 0.23514 | 0 | 0.85931 | 0 | 0 | 1 | 0.23514 | 0 | 1
8319 | 0.15888 | 0 | 0.85931 | 0 | 0 | 1 | 0.15888 | 0 | 1
8320 | 0.092373 | 0 | 0.85931 | 0 | 0 | 1 | 0.092373 | 0 | 1
8321 | 0.029944 | 0 | 0.85931 | 0 | 0 | 1 | 0.029944 | 0 | 1
8322 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8323 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8324 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8325 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8326 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8327 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8328 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8329 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8330 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8331 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8332 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8333 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8334 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8335 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8336 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8337 | 0.019042 | 0 | 0.85931 | 0 | 0 | 1 | 0.019042 | 0 | 1
8338 | 0.14392 | 0 | 0.85931 | 0 | 0 | 1 | 0.14392 | 0 | 1
8339 | 0.19279 | 0.0070039 | 0.85931 | 0 | 0 | 1 | 0.19279 | 0.0070039 | 1
8340 | 0.26124 | 0.0046419 | 0.85931 | 0 | 0 | 1 | 0.26124 | 0.0046419 | 1
8341 | 0.27018 | 0.036324 | 0.85931 | 0 | 0 | 1 | 0.27018 | 0.036324 | 1
8342 | 0.22848 | 0.031748 | 0.85931 | 0 | 0 | 1 | 0.22848 | 0.031748 | 1
8343 | 0.17002 | 0.052687 | 0.85931 | 0 | 0 | 1 | 0.17002 | 0.052687 | 1
8344 | 0.053908 | 0.041787 | 0.85931 | 0 | 0 | 1 | 0.053908 | 0.041787 | 1
8345 | 0.02118 | 0.033944 | 0.85931 | 0 | 0 | 1 | 0.02118 | 0.033944 | 1
8346 | 0 | 0.014032 | 0.85931 | 0 | 1 | 1 | 0 | 0.014032 | 1
8347 | 0 | 0.016469 | 0.85931 | 0 | 1 | 1 | 0 | 0.016469 | 1
8348 | 0 | 0.022863 | 0.85931 | 0 | 1 | 1 | 0 | 0.022863 | 1
8349 | 0 | 0.027996 | 0.85931 | 0 | 1 | 1 | 0 | 0.027996 | 1
8350 | 0 | 0.033941 | 0.85931 | 0 | 0 | 1 | 0 | 0.033941 | 1
8351 | 0 | 0.01915 | 0.85931 | 0 | 0 | 1 | 0 | 0.01915 | 1
8352 | 0 | 0.017559 | 0.85931 | 0 | 0 | 1 | 0 | 0.017559 | 1
8353 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8354 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8355 | 0 | 0.0030422 | 0.85931 | 0 | 0 | 1 | 0 | 0.0030422 | 1
8356 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8357 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8358 | 0 | 0.0022981 | 0.85931 | 0 | 0 | 1 | 0 | 0.0022981 | 1
8359 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8360 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8361 | 0.016271 | 0 | 0.85931 | 0 | 0 | 1 | 0.016271 | 0 | 1
8362 | 0.16043 | 0 | 0.85931 | 0 | 0 | 1 | 0.16043 | 0 | 1
8363 | 0.26346 | 0.0052672 | 0.85931 | 0 | 0 | 1 | 0.26346 | 0.0052672 | 1
8364 | 0.29378 | 0.01978 | 0.85931 | 0 | 0 | 1 | 0.29378 | 0.01978 | 1
8365 | 0.32502 | 0.047116 | 0.85931 | 0 | 0 | 1 | 0.32502 | 0.047116 | 1
8366 | 0.19495 | 0.046383 | 0.85931 | 0 | 0 | 1 | 0.19495 | 0.046383 | 1
8367 | 0.20916 | 0.062495 | 0.85931 | 0 | 0 | 1 | 0.20916 | 0.062495 | 1
8368 | 0.056275 | 0.04807 | 0.85931 | 0 | 0 | 1 | 0.056275 | 0.04807 | 1
8369 | 0.0033762 | 0.03644 | 0.85931 | 0 | 0 | 1 | 0.0033762 | 0.03644 | 1
8370 | 0 | 0.010713 | 0.85931 | 0 | 1 | 1 | 0 | 0.010713 | 1
8371 | 0 | 0.016932 | 0.85931 | 0 | 1 | 1 | 0 | 0.016932 | 1
8372 | 0 | 0.011084 | 0.85931 | 0 | 1 | 1 | 0 | 0.011084 | 1
8373 | 0 | 0.0011884 | 0.85931 | 0 | 1 | 1 | 0 | 0.0011884 | 1
8374 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8375 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8376 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8377 | 0 | 0.0019125 | 0.85931 | 0 | 0 | 1 | 0 | 0.0019125 | 1
8378 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8379 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8380 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8381 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8382 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8383 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8384 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8385 | 0.014159 | 0 | 0.85931 | 0 | 0 | 1 | 0.014159 | 0 | 1
8386 | 0.14645 | 0 | 0.85931 | 0 | 0 | 1 | 0.14645 | 0 | 1
8387 | 0.27558 | 0 | 0.85931 | 0 | 0 | 1 | 0.27558 | 0 | 1
8388 | 0.31226 | 0 | 0.85931 | 0 | 0 | 1 | 0.31226 | 0 | 1
8389 | 0.31229 | 0.0027784 | 0.85931 | 0 | 0 | 1 | 0.31229 | 0.0027784 | 1
8390 | 0.23041 | 0.026529 | 0.85931 | 0 | 0 | 1 | 0.23041 | 0.026529 | 1
8391 | 0.28256 | 0.0467 | 0.85931 | 0 | 0 | 1 | 0.28256 | 0.0467 | 1
8392 | 0.10783 | 0.029047 | 0.85931 | 0 | 0 | 1 | 0.10783 | 0.029047 | 1
8393 | 0.0019901 | 0.0038416 | 0.85931 | 0 | 0 | 1 | 0.0019901 | 0.0038416 | 1
8394 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8395 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8396 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8397 | 0 | 0 | 0.85931 | 0 | 1 | 1 | 0 | 0 | 1
8398 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8399 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8400 | 0 | 0 | 0.85931 | 0 | 0 | 1 | 0 | 0 | 1
8401 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8402 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8403 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8404 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8405 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8406 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8407 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8408 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8409 | 0.050434 | 0 | 0.82379 | 0 | 0 | 1 | 0.050434 | 0 | 1
8410 | 0.21526 | 0 | 0.82379 | 0 | 0 | 1 | 0.21526 | 0 | 1
8411 | 0.29332 | 0 | 0.82379 | 0 | 0 | 1 | 0.29332 | 0 | 1
8412 | 0.29666 | 0 | 0.82379 | 0 | 0 | 1 | 0.29666 | 0 | 1
8413 | 0.26886 | 0 | 0.82379 | 0 | 0 | 1 | 0.26886 | 0 | 1
8414 | 0.24769 | 0.021555 | 0.82379 | 0 | 0 | 1 | 0.24769 | 0.021555 | 1
8415 | 0.25979 | 0.010497 | 0.82379 | 0 | 0 | 1 | 0.25979 | 0.010497 | 1
8416 | 0.10976 | 0 | 0.82379 | 0 | 0 | 1 | 0.10976 | 0 | 1
8417 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8418 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8419 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8420 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8421 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8422 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8423 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8424 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8425 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8426 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8427 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8428 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8429 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8430 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8431 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8432 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8433 | 0.016354 | 0 | 0.82379 | 0 | 0 | 1 | 0.016354 | 0 | 1
8434 | 0.12641 | 0 | 0.82379 | 0 | 0 | 1 | 0.12641 | 0 | 1
8435 | 0.20531 | 0 | 0.82379 | 0 | 0 | 1 | 0.20531 | 0 | 1
8436 | 0.19333 | 0 | 0.82379 | 0 | 0 | 1 | 0.19333 | 0 | 1
8437 | 0.15007 | 0 | 0.82379 | 0 | 0 | 1 | 0.15007 | 0 | 1
8438 | 0.15788 | 0.021904 | 0.82379 | 0 | 0 | 1 | 0.15788 | 0.021904 | 1
8439 | 0.11834 | 0.017293 | 0.82379 | 0 | 0 | 1 | 0.11834 | 0.017293 | 1
8440 | 0.028453 | 0 | 0.82379 | 0 | 0 | 1 | 0.028453 | 0 | 1
8441 | 0 | 0.0018156 | 0.82379 | 0 | 0 | 1 | 0 | 0.0018156 | 1
8442 | 0 | 0.00067356 | 0.82379 | 0 | 1 | 1 | 0 | 0.00067356 | 1
8443 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8444 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8445 | 0 | 0.0038368 | 0.82379 | 0 | 1 | 1 | 0 | 0.0038368 | 1
8446 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8447 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8448 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8449 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8450 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8451 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8452 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8453 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8454 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8455 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8456 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8457 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8458 | 0.052769 | 0 | 0.82379 | 0 | 0 | 1 | 0.052769 | 0 | 1
8459 | 0.10642 | 0 | 0.82379 | 0 | 0 | 1 | 0.10642 | 0 | 1
8460 | 0.14429 | 0.0022023 | 0.82379 | 0 | 0 | 1 | 0.14429 | 0.0022023 | 1
8461 | 0.060509 | 0.032658 | 0.82379 | 0 | 0 | 1 | 0.060509 | 0.032658 | 1
8462 | 0.040297 | 0.050919 | 0.82379 | 0 | 0 | 1 | 0.040297 | 0.050919 | 1
8463 | 0.029943 | 0.043485 | 0.82379 | 0 | 0 | 1 | 0.029943 | 0.043485 | 1
8464 | 0 | 0.023752 | 0.82379 | 0 | 0 | 1 | 0 | 0.023752 | 1
8465 | 0 | 0.030481 | 0.82379 | 0 | 0 | 1 | 0 | 0.030481 | 1
8466 | 0 | 0.038655 | 0.82379 | 0 | 1 | 1 | 0 | 0.038655 | 1
8467 | 0 | 0.023769 | 0.82379 | 0 | 1 | 1 | 0 | 0.023769 | 1
8468 | 0 | 0.042103 | 0.82379 | 0 | 1 | 1 | 0 | 0.042103 | 1
8469 | 0 | 0.058295 | 0.82379 | 0 | 1 | 1 | 0 | 0.058295 | 1
8470 | 0 | 0.033053 | 0.82379 | 0 | 0 | 1 | 0 | 0.033053 | 1
8471 | 0 | 0.010132 | 0.82379 | 0 | 0 | 1 | 0 | 0.010132 | 1
8472 | 0 | 0.015287 | 0.82379 | 0 | 0 | 1 | 0 | 0.015287 | 1
8473 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8474 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8475 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8476 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8477 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8478 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8479 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8480 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8481 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8482 | 0.056622 | 0 | 0.82379 | 0 | 0 | 1 | 0.056622 | 0 | 1
8483 | 0.14993 | 0.0017955 | 0.82379 | 0 | 0 | 1 | 0.14993 | 0.0017955 | 1
8484 | 0.20286 | 0.027004 | 0.82379 | 0 | 0 | 1 | 0.20286 | 0.027004 | 1
8485 | 0.11525 | 0.016601 | 0.82379 | 0 | 0 | 1 | 0.11525 | 0.016601 | 1
8486 | 0.035607 | 0.025026 | 0.82379 | 0 | 0 | 1 | 0.035607 | 0.025026 | 1
8487 | 0.0043581 | 0.026065 | 0.82379 | 0 | 0 | 1 | 0.0043581 | 0.026065 | 1
8488 | 0 | 0.018544 | 0.82379 | 0 | 0 | 1 | 0 | 0.018544 | 1
8489 | 0 | 0.01111 | 0.82379 | 0 | 0 | 1 | 0 | 0.01111 | 1
8490 | 0 | 0.006064 | 0.82379 | 0 | 1 | 1 | 0 | 0.006064 | 1
8491 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8492 | 0 | 0.0060654 | 0.82379 | 0 | 1 | 1 | 0 | 0.0060654 | 1
8493 | 0 | 0.036108 | 0.82379 | 0 | 1 | 1 | 0 | 0.036108 | 1
8494 | 0 | 0.025679 | 0.82379 | 0 | 0 | 1 | 0 | 0.025679 | 1
8495 | 0 | 0.005344 | 0.82379 | 0 | 0 | 1 | 0 | 0.005344 | 1
8496 | 0 | 0.010306 | 0.82379 | 0 | 0 | 1 | 0 | 0.010306 | 1
8497 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8498 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8499 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8500 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8501 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8502 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8503 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8504 | 0 | 0 | 0.82379 | 0 | 0 | 1 | 0 | 0 | 1
8505 | 0 | 0.011828 | 0.82379 | 0 | 0 | 1 | 0 | 0.011828 | 1
8506 | 0.13157 | 0.0046518 | 0.82379 | 0 | 0 | 1 | 0.13157 | 0.0046518 | 1
8507 | 0.1764 | 0.0149 | 0.82379 | 0 | 0 | 1 | 0.1764 | 0.0149 | 1
8508 | 0.28252 | 0.044742 | 0.82379 | 0 | 0 | 1 | 0.28252 | 0.044742 | 1
8509 | 0.22009 | 0.042897 | 0.82379 | 0 | 0 | 1 | 0.22009 | 0.042897 | 1
8510 | 0.1155 | 0.040093 | 0.82379 | 0 | 0 | 1 | 0.1155 | 0.040093 | 1
8511 | 0.064492 | 0.035878 | 0.82379 | 0 | 0 | 1 | 0.064492 | 0.035878 | 1
8512 | 0 | 0.029088 | 0.82379 | 0 | 0 | 1 | 0 | 0.029088 | 1
8513 | 0 | 0.012851 | 0.82379 | 0 | 0 | 1 | 0 | 0.012851 | 1
8514 | 0 | 0.0075869 | 0.82379 | 0 | 1 | 1 | 0 | 0.0075869 | 1
8515 | 0 | 0 | 0.82379 | 0 | 1 | 1 | 0 | 0 | 1
8516 | 0 | 0.0070981 | 0.82379 | 0 | 1 | 1 | 0 | 0.0070981 | 1
8517 | 0 | 0.026084 | 0.82379 | 0 | 1 | 1 | 0 | 0.026084 | 1
8518 | 0 | 0.024692 | 0.82379 | 0 | 0 | 1 | 0 | 0.024692 | 1
8519 | 0 | 0.030359 | 0.82379 | 0 | 0 | 1 | 0 | 0.030359 | 1
8520 | 0 | 0.02654 | 0.82379 | 0 | 0 | 1 | 0 | 0.02654 | 1
8521 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8522 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8523 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8524 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8525 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8526 | 0 | 0.0015529 | 0.90934 | 0 | 0 | 1 | 0 | 0.0015529 | 1
8527 | 0 | 0.0095302 | 0.90934 | 0 | 0 | 1 | 0 | 0.0095302 | 1
8528 | 0 | 0.0057889 | 0.90934 | 0 | 0 | 1 | 0 | 0.0057889 | 1
8529 | 0.011928 | 0.010149 | 0.90934 | 0 | 0 | 1 | 0.011928 | 0.010149 | 1
8530 | 0.22695 | 0.0018615 | 0.90934 | 0 | 0 | 1 | 0.22695 | 0.0018615 | 1
8531 | 0.26502 | 0.013588 | 0.90934 | 0 | 0 | 1 | 0.26502 | 0.013588 | 1
8532 | 0.30773 | 0.043653 | 0.90934 | 0 | 0 | 1 | 0.30773 | 0.043653 | 1
8533 | 0.33273 | 0.033457 | 0.90934 | 0 | 0 | 1 | 0.33273 | 0.033457 | 1
8534 | 0.24394 | 0.03697 | 0.90934 | 0 | 0 | 1 | 0.24394 | 0.03697 | 1
8535 | 0.17185 | 0.037017 | 0.90934 | 0 | 0 | 1 | 0.17185 | 0.037017 | 1
8536 | 0.085343 | 0.040892 | 0.90934 | 0 | 0 | 1 | 0.085343 | 0.040892 | 1
8537 | 0.0071547 | 0.036193 | 0.90934 | 0 | 0 | 1 | 0.0071547 | 0.036193 | 1
8538 | 0 | 0.024632 | 0.90934 | 0 | 1 | 1 | 0 | 0.024632 | 1
8539 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8540 | 0 | 0.017541 | 0.90934 | 0 | 1 | 1 | 0 | 0.017541 | 1
8541 | 0 | 0.033396 | 0.90934 | 0 | 1 | 1 | 0 | 0.033396 | 1
8542 | 0 | 0.038314 | 0.90934 | 0 | 0 | 1 | 0 | 0.038314 | 1
8543 | 0 | 0.03071 | 0.90934 | 0 | 0 | 1 | 0 | 0.03071 | 1
8544 | 0 | 0.022684 | 0.90934 | 0 | 0 | 1 | 0 | 0.022684 | 1
8545 | 0 | 0.00019688 | 0.90934 | 0 | 0 | 1 | 0 | 0.00019688 | 1
8546 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8547 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8548 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8549 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8550 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8551 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8552 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8553 | 0 | 0.0088446 | 0.90934 | 0 | 0 | 1 | 0 | 0.0088446 | 1
8554 | 0.18127 | 0 | 0.90934 | 0 | 0 | 1 | 0.18127 | 0 | 1
8555 | 0.23057 | 0.011178 | 0.90934 | 0 | 0 | 1 | 0.23057 | 0.011178 | 1
8556 | 0.29111 | 0.038988 | 0.90934 | 0 | 0 | 1 | 0.29111 | 0.038988 | 1
8557 | 0.32034 | 0.039407 | 0.90934 | 0 | 0 | 1 | 0.32034 | 0.039407 | 1
8558 | 0.27061 | 0.041403 | 0.90934 | 0 | 0 | 1 | 0.27061 | 0.041403 | 1
8559 | 0.20311 | 0.043268 | 0.90934 | 0 | 0 | 1 | 0.20311 | 0.043268 | 1
8560 | 0.084667 | 0.046289 | 0.90934 | 0 | 0 | 1 | 0.084667 | 0.046289 | 1
8561 | 0.0016264 | 0.043609 | 0.90934 | 0 | 0 | 1 | 0.0016264 | 0.043609 | 1
8562 | 0 | 0.033141 | 0.90934 | 0 | 1 | 1 | 0 | 0.033141 | 1
8563 | 0 | 0.0075784 | 0.90934 | 0 | 1 | 1 | 0 | 0.0075784 | 1
8564 | 0 | 0.023126 | 0.90934 | 0 | 1 | 1 | 0 | 0.023126 | 1
8565 | 0 | 0.031665 | 0.90934 | 0 | 1 | 1 | 0 | 0.031665 | 1
8566 | 0 | 0.034119 | 0.90934 | 0 | 0 | 1 | 0 | 0.034119 | 1
8567 | 0 | 0.028688 | 0.90934 | 0 | 0 | 1 | 0 | 0.028688 | 1
8568 | 0 | 0.021069 | 0.90934 | 0 | 0 | 1 | 0 | 0.021069 | 1
8569 | 0 | 0.0024507 | 0.90934 | 0 | 0 | 1 | 0 | 0.0024507 | 1
8570 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8571 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8572 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8573 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8574 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8575 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8576 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8577 | 0.010657 | 0 | 0.90934 | 0 | 0 | 1 | 0.010657 | 0 | 1
8578 | 0.20963 | 0.0025481 | 0.90934 | 0 | 0 | 1 | 0.20963 | 0.0025481 | 1
8579 | 0.28006 | 0.029665 | 0.90934 | 0 | 0 | 1 | 0.28006 | 0.029665 | 1
8580 | 0.28005 | 0.040008 | 0.90934 | 0 | 0 | 1 | 0.28005 | 0.040008 | 1
8581 | 0.25499 | 0.035191 | 0.90934 | 0 | 0 | 1 | 0.25499 | 0.035191 | 1
8582 | 0.29309 | 0.042973 | 0.90934 | 0 | 0 | 1 | 0.29309 | 0.042973 | 1
8583 | 0.27754 | 0.050375 | 0.90934 | 0 | 0 | 1 | 0.27754 | 0.050375 | 1
8584 | 0.13586 | 0.062656 | 0.90934 | 0 | 0 | 1 | 0.13586 | 0.062656 | 1
8585 | 0.0058458 | 0.053603 | 0.90934 | 0 | 0 | 1 | 0.0058458 | 0.053603 | 1
8586 | 0 | 0.038191 | 0.90934 | 0 | 1 | 1 | 0 | 0.038191 | 1
8587 | 0 | 0.014893 | 0.90934 | 0 | 1 | 1 | 0 | 0.014893 | 1
8588 | 0 | 0.017782 | 0.90934 | 0 | 1 | 1 | 0 | 0.017782 | 1
8589 | 0 | 0.026045 | 0.90934 | 0 | 1 | 1 | 0 | 0.026045 | 1
8590 | 0 | 0.015211 | 0.90934 | 0 | 0 | 1 | 0 | 0.015211 | 1
8591 | 0 | 5.0822e-06 | 0.90934 | 0 | 0 | 1 | 0 | 5.0822e-06 | 1
8592 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8593 | 0 | 0.0029039 | 0.90934 | 0 | 0 | 1 | 0 | 0.0029039 | 1
8594 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8595 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8596 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8597 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8598 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8599 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8600 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8601 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8602 | 0.10935 | 0 | 0.90934 | 0 | 0 | 1 | 0.10935 | 0 | 1
8603 | 0.18542 | 0 | 0.90934 | 0 | 0 | 1 | 0.18542 | 0 | 1
8604 | 0.16635 | 0 | 0.90934 | 0 | 0 | 1 | 0.16635 | 0 | 1
8605 | 0.11944 | 0 | 0.90934 | 0 | 0 | 1 | 0.11944 | 0 | 1
8606 | 0.16731 | 0 | 0.90934 | 0 | 0 | 1 | 0.16731 | 0 | 1
8607 | 0.15488 | 0.013862 | 0.90934 | 0 | 0 | 1 | 0.15488 | 0.013862 | 1
8608 | 0.040227 | 0.010884 | 0.90934 | 0 | 0 | 1 | 0.040227 | 0.010884 | 1
8609 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8610 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8611 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8612 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8613 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8614 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8615 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8616 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8617 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8618 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8619 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8620 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8621 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8622 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8623 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8624 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8625 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8626 | 0.14178 | 0 | 0.90934 | 0 | 0 | 1 | 0.14178 | 0 | 1
8627 | 0.21844 | 0 | 0.90934 | 0 | 0 | 1 | 0.21844 | 0 | 1
8628 | 0.19886 | 0 | 0.90934 | 0 | 0 | 1 | 0.19886 | 0 | 1
8629 | 0.12019 | 0 | 0.90934 | 0 | 0 | 1 | 0.12019 | 0 | 1
8630 | 0.17223 | 0 | 0.90934 | 0 | 0 | 1 | 0.17223 | 0 | 1
8631 | 0.1634 | 0 | 0.90934 | 0 | 0 | 1 | 0.1634 | 0 | 1
8632 | 0.065672 | 0 | 0.90934 | 0 | 0 | 1 | 0.065672 | 0 | 1
8633 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8634 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8635 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8636 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8637 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8638 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8639 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8640 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8641 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8642 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8643 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8644 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8645 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8646 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8647 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8648 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8649 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8650 | 0.05999 | 0 | 0.90934 | 0 | 0 | 1 | 0.05999 | 0 | 1
8651 | 0.087423 | 0 | 0.90934 | 0 | 0 | 1 | 0.087423 | 0 | 1
8652 | 0.065812 | 0 | 0.90934 | 0 | 0 | 1 | 0.065812 | 0 | 1
8653 | 0.046338 | 0 | 0.90934 | 0 | 0 | 1 | 0.046338 | 0 | 1
8654 | 0.07159 | 0 | 0.90934 | 0 | 0 | 1 | 0.07159 | 0 | 1
8655 | 0.049913 | 0 | 0.90934 | 0 | 0 | 1 | 0.049913 | 0 | 1
8656 | 0.0011014 | 0 | 0.90934 | 0 | 0 | 1 | 0.0011014 | 0 | 1
8657 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8658 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8659 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8660 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8661 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8662 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8663 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8664 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8665 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8666 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8667 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8668 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8669 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8670 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8671 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8672 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8673 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8674 | 0.052552 | 0 | 0.90934 | 0 | 0 | 1 | 0.052552 | 0 | 1
8675 | 0.18272 | 0 | 0.90934 | 0 | 0 | 1 | 0.18272 | 0 | 1
8676 | 0.19664 | 0 | 0.90934 | 0 | 0 | 1 | 0.19664 | 0 | 1
8677 | 0.181 | 0 | 0.90934 | 0 | 0 | 1 | 0.181 | 0 | 1
8678 | 0.18898 | 0 | 0.90934 | 0 | 0 | 1 | 0.18898 | 0 | 1
8679 | 0.15924 | 0 | 0.90934 | 0 | 0 | 1 | 0.15924 | 0 | 1
8680 | 0.096722 | 0 | 0.90934 | 0 | 0 | 1 | 0.096722 | 0 | 1
8681 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8682 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8683 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8684 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8685 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8686 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8687 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8688 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8689 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8690 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8691 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8692 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8693 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8694 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8695 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8696 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8697 | 0 | 0.00013538 | 0.90934 | 0 | 0 | 1 | 0 | 0.00013538 | 1
8698 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8699 | 0.06749 | 0.0043324 | 0.90934 | 0 | 0 | 1 | 0.06749 | 0.0043324 | 1
8700 | 0.13018 | 0.0272 | 0.90934 | 0 | 0 | 1 | 0.13018 | 0.0272 | 1
8701 | 0.1148 | 0.058783 | 0.90934 | 0 | 0 | 1 | 0.1148 | 0.058783 | 1
8702 | 0.092121 | 0.06238 | 0.90934 | 0 | 0 | 1 | 0.092121 | 0.06238 | 1
8703 | 0.1105 | 0.025573 | 0.90934 | 0 | 0 | 1 | 0.1105 | 0.025573 | 1
8704 | 0.088045 | 0.010451 | 0.90934 | 0 | 0 | 1 | 0.088045 | 0.010451 | 1
8705 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8706 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8707 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8708 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8709 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8710 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8711 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8712 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8713 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8714 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8715 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8716 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8717 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8718 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8719 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8720 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8721 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8722 | 0.030034 | 0 | 0.90934 | 0 | 0 | 1 | 0.030034 | 0 | 1
8723 | 0.20123 | 0.0048204 | 0.90934 | 0 | 0 | 1 | 0.20123 | 0.0048204 | 1
8724 | 0.3082 | 0.030841 | 0.90934 | 0 | 0 | 1 | 0.3082 | 0.030841 | 1
8725 | 0.2727 | 0.036878 | 0.90934 | 0 | 0 | 1 | 0.2727 | 0.036878 | 1
8726 | 0.26408 | 0.0521 | 0.90934 | 0 | 0 | 1 | 0.26408 | 0.0521 | 1
8727 | 0.26436 | 0.039302 | 0.90934 | 0 | 0 | 1 | 0.26436 | 0.039302 | 1
8728 | 0.16347 | 0.036115 | 0.90934 | 0 | 0 | 1 | 0.16347 | 0.036115 | 1
8729 | 0 | 0.031882 | 0.90934 | 0 | 0 | 1 | 0 | 0.031882 | 1
8730 | 0 | 0.032139 | 0.90934 | 0 | 1 | 1 | 0 | 0.032139 | 1
8731 | 0 | 0.029216 | 0.90934 | 0 | 1 | 1 | 0 | 0.029216 | 1
8732 | 0 | 0.0097568 | 0.90934 | 0 | 1 | 1 | 0 | 0.0097568 | 1
8733 | 0 | 0 | 0.90934 | 0 | 1 | 1 | 0 | 0 | 1
8734 | 0 | 0.0084342 | 0.90934 | 0 | 0 | 1 | 0 | 0.0084342 | 1
8735 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8736 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8737 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8738 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8739 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8740 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8741 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8742 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8743 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8744 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8745 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8746 | 0.11534 | 0 | 0.90934 | 0 | 0 | 1 | 0.11534 | 0 | 1
8747 | 0.21303 | 0 | 0.90934 | 0 | 0 | 1 | 0.21303 | 0 | 1
8748 | 0.31407 | 0.010538 | 0.90934 | 0 | 0 | 1 | 0.31407 | 0.010538 | 1
8749 | 0.2535 | 0.014059 | 0.90934 | 0 | 0 | 1 | 0.2535 | 0.014059 | 1
8750 | 0.22975 | 0.025075 | 0.90934 | 0 | 0 | 1 | 0.22975 | 0.025075 | 1
8751 | 0.23113 | 0.030222 | 0.90934 | 0 | 0 | 1 | 0.23113 | 0.030222 | 1
8752 | 0.15406 | 0.051712 | 0.90934 | 0 | 0 | 1 | 0.15406 | 0.051712 | 1
8753 | 0 | 0.036675 | 0.90934 | 0 | 0 | 1 | 0 | 0.036675 | 1
8754 | 0 | 0.037807 | 0.90934 | 0 | 1 | 1 | 0 | 0.037807 | 1
8755 | 0 | 0.043229 | 0.90934 | 0 | 1 | 1 | 0 | 0.043229 | 1
8756 | 0 | 0.033433 | 0.90934 | 0 | 1 | 1 | 0 | 0.033433 | 1
8757 | 0 | 0.022723 | 0.90934 | 0 | 1 | 1 | 0 | 0.022723 | 1
8758 | 0 | 0.022792 | 0.90934 | 0 | 0 | 1 | 0 | 0.022792 | 1
8759 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1
8760 | 0 | 0 | 0.90934 | 0 | 0 | 1 | 0 | 0 | 1

## erm_timepoint_params
ERM Timepoint Params |  | Index
erm_hour | input_load_mw
1 | 0.57795
2 | 0.54254
3 | 0.51308
4 | 0.49466
5 | 0.49803
6 | 0.51603
7 | 0.5586
8 | 0.58897
9 | 0.58137
10 | 0.53258
11 | 0.47629
12 | 0.4524
13 | 0.44111
14 | 0.45614
15 | 0.521
16 | 0.5766
17 | 0.69442
18 | 0.77503
19 | 0.85466
20 | 0.84439
21 | 0.81992
22 | 0.77162
23 | 0.69964
24 | 0.61368
25 | 0.57795
26 | 0.55792
27 | 0.52883
28 | 0.50995
29 | 0.52602
30 | 0.57031
31 | 0.63092
32 | 0.65344
33 | 0.66325
34 | 0.62039
35 | 0.59767
36 | 0.5835
37 | 0.54316
38 | 0.53898
39 | 0.56545
40 | 0.65989
41 | 0.75162
42 | 0.82631
43 | 0.8874
44 | 0.86693
45 | 0.83031
46 | 0.78702
47 | 0.71365
48 | 0.6314
49 | 0.59315
50 | 0.52237
51 | 0.49517
52 | 0.48501
53 | 0.51518
54 | 0.60404
55 | 0.71502
56 | 0.73122
57 | 0.69284
58 | 0.62789
59 | 0.57458
60 | 0.54683
61 | 0.56063
62 | 0.5487
63 | 0.55466
64 | 0.61621
65 | 0.72191
66 | 0.80048
67 | 0.86753
68 | 0.87436
69 | 0.83175
70 | 0.76019
71 | 0.68359
72 | 0.59907
73 | 0.55453
74 | 0.50702
75 | 0.47863
76 | 0.47002
77 | 0.49613
78 | 0.57844
79 | 0.68509
80 | 0.69974
81 | 0.64708
82 | 0.58617
83 | 0.53793
84 | 0.50301
85 | 0.48578
86 | 0.50103
87 | 0.53437
88 | 0.6047
89 | 0.69688
90 | 0.77556
91 | 0.838
92 | 0.83902
93 | 0.79789
94 | 0.7366
95 | 0.66642
96 | 0.58277
97 | 0.53155
98 | 0.50172
99 | 0.47541
100 | 0.46986
101 | 0.4936
102 | 0.576
103 | 0.68136
104 | 0.68858
105 | 0.63082
106 | 0.57901
107 | 0.53392
108 | 0.49589
109 | 0.50782
110 | 0.51267
111 | 0.50378
112 | 0.5885
113 | 0.68126
114 | 0.75627
115 | 0.8264
116 | 0.84057
117 | 0.80099
118 | 0.73546
119 | 0.65872
120 | 0.57807
121 | 0.5225
122 | 0.51748
123 | 0.48622
124 | 0.47443
125 | 0.50021
126 | 0.58116
127 | 0.68765
128 | 0.70325
129 | 0.65988
130 | 0.59588
131 | 0.53516
132 | 0.49288
133 | 0.4894
134 | 0.49354
135 | 0.52488
136 | 0.59655
137 | 0.6856
138 | 0.75767
139 | 0.81784
140 | 0.81724
141 | 0.77821
142 | 0.72645
143 | 0.67598
144 | 0.60137
145 | 0.54295
146 | 0.5213
147 | 0.4886
148 | 0.47333
149 | 0.47782
150 | 0.50173
151 | 0.56084
152 | 0.58865
153 | 0.56994
154 | 0.52682
155 | 0.47613
156 | 0.43846
157 | 0.41835
158 | 0.40918
159 | 0.42413
160 | 0.50904
161 | 0.61918
162 | 0.71454
163 | 0.78646
164 | 0.78187
165 | 0.75512
166 | 0.70644
167 | 0.66479
168 | 0.59933
169 | 0.55404
170 | 0.54316
171 | 0.51379
172 | 0.4936
173 | 0.49622
174 | 0.51314
175 | 0.55942
176 | 0.58794
177 | 0.5759
178 | 0.54061
179 | 0.48694
180 | 0.4594
181 | 0.42798
182 | 0.42136
183 | 0.45781
184 | 0.54898
185 | 0.67237
186 | 0.76384
187 | 0.85395
188 | 0.84358
189 | 0.82116
190 | 0.76534
191 | 0.69595
192 | 0.61101
193 | 0.57657
194 | 0.50862
195 | 0.48357
196 | 0.47653
197 | 0.50385
198 | 0.59261
199 | 0.70446
200 | 0.72512
201 | 0.67247
202 | 0.61273
203 | 0.5787
204 | 0.55893
205 | 0.52476
206 | 0.51455
207 | 0.53367
208 | 0.60433
209 | 0.70868
210 | 0.78629
211 | 0.8694
212 | 0.86788
213 | 0.82219
214 | 0.75453
215 | 0.68042
216 | 0.59438
217 | 0.54208
218 | 0.53488
219 | 0.50984
220 | 0.49876
221 | 0.52581
222 | 0.61594
223 | 0.72761
224 | 0.74678
225 | 0.70279
226 | 0.64288
227 | 0.5882
228 | 0.54438
229 | 0.55399
230 | 0.54192
231 | 0.55445
232 | 0.64427
233 | 0.73678
234 | 0.81438
235 | 0.88707
236 | 0.88675
237 | 0.84645
238 | 0.77333
239 | 0.69978
240 | 0.61355
241 | 0.56468
242 | 0.52515
243 | 0.49825
244 | 0.49045
245 | 0.51566
246 | 0.60082
247 | 0.70807
248 | 0.72701
249 | 0.68059
250 | 0.62733
251 | 0.60127
252 | 0.58209
253 | 0.55948
254 | 0.5428
255 | 0.55642
256 | 0.61777
257 | 0.7209
258 | 0.80004
259 | 0.87038
260 | 0.86253
261 | 0.82247
262 | 0.76217
263 | 0.69432
264 | 0.60673
265 | 0.54869
266 | 0.52214
267 | 0.50417
268 | 0.49616
269 | 0.52366
270 | 0.60715
271 | 0.71464
272 | 0.72982
273 | 0.677
274 | 0.61204
275 | 0.56679
276 | 0.53013
277 | 0.51821
278 | 0.51043
279 | 0.54093
280 | 0.61528
281 | 0.70997
282 | 0.79665
283 | 0.87181
284 | 0.87584
285 | 0.83763
286 | 0.7727
287 | 0.6971
288 | 0.61249
289 | 0.55337
290 | 0.53481
291 | 0.50716
292 | 0.49694
293 | 0.51975
294 | 0.60248
295 | 0.70856
296 | 0.72938
297 | 0.67888
298 | 0.60514
299 | 0.55588
300 | 0.50231
301 | 0.47691
302 | 0.49005
303 | 0.52481
304 | 0.6123
305 | 0.70475
306 | 0.78179
307 | 0.8481
308 | 0.84106
309 | 0.80198
310 | 0.75312
311 | 0.69922
312 | 0.62336
313 | 0.55944
314 | 0.54806
315 | 0.5193
316 | 0.50258
317 | 0.5062
318 | 0.53409
319 | 0.59391
320 | 0.63366
321 | 0.62373
322 | 0.58283
323 | 0.53068
324 | 0.50121
325 | 0.46659
326 | 0.45168
327 | 0.49288
328 | 0.58152
329 | 0.6874
330 | 0.76434
331 | 0.83254
332 | 0.8195
333 | 0.79233
334 | 0.7489
335 | 0.70189
336 | 0.6342
337 | 0.58127
338 | 0.53052
339 | 0.50308
340 | 0.48507
341 | 0.48534
342 | 0.49823
343 | 0.541
344 | 0.56819
345 | 0.56935
346 | 0.53523
347 | 0.48666
348 | 0.45346
349 | 0.43536
350 | 0.43484
351 | 0.4698
352 | 0.55612
353 | 0.66249
354 | 0.74318
355 | 0.83244
356 | 0.82409
357 | 0.80066
358 | 0.74702
359 | 0.67412
360 | 0.59282
361 | 0.56353
362 | 0.54891
363 | 0.52284
364 | 0.50545
365 | 0.51667
366 | 0.55465
367 | 0.61438
368 | 0.63605
369 | 0.6484
370 | 0.60949
371 | 0.58662
372 | 0.54945
373 | 0.52351
374 | 0.50816
375 | 0.51424
376 | 0.60232
377 | 0.71298
378 | 0.79129
379 | 0.86853
380 | 0.85148
381 | 0.81444
382 | 0.76711
383 | 0.69253
384 | 0.6146
385 | 0.5824
386 | 0.52802
387 | 0.50589
388 | 0.49745
389 | 0.5248
390 | 0.61095
391 | 0.72118
392 | 0.74084
393 | 0.70681
394 | 0.64854
395 | 0.60736
396 | 0.56742
397 | 0.54761
398 | 0.54898
399 | 0.55893
400 | 0.6222
401 | 0.71463
402 | 0.80482
403 | 0.88286
404 | 0.88394
405 | 0.84194
406 | 0.76791
407 | 0.69109
408 | 0.60864
409 | 0.56031
410 | 0.52198
411 | 0.4963
412 | 0.48874
413 | 0.51603
414 | 0.59975
415 | 0.70636
416 | 0.72256
417 | 0.66802
418 | 0.59715
419 | 0.54789
420 | 0.50982
421 | 0.48336
422 | 0.49584
423 | 0.51835
424 | 0.59374
425 | 0.70208
426 | 0.78565
427 | 0.86597
428 | 0.86135
429 | 0.81895
430 | 0.75894
431 | 0.68804
432 | 0.60338
433 | 0.54541
434 | 0.51795
435 | 0.48946
436 | 0.48909
437 | 0.51574
438 | 0.6011
439 | 0.70405
440 | 0.71961
441 | 0.66774
442 | 0.60138
443 | 0.55583
444 | 0.51158
445 | 0.49147
446 | 0.49921
447 | 0.52109
448 | 0.59396
449 | 0.69273
450 | 0.77795
451 | 0.85465
452 | 0.86348
453 | 0.82589
454 | 0.76093
455 | 0.67919
456 | 0.59989
457 | 0.54346
458 | 0.51708
459 | 0.48961
460 | 0.48303
461 | 0.50845
462 | 0.58494
463 | 0.686
464 | 0.70066
465 | 0.6781
466 | 0.62164
467 | 0.55927
468 | 0.54541
469 | 0.55547
470 | 0.55515
471 | 0.59157
472 | 0.6554
473 | 0.71351
474 | 0.75784
475 | 0.82216
476 | 0.8214
477 | 0.78101
478 | 0.72662
479 | 0.67751
480 | 0.59853
481 | 0.54115
482 | 0.54349
483 | 0.51505
484 | 0.50088
485 | 0.50494
486 | 0.53077
487 | 0.58849
488 | 0.62285
489 | 0.61305
490 | 0.58286
491 | 0.53583
492 | 0.50586
493 | 0.46906
494 | 0.44671
495 | 0.46946
496 | 0.55906
497 | 0.65783
498 | 0.74763
499 | 0.82283
500 | 0.81364
501 | 0.78783
502 | 0.7401
503 | 0.69643
504 | 0.62534
505 | 0.57425
506 | 0.53498
507 | 0.50788
508 | 0.49197
509 | 0.49363
510 | 0.50556
511 | 0.54757
512 | 0.57274
513 | 0.57626
514 | 0.5466
515 | 0.50476
516 | 0.46052
517 | 0.42748
518 | 0.43061
519 | 0.45405
520 | 0.53628
521 | 0.63574
522 | 0.73591
523 | 0.83746
524 | 0.82968
525 | 0.80739
526 | 0.75475
527 | 0.68236
528 | 0.59628
529 | 0.56609
530 | 0.49006
531 | 0.46496
532 | 0.4634
533 | 0.49146
534 | 0.57276
535 | 0.67808
536 | 0.69166
537 | 0.64222
538 | 0.57671
539 | 0.51631
540 | 0.50751
541 | 0.50711
542 | 0.52496
543 | 0.53302
544 | 0.59297
545 | 0.68322
546 | 0.74119
547 | 0.83693
548 | 0.84444
549 | 0.79814
550 | 0.72754
551 | 0.64934
552 | 0.56486
553 | 0.52214
554 | 0.50331
555 | 0.47735
556 | 0.47246
557 | 0.50062
558 | 0.5815
559 | 0.68629
560 | 0.702
561 | 0.65996
562 | 0.60497
563 | 0.56052
564 | 0.52456
565 | 0.51865
566 | 0.51026
567 | 0.5124
568 | 0.57223
569 | 0.66236
570 | 0.74628
571 | 0.83522
572 | 0.84866
573 | 0.80484
574 | 0.73066
575 | 0.65273
576 | 0.56902
577 | 0.53144
578 | 0.50509
579 | 0.47818
580 | 0.47334
581 | 0.50047
582 | 0.58302
583 | 0.68747
584 | 0.70079
585 | 0.65324
586 | 0.60142
587 | 0.54573
588 | 0.52808
589 | 0.53435
590 | 0.53448
591 | 0.54365
592 | 0.59636
593 | 0.67541
594 | 0.75356
595 | 0.83857
596 | 0.83619
597 | 0.79414
598 | 0.73307
599 | 0.6642
600 | 0.57963
601 | 0.52939
602 | 0.5288
603 | 0.50679
604 | 0.49546
605 | 0.52943
606 | 0.61753
607 | 0.72569
608 | 0.74139
609 | 0.68945
610 | 0.62069
611 | 0.56345
612 | 0.51594
613 | 0.49456
614 | 0.50619
615 | 0.52229
616 | 0.60539
617 | 0.6969
618 | 0.78774
619 | 0.8802
620 | 0.87985
621 | 0.84175
622 | 0.77741
623 | 0.69849
624 | 0.61577
625 | 0.55564
626 | 0.52082
627 | 0.49398
628 | 0.48833
629 | 0.5161
630 | 0.5971
631 | 0.69846
632 | 0.71441
633 | 0.67367
634 | 0.60526
635 | 0.55741
636 | 0.53403
637 | 0.53372
638 | 0.53092
639 | 0.57483
640 | 0.65493
641 | 0.71169
642 | 0.76451
643 | 0.83227
644 | 0.82766
645 | 0.78851
646 | 0.74023
647 | 0.68504
648 | 0.60839
649 | 0.54623
650 | 0.52413
651 | 0.49694
652 | 0.48452
653 | 0.49076
654 | 0.51458
655 | 0.57056
656 | 0.59944
657 | 0.57397
658 | 0.52792
659 | 0.48857
660 | 0.4764
661 | 0.4668
662 | 0.43117
663 | 0.42352
664 | 0.51303
665 | 0.61809
666 | 0.70893
667 | 0.80256
668 | 0.79233
669 | 0.76425
670 | 0.71597
671 | 0.67085
672 | 0.60353
673 | 0.55454
674 | 0.52871
675 | 0.50371
676 | 0.48844
677 | 0.49237
678 | 0.50543
679 | 0.54538
680 | 0.57371
681 | 0.57454
682 | 0.5345
683 | 0.49127
684 | 0.44307
685 | 0.42772
686 | 0.4227
687 | 0.44197
688 | 0.5255
689 | 0.64654
690 | 0.73848
691 | 0.84118
692 | 0.82883
693 | 0.8058
694 | 0.74881
695 | 0.677
696 | 0.59223
697 | 0.55947
698 | 0.5173
699 | 0.49499
700 | 0.49133
701 | 0.52067
702 | 0.61053
703 | 0.71779
704 | 0.73696
705 | 0.68089
706 | 0.61681
707 | 0.56114
708 | 0.54147
709 | 0.52167
710 | 0.52257
711 | 0.52722
712 | 0.60659
713 | 0.7
714 | 0.78545
715 | 0.89453
716 | 0.88639
717 | 0.8409
718 | 0.77126
719 | 0.69479
720 | 0.60601
721 | 0.54828
722 | 0.52906
723 | 0.50738
724 | 0.49913
725 | 0.52995
726 | 0.61832
727 | 0.7263
728 | 0.74247
729 | 0.70535
730 | 0.64288
731 | 0.59181
732 | 0.54742
733 | 0.53021
734 | 0.52198
735 | 0.54801
736 | 0.6195
737 | 0.70349
738 | 0.79306
739 | 0.88692
740 | 0.88608
741 | 0.84563
742 | 0.77051
743 | 0.69173
744 | 0.60721
745 | 0.5581
746 | 0.52939
747 | 0.5021
748 | 0.49206
749 | 0.52185
750 | 0.60891
751 | 0.70194
752 | 0.71558
753 | 0.64225
754 | 0.55286
755 | 0.51252
756 | 0.5037
757 | 0.47531
758 | 0.48392
759 | 0.48841
760 | 0.54586
761 | 0.64393
762 | 0.74142
763 | 0.81875
764 | 0.83137
765 | 0.79931
766 | 0.74236
767 | 0.66926
768 | 0.59754
769 | 0.54171
770 | 0.51784
771 | 0.49263
772 | 0.48462
773 | 0.50939
774 | 0.60094
775 | 0.69167
776 | 0.70338
777 | 0.64016
778 | 0.58194
779 | 0.54592
780 | 0.4799
781 | 0.41958
782 | 0.44073
783 | 0.49779
784 | 0.54199
785 | 0.64447
786 | 0.71824
787 | 0.79665
788 | 0.8264
789 | 0.79585
790 | 0.73511
791 | 0.65528
792 | 0.58503
793 | 0.53379
794 | 0.51977
795 | 0.49111
796 | 0.48251
797 | 0.51275
798 | 0.59616
799 | 0.68442
800 | 0.70035
801 | 0.66069
802 | 0.59487
803 | 0.54243
804 | 0.50836
805 | 0.46928
806 | 0.46578
807 | 0.4849
808 | 0.53872
809 | 0.63287
810 | 0.7104
811 | 0.77456
812 | 0.79461
813 | 0.76638
814 | 0.71503
815 | 0.6597
816 | 0.59135
817 | 0.53432
818 | 0.52137
819 | 0.49364
820 | 0.48118
821 | 0.4924
822 | 0.52719
823 | 0.57681
824 | 0.60252
825 | 0.57208
826 | 0.53168
827 | 0.47867
828 | 0.44789
829 | 0.42688
830 | 0.41235
831 | 0.4089
832 | 0.47062
833 | 0.58163
834 | 0.67556
835 | 0.74826
836 | 0.76487
837 | 0.7444
838 | 0.69993
839 | 0.6484
840 | 0.58859
841 | 0.54531
842 | 0.53133
843 | 0.50633
844 | 0.49084
845 | 0.49983
846 | 0.52676
847 | 0.56317
848 | 0.58483
849 | 0.56134
850 | 0.49292
851 | 0.45004
852 | 0.41034
853 | 0.42303
854 | 0.41284
855 | 0.41829
856 | 0.47837
857 | 0.58043
858 | 0.69225
859 | 0.79107
860 | 0.80399
861 | 0.78882
862 | 0.73563
863 | 0.66251
864 | 0.58737
865 | 0.55544
866 | 0.51667
867 | 0.49542
868 | 0.48882
869 | 0.51871
870 | 0.60875
871 | 0.70364
872 | 0.71774
873 | 0.66388
874 | 0.59719
875 | 0.55619
876 | 0.55219
877 | 0.51521
878 | 0.50708
879 | 0.49362
880 | 0.55006
881 | 0.65251
882 | 0.74226
883 | 0.82998
884 | 0.84775
885 | 0.81178
886 | 0.74633
887 | 0.66981
888 | 0.59366
889 | 0.54105
890 | 0.52836
891 | 0.50547
892 | 0.49622
893 | 0.52637
894 | 0.61626
895 | 0.70983
896 | 0.72212
897 | 0.63399
898 | 0.53972
899 | 0.48231
900 | 0.44392
901 | 0.41823
902 | 0.43616
903 | 0.44434
904 | 0.51979
905 | 0.62566
906 | 0.72508
907 | 0.82078
908 | 0.8457
909 | 0.81528
910 | 0.74685
911 | 0.66957
912 | 0.59468
913 | 0.54927
914 | 0.52271
915 | 0.49794
916 | 0.48719
917 | 0.51679
918 | 0.60455
919 | 0.69701
920 | 0.7073
921 | 0.62308
922 | 0.52213
923 | 0.45418
924 | 0.43309
925 | 0.40428
926 | 0.4146
927 | 0.45015
928 | 0.51758
929 | 0.61981
930 | 0.72247
931 | 0.80699
932 | 0.82571
933 | 0.79314
934 | 0.73606
935 | 0.66466
936 | 0.59093
937 | 0.53772
938 | 0.53262
939 | 0.5089
940 | 0.49867
941 | 0.5294
942 | 0.61425
943 | 0.71171
944 | 0.72018
945 | 0.63709
946 | 0.54763
947 | 0.48979
948 | 0.45267
949 | 0.41919
950 | 0.43129
951 | 0.44699
952 | 0.51476
953 | 0.63075
954 | 0.73386
955 | 0.82431
956 | 0.84688
957 | 0.81919
958 | 0.75677
959 | 0.67781
960 | 0.60726
961 | 0.54866
962 | 0.53811
963 | 0.51149
964 | 0.50023
965 | 0.53047
966 | 0.61926
967 | 0.70951
968 | 0.72591
969 | 0.67416
970 | 0.57756
971 | 0.52406
972 | 0.47116
973 | 0.46752
974 | 0.46955
975 | 0.49793
976 | 0.57008
977 | 0.65062
978 | 0.73245
979 | 0.80625
980 | 0.81832
981 | 0.79142
982 | 0.74038
983 | 0.68965
984 | 0.6203
985 | 0.55509
986 | 0.53088
987 | 0.49943
988 | 0.48631
989 | 0.49978
990 | 0.53644
991 | 0.58891
992 | 0.61191
993 | 0.57726
994 | 0.51543
995 | 0.46434
996 | 0.43281
997 | 0.39956
998 | 0.38996
999 | 0.39339
1000 | 0.45089
1001 | 0.56418
1002 | 0.6746
1003 | 0.75943
1004 | 0.77455
1005 | 0.75704
1006 | 0.70864
1007 | 0.66151
1008 | 0.60211
1009 | 0.55173
1010 | 0.53383
1011 | 0.50549
1012 | 0.48997
1013 | 0.50133
1014 | 0.52889
1015 | 0.56939
1016 | 0.58978
1017 | 0.55257
1018 | 0.48495
1019 | 0.41655
1020 | 0.37862
1021 | 0.33317
1022 | 0.32952
1023 | 0.3592
1024 | 0.44825
1025 | 0.58139
1026 | 0.6823
1027 | 0.79314
1028 | 0.80688
1029 | 0.79372
1030 | 0.73744
1031 | 0.6643
1032 | 0.59169
1033 | 0.55642
1034 | 0.5265
1035 | 0.50183
1036 | 0.49688
1037 | 0.52763
1038 | 0.61929
1039 | 0.7164
1040 | 0.73488
1041 | 0.69751
1042 | 0.64682
1043 | 0.62221
1044 | 0.51804
1045 | 0.50687
1046 | 0.51473
1047 | 0.52358
1048 | 0.57735
1049 | 0.67228
1050 | 0.7542
1051 | 0.84422
1052 | 0.86022
1053 | 0.82509
1054 | 0.75817
1055 | 0.68478
1056 | 0.60764
1057 | 0.55034
1058 | 0.53167
1059 | 0.50684
1060 | 0.49741
1061 | 0.52988
1062 | 0.61921
1063 | 0.71521
1064 | 0.72874
1065 | 0.67755
1066 | 0.61572
1067 | 0.56975
1068 | 0.55867
1069 | 0.54475
1070 | 0.53795
1071 | 0.50605
1072 | 0.55379
1073 | 0.64569
1074 | 0.73561
1075 | 0.8265
1076 | 0.85079
1077 | 0.81994
1078 | 0.75059
1079 | 0.67334
1080 | 0.60135
1081 | 0.55202
1082 | 0.53862
1083 | 0.51208
1084 | 0.50297
1085 | 0.53172
1086 | 0.62245
1087 | 0.71742
1088 | 0.73371
1089 | 0.67686
1090 | 0.59713
1091 | 0.51557
1092 | 0.48713
1093 | 0.44877
1094 | 0.46742
1095 | 0.47425
1096 | 0.53221
1097 | 0.63077
1098 | 0.73551
1099 | 0.83401
1100 | 0.84546
1101 | 0.81694
1102 | 0.75957
1103 | 0.68838
1104 | 0.61523
1105 | 0.55349
1106 | 0.52255
1107 | 0.4986
1108 | 0.48939
1109 | 0.51903
1110 | 0.60787
1111 | 0.69617
1112 | 0.70214
1113 | 0.63334
1114 | 0.55031
1115 | 0.4743
1116 | 0.43942
1117 | 0.41275
1118 | 0.43415
1119 | 0.44646
1120 | 0.5004
1121 | 0.60873
1122 | 0.70925
1123 | 0.80704
1124 | 0.83649
1125 | 0.80539
1126 | 0.74615
1127 | 0.66564
1128 | 0.59649
1129 | 0.53886
1130 | 0.52777
1131 | 0.49844
1132 | 0.48873
1133 | 0.5178
1134 | 0.6042
1135 | 0.69709
1136 | 0.70768
1137 | 0.63139
1138 | 0.55153
1139 | 0.5142
1140 | 0.46562
1141 | 0.42485
1142 | 0.43223
1143 | 0.44944
1144 | 0.52305
1145 | 0.61185
1146 | 0.7024
1147 | 0.78631
1148 | 0.80556
1149 | 0.777
1150 | 0.72492
1151 | 0.67009
1152 | 0.60492
1153 | 0.54374
1154 | 0.54422
1155 | 0.51706
1156 | 0.49837
1157 | 0.5121
1158 | 0.55422
1159 | 0.60833
1160 | 0.63192
1161 | 0.59692
1162 | 0.52428
1163 | 0.51085
1164 | 0.50139
1165 | 0.47158
1166 | 0.48389
1167 | 0.47305
1168 | 0.52587
1169 | 0.62402
1170 | 0.70929
1171 | 0.78339
1172 | 0.79583
1173 | 0.77876
1174 | 0.73137
1175 | 0.68309
1176 | 0.62282
1177 | 0.56839
1178 | 0.54109
1179 | 0.51423
1180 | 0.49425
1181 | 0.50584
1182 | 0.53702
1183 | 0.57783
1184 | 0.59449
1185 | 0.57551
1186 | 0.51767
1187 | 0.45688
1188 | 0.40702
1189 | 0.36236
1190 | 0.35389
1191 | 0.40133
1192 | 0.48233
1193 | 0.58287
1194 | 0.69411
1195 | 0.80156
1196 | 0.81624
1197 | 0.80092
1198 | 0.74861
1199 | 0.67714
1200 | 0.60289
1201 | 0.56563
1202 | 0.54361
1203 | 0.51741
1204 | 0.49793
1205 | 0.51974
1206 | 0.56841
1207 | 0.6224
1208 | 0.63308
1209 | 0.6025
1210 | 0.53482
1211 | 0.49754
1212 | 0.46929
1213 | 0.43222
1214 | 0.45515
1215 | 0.45605
1216 | 0.53665
1217 | 0.61634
1218 | 0.71411
1219 | 0.81013
1220 | 0.81841
1221 | 0.79136
1222 | 0.74662
1223 | 0.66863
1224 | 0.60191
1225 | 0.56801
1226 | 0.52444
1227 | 0.50004
1228 | 0.4893
1229 | 0.52212
1230 | 0.61264
1231 | 0.7065
1232 | 0.71079
1233 | 0.65042
1234 | 0.56894
1235 | 0.49881
1236 | 0.46877
1237 | 0.44394
1238 | 0.46986
1239 | 0.4671
1240 | 0.52378
1241 | 0.62631
1242 | 0.72107
1243 | 0.81637
1244 | 0.8437
1245 | 0.81255
1246 | 0.74375
1247 | 0.66785
1248 | 0.59479
1249 | 0.54698
1250 | 0.53301
1251 | 0.50692
1252 | 0.4954
1253 | 0.52689
1254 | 0.61555
1255 | 0.70983
1256 | 0.7202
1257 | 0.64194
1258 | 0.57449
1259 | 0.54207
1260 | 0.51132
1261 | 0.48564
1262 | 0.48691
1263 | 0.50913
1264 | 0.57889
1265 | 0.66471
1266 | 0.73908
1267 | 0.82388
1268 | 0.84142
1269 | 0.80978
1270 | 0.75449
1271 | 0.68286
1272 | 0.60819
1273 | 0.55021
1274 | 0.52456
1275 | 0.5002
1276 | 0.4912
1277 | 0.5209
1278 | 0.60955
1279 | 0.7038
1280 | 0.70353
1281 | 0.644
1282 | 0.54726
1283 | 0.49507
1284 | 0.4499
1285 | 0.43548
1286 | 0.44662
1287 | 0.47529
1288 | 0.51828
1289 | 0.61772
1290 | 0.71388
1291 | 0.81184
1292 | 0.84054
1293 | 0.81426
1294 | 0.7488
1295 | 0.66953
1296 | 0.59868
1297 | 0.5426
1298 | 0.52728
1299 | 0.49856
1300 | 0.4868
1301 | 0.51671
1302 | 0.60164
1303 | 0.69457
1304 | 0.70514
1305 | 0.65858
1306 | 0.57372
1307 | 0.50617
1308 | 0.46451
1309 | 0.45992
1310 | 0.47706
1311 | 0.48671
1312 | 0.55081
1313 | 0.62184
1314 | 0.7058
1315 | 0.78502
1316 | 0.80614
1317 | 0.77527
1318 | 0.72748
1319 | 0.67214
1320 | 0.60507
1321 | 0.5445
1322 | 0.52136
1323 | 0.48964
1324 | 0.47609
1325 | 0.485
1326 | 0.52235
1327 | 0.57749
1328 | 0.59224
1329 | 0.55368
1330 | 0.49177
1331 | 0.44698
1332 | 0.41406
1333 | 0.37812
1334 | 0.38754
1335 | 0.44181
1336 | 0.49567
1337 | 0.56583
1338 | 0.65332
1339 | 0.73987
1340 | 0.75805
1341 | 0.74048
1342 | 0.69509
1343 | 0.64704
1344 | 0.58796
1345 | 0.5442
1346 | 0.52251
1347 | 0.49273
1348 | 0.47564
1349 | 0.48279
1350 | 0.51001
1351 | 0.55112
1352 | 0.56532
1353 | 0.5401
1354 | 0.46001
1355 | 0.40241
1356 | 0.36292
1357 | 0.32366
1358 | 0.33822
1359 | 0.35433
1360 | 0.42204
1361 | 0.5509
1362 | 0.66177
1363 | 0.77329
1364 | 0.79526
1365 | 0.77829
1366 | 0.71981
1367 | 0.64542
1368 | 0.57438
1369 | 0.54516
1370 | 0.49941
1371 | 0.47243
1372 | 0.46661
1373 | 0.49531
1374 | 0.58473
1375 | 0.67915
1376 | 0.68201
1377 | 0.59395
1378 | 0.486
1379 | 0.44069
1380 | 0.42394
1381 | 0.40758
1382 | 0.44882
1383 | 0.47076
1384 | 0.51025
1385 | 0.61722
1386 | 0.69309
1387 | 0.79316
1388 | 0.8206
1389 | 0.78465
1390 | 0.71933
1391 | 0.64236
1392 | 0.56759
1393 | 0.52328
1394 | 0.52957
1395 | 0.5035
1396 | 0.4921
1397 | 0.52207
1398 | 0.61287
1399 | 0.71028
1400 | 0.71813
1401 | 0.6743
1402 | 0.60029
1403 | 0.55152
1404 | 0.53474
1405 | 0.5317
1406 | 0.53161
1407 | 0.56345
1408 | 0.60378
1409 | 0.67414
1410 | 0.73778
1411 | 0.82254
1412 | 0.84989
1413 | 0.81755
1414 | 0.74757
1415 | 0.67108
1416 | 0.59727
1417 | 0.55006
1418 | 0.51124
1419 | 0.48334
1420 | 0.46656
1421 | 0.49252
1422 | 0.57534
1423 | 0.6655
1424 | 0.69541
1425 | 0.63514
1426 | 0.57512
1427 | 0.52211
1428 | 0.48083
1429 | 0.4733
1430 | 0.45793
1431 | 0.48204
1432 | 0.53694
1433 | 0.61787
1434 | 0.71867
1435 | 0.7996
1436 | 0.81597
1437 | 0.77595
1438 | 0.74378
1439 | 0.67375
1440 | 0.59667
1441 | 0.53186
1442 | 0.49426
1443 | 0.46824
1444 | 0.45303
1445 | 0.47787
1446 | 0.55856
1447 | 0.64777
1448 | 0.66516
1449 | 0.59241
1450 | 0.53271
1451 | 0.50015
1452 | 0.45824
1453 | 0.43972
1454 | 0.44171
1455 | 0.41946
1456 | 0.47067
1457 | 0.57661
1458 | 0.67581
1459 | 0.76644
1460 | 0.80123
1461 | 0.7616
1462 | 0.72369
1463 | 0.64565
1464 | 0.57201
1465 | 0.51485
1466 | 0.49344
1467 | 0.46327
1468 | 0.44577
1469 | 0.47133
1470 | 0.54458
1471 | 0.63371
1472 | 0.64916
1473 | 0.58776
1474 | 0.54121
1475 | 0.48441
1476 | 0.4039
1477 | 0.37853
1478 | 0.3976
1479 | 0.45352
1480 | 0.51578
1481 | 0.57799
1482 | 0.65959
1483 | 0.73788
1484 | 0.76064
1485 | 0.72056
1486 | 0.69393
1487 | 0.647
1488 | 0.57469
1489 | 0.51498
1490 | 0.50794
1491 | 0.47863
1492 | 0.45527
1493 | 0.46162
1494 | 0.48769
1495 | 0.53735
1496 | 0.58144
1497 | 0.54672
1498 | 0.51514
1499 | 0.46374
1500 | 0.42404
1501 | 0.39579
1502 | 0.37027
1503 | 0.41526
1504 | 0.49012
1505 | 0.57356
1506 | 0.65527
1507 | 0.73388
1508 | 0.7457
1509 | 0.71931
1510 | 0.69675
1511 | 0.65277
1512 | 0.59036
1513 | 0.53579
1514 | 0.50583
1515 | 0.47661
1516 | 0.45026
1517 | 0.45352
1518 | 0.46597
1519 | 0.50236
1520 | 0.52536
1521 | 0.48389
1522 | 0.4162
1523 | 0.36879
1524 | 0.30164
1525 | 0.27284
1526 | 0.26866
1527 | 0.30713
1528 | 0.37867
1529 | 0.49793
1530 | 0.63393
1531 | 0.75375
1532 | 0.77099
1533 | 0.75033
1534 | 0.71645
1535 | 0.64557
1536 | 0.56797
1537 | 0.53349
1538 | 0.49483
1539 | 0.47012
1540 | 0.45442
1541 | 0.47882
1542 | 0.55814
1543 | 0.65517
1544 | 0.67327
1545 | 0.58561
1546 | 0.51248
1547 | 0.45267
1548 | 0.39792
1549 | 0.38166
1550 | 0.38146
1551 | 0.39301
1552 | 0.46803
1553 | 0.56103
1554 | 0.6812
1555 | 0.80127
1556 | 0.82286
1557 | 0.78415
1558 | 0.74085
1559 | 0.66569
1560 | 0.58458
1561 | 0.52533
1562 | 0.50675
1563 | 0.48125
1564 | 0.46053
1565 | 0.48584
1566 | 0.5649
1567 | 0.66257
1568 | 0.67595
1569 | 0.59206
1570 | 0.50788
1571 | 0.44254
1572 | 0.40915
1573 | 0.39704
1574 | 0.41842
1575 | 0.45008
1576 | 0.51326
1577 | 0.6082
1578 | 0.70572
1579 | 0.79863
1580 | 0.82404
1581 | 0.78717
1582 | 0.74143
1583 | 0.664
1584 | 0.58821
1585 | 0.53369
1586 | 0.4993
1587 | 0.47152
1588 | 0.4523
1589 | 0.47543
1590 | 0.55357
1591 | 0.64684
1592 | 0.66276
1593 | 0.58988
1594 | 0.5196
1595 | 0.47352
1596 | 0.4383
1597 | 0.42749
1598 | 0.45651
1599 | 0.48647
1600 | 0.51883
1601 | 0.59198
1602 | 0.67427
1603 | 0.77991
1604 | 0.80058
1605 | 0.76603
1606 | 0.72993
1607 | 0.66247
1608 | 0.58146
1609 | 0.52087
1610 | 0.51038
1611 | 0.48743
1612 | 0.4682
1613 | 0.49161
1614 | 0.57045
1615 | 0.66513
1616 | 0.68471
1617 | 0.61757
1618 | 0.56033
1619 | 0.50733
1620 | 0.46019
1621 | 0.43409
1622 | 0.43276
1623 | 0.46124
1624 | 0.50895
1625 | 0.59325
1626 | 0.69586
1627 | 0.80171
1628 | 0.82578
1629 | 0.79263
1630 | 0.75488
1631 | 0.67641
1632 | 0.59974
1633 | 0.53584
1634 | 0.51273
1635 | 0.48408
1636 | 0.46402
1637 | 0.48515
1638 | 0.56226
1639 | 0.65132
1640 | 0.6641
1641 | 0.59193
1642 | 0.50437
1643 | 0.47364
1644 | 0.4096
1645 | 0.38629
1646 | 0.38727
1647 | 0.43199
1648 | 0.51097
1649 | 0.58237
1650 | 0.67983
1651 | 0.76893
1652 | 0.78814
1653 | 0.75142
1654 | 0.73092
1655 | 0.68046
1656 | 0.60524
1657 | 0.5352
1658 | 0.51623
1659 | 0.48738
1660 | 0.46354
1661 | 0.46734
1662 | 0.49471
1663 | 0.541
1664 | 0.58003
1665 | 0.55744
1666 | 0.53364
1667 | 0.49116
1668 | 0.44971
1669 | 0.42714
1670 | 0.38869
1671 | 0.41703
1672 | 0.47567
1673 | 0.56386
1674 | 0.66484
1675 | 0.7555
1676 | 0.75961
1677 | 0.73336
1678 | 0.71005
1679 | 0.66779
1680 | 0.60276
1681 | 0.54571
1682 | 0.52511
1683 | 0.49881
1684 | 0.47158
1685 | 0.47372
1686 | 0.49241
1687 | 0.52586
1688 | 0.56095
1689 | 0.5506
1690 | 0.49557
1691 | 0.45281
1692 | 0.42192
1693 | 0.39785
1694 | 0.36778
1695 | 0.38803
1696 | 0.44082
1697 | 0.54333
1698 | 0.66531
1699 | 0.79074
1700 | 0.80184
1701 | 0.78039
1702 | 0.74799
1703 | 0.67568
1704 | 0.59859
1705 | 0.55516
1706 | 0.5095
1707 | 0.4864
1708 | 0.47021
1709 | 0.49386
1710 | 0.5777
1711 | 0.67317
1712 | 0.68725
1713 | 0.61389
1714 | 0.54198
1715 | 0.48879
1716 | 0.47551
1717 | 0.45055
1718 | 0.46015
1719 | 0.47682
1720 | 0.53736
1721 | 0.62222
1722 | 0.71972
1723 | 0.83268
1724 | 0.84601
1725 | 0.80444
1726 | 0.76275
1727 | 0.68929
1728 | 0.6065
1729 | 0.54196
1730 | 0.51566
1731 | 0.49205
1732 | 0.4716
1733 | 0.49446
1734 | 0.57717
1735 | 0.67224
1736 | 0.68676
1737 | 0.61708
1738 | 0.55306
1739 | 0.51245
1740 | 0.47532
1741 | 0.46148
1742 | 0.47803
1743 | 0.48047
1744 | 0.54426
1745 | 0.62966
1746 | 0.71516
1747 | 0.81394
1748 | 0.83833
1749 | 0.80216
1750 | 0.75404
1751 | 0.67848
1752 | 0.59996
1753 | 0.54295
1754 | 0.50307
1755 | 0.47504
1756 | 0.45688
1757 | 0.4783
1758 | 0.55712
1759 | 0.65108
1760 | 0.65954
1761 | 0.59746
1762 | 0.51085
1763 | 0.45024
1764 | 0.4139
1765 | 0.38913
1766 | 0.40085
1767 | 0.43193
1768 | 0.50164
1769 | 0.57249
1770 | 0.67883
1771 | 0.78387
1772 | 0.80607
1773 | 0.76823
1774 | 0.73346
1775 | 0.66478
1776 | 0.58678
1777 | 0.52613
1778 | 0.4873
1779 | 0.459
1780 | 0.44411
1781 | 0.46594
1782 | 0.54151
1783 | 0.63246
1784 | 0.62473
1785 | 0.53739
1786 | 0.46999
1787 | 0.41382
1788 | 0.37747
1789 | 0.3666
1790 | 0.38761
1791 | 0.3859
1792 | 0.43075
1793 | 0.53273
1794 | 0.64496
1795 | 0.7549
1796 | 0.79488
1797 | 0.75623
1798 | 0.71676
1799 | 0.63719
1800 | 0.5626
1801 | 0.50869
1802 | 0.49907
1803 | 0.47015
1804 | 0.45178
1805 | 0.47354
1806 | 0.5462
1807 | 0.63732
1808 | 0.63274
1809 | 0.55387
1810 | 0.4695
1811 | 0.41698
1812 | 0.35929
1813 | 0.34838
1814 | 0.3399
1815 | 0.37768
1816 | 0.45309
1817 | 0.53824
1818 | 0.64507
1819 | 0.74389
1820 | 0.77328
1821 | 0.73407
1822 | 0.70896
1823 | 0.65827
1824 | 0.58649
1825 | 0.52175
1826 | 0.4999
1827 | 0.4685
1828 | 0.44643
1829 | 0.45118
1830 | 0.47333
1831 | 0.5197
1832 | 0.53243
1833 | 0.49216
1834 | 0.44638
1835 | 0.39036
1836 | 0.34182
1837 | 0.32207
1838 | 0.30778
1839 | 0.34278
1840 | 0.39834
1841 | 0.50178
1842 | 0.61658
1843 | 0.71818
1844 | 0.73851
1845 | 0.70785
1846 | 0.68437
1847 | 0.64053
1848 | 0.57925
1849 | 0.52861
1850 | 0.50831
1851 | 0.47954
1852 | 0.45486
1853 | 0.45716
1854 | 0.47109
1855 | 0.50437
1856 | 0.51286
1857 | 0.48572
1858 | 0.45036
1859 | 0.41388
1860 | 0.39053
1861 | 0.36607
1862 | 0.34711
1863 | 0.38419
1864 | 0.4181
1865 | 0.51581
1866 | 0.62909
1867 | 0.75676
1868 | 0.77811
1869 | 0.75568
1870 | 0.72193
1871 | 0.6479
1872 | 0.57149
1873 | 0.53667
1874 | 0.4983
1875 | 0.47243
1876 | 0.45802
1877 | 0.48225
1878 | 0.56289
1879 | 0.658
1880 | 0.65705
1881 | 0.58929
1882 | 0.5109
1883 | 0.48241
1884 | 0.44938
1885 | 0.43139
1886 | 0.44216
1887 | 0.47235
1888 | 0.52289
1889 | 0.59858
1890 | 0.68907
1891 | 0.80438
1892 | 0.82999
1893 | 0.78653
1894 | 0.7422
1895 | 0.66799
1896 | 0.58742
1897 | 0.52962
1898 | 0.50938
1899 | 0.48521
1900 | 0.46645
1901 | 0.4903
1902 | 0.56934
1903 | 0.66517
1904 | 0.6677
1905 | 0.60167
1906 | 0.53749
1907 | 0.50852
1908 | 0.46325
1909 | 0.42934
1910 | 0.4317
1911 | 0.44474
1912 | 0.51455
1913 | 0.60525
1914 | 0.69054
1915 | 0.7951
1916 | 0.82722
1917 | 0.79095
1918 | 0.74377
1919 | 0.66727
1920 | 0.59123
1921 | 0.53674
1922 | 0.51295
1923 | 0.48427
1924 | 0.46521
1925 | 0.48811
1926 | 0.56575
1927 | 0.66005
1928 | 0.66286
1929 | 0.60371
1930 | 0.54244
1931 | 0.51242
1932 | 0.48956
1933 | 0.47526
1934 | 0.47008
1935 | 0.49744
1936 | 0.52771
1937 | 0.62875
1938 | 0.7053
1939 | 0.79499
1940 | 0.81157
1941 | 0.77989
1942 | 0.74554
1943 | 0.67699
1944 | 0.59753
1945 | 0.53298
1946 | 0.50384
1947 | 0.48016
1948 | 0.46048
1949 | 0.48484
1950 | 0.56152
1951 | 0.65429
1952 | 0.64493
1953 | 0.57303
1954 | 0.50956
1955 | 0.47893
1956 | 0.43923
1957 | 0.42101
1958 | 0.42523
1959 | 0.44115
1960 | 0.50536
1961 | 0.59285
1962 | 0.68257
1963 | 0.78342
1964 | 0.81414
1965 | 0.78155
1966 | 0.74162
1967 | 0.66428
1968 | 0.58894
1969 | 0.5292
1970 | 0.50874
1971 | 0.47985
1972 | 0.46133
1973 | 0.48373
1974 | 0.55856
1975 | 0.64772
1976 | 0.6442
1977 | 0.58242
1978 | 0.5458
1979 | 0.50203
1980 | 0.48073
1981 | 0.46864
1982 | 0.45731
1983 | 0.48402
1984 | 0.51912
1985 | 0.58481
1986 | 0.67675
1987 | 0.76351
1988 | 0.78293
1989 | 0.7485
1990 | 0.72108
1991 | 0.67139
1992 | 0.59997
1993 | 0.5322
1994 | 0.52478
1995 | 0.49576
1996 | 0.47074
1997 | 0.47638
1998 | 0.50462
1999 | 0.55078
2000 | 0.55512
2001 | 0.51607
2002 | 0.4966
2003 | 0.48038
2004 | 0.44813
2005 | 0.40932
2006 | 0.38845
2007 | 0.40937
2008 | 0.46941
2009 | 0.56475
2010 | 0.6733
2011 | 0.76457
2012 | 0.77657
2013 | 0.7489
2014 | 0.71895
2015 | 0.67793
2016 | 0.61385
2017 | 0.55446
2018 | 0.52863
2019 | 0.5021
2020 | 0.47478
2021 | 0.47988
2022 | 0.4985
2023 | 0.53103
2024 | 0.53466
2025 | 0.49468
2026 | 0.43732
2027 | 0.39548
2028 | 0.3577
2029 | 0.32931
2030 | 0.32253
2031 | 0.35186
2032 | 0.41705
2033 | 0.53394
2034 | 0.66926
2035 | 0.7947
2036 | 0.80395
2037 | 0.78621
2038 | 0.75282
2039 | 0.68287
2040 | 0.60351
2041 | 0.56011
2042 | 0.53138
2043 | 0.50392
2044 | 0.47548
2045 | 0.48973
2046 | 0.52526
2047 | 0.56931
2048 | 0.55478
2049 | 0.50737
2050 | 0.43848
2051 | 0.40405
2052 | 0.3514
2053 | 0.33482
2054 | 0.33848
2055 | 0.34446
2056 | 0.41785
2057 | 0.53882
2058 | 0.6742
2059 | 0.79725
2060 | 0.80689
2061 | 0.77223
2062 | 0.7491
2063 | 0.67466
2064 | 0.60397
2065 | 0.56186
2066 | 0.51266
2067 | 0.48745
2068 | 0.46845
2069 | 0.49546
2070 | 0.57543
2071 | 0.66483
2072 | 0.6442
2073 | 0.58359
2074 | 0.52802
2075 | 0.49603
2076 | 0.45496
2077 | 0.43336
2078 | 0.43555
2079 | 0.43205
2080 | 0.48455
2081 | 0.57644
2082 | 0.69291
2083 | 0.80648
2084 | 0.832
2085 | 0.7978
2086 | 0.74999
2087 | 0.67304
2088 | 0.59624
2089 | 0.54058
2090 | 0.50832
2091 | 0.48215
2092 | 0.46234
2093 | 0.48717
2094 | 0.56537
2095 | 0.65377
2096 | 0.64754
2097 | 0.57776
2098 | 0.51055
2099 | 0.43946
2100 | 0.39326
2101 | 0.37063
2102 | 0.37854
2103 | 0.41358
2104 | 0.48334
2105 | 0.57381
2106 | 0.6815
2107 | 0.79258
2108 | 0.81149
2109 | 0.77419
2110 | 0.74351
2111 | 0.6752
2112 | 0.59636
2113 | 0.53178
2114 | 0.50713
2115 | 0.47988
2116 | 0.46424
2117 | 0.48756
2118 | 0.56683
2119 | 0.65491
2120 | 0.62995
2121 | 0.56003
2122 | 0.48565
2123 | 0.43658
2124 | 0.39282
2125 | 0.38207
2126 | 0.38322
2127 | 0.40163
2128 | 0.44324
2129 | 0.54516
2130 | 0.67237
2131 | 0.78564
2132 | 0.81916
2133 | 0.78509
2134 | 0.7482
2135 | 0.66667
2136 | 0.59033
2137 | 0.52994
2138 | 0.52158
2139 | 0.4925
2140 | 0.4726
2141 | 0.49807
2142 | 0.57536
2143 | 0.66396
2144 | 0.6486
2145 | 0.57965
2146 | 0.52016
2147 | 0.50246
2148 | 0.48815
2149 | 0.48059
2150 | 0.4604
2151 | 0.48429
2152 | 0.53366
2153 | 0.61459
2154 | 0.70852
2155 | 0.78781
2156 | 0.80122
2157 | 0.76302
2158 | 0.74384
2159 | 0.68951
2160 | 0.61933
2161 | 0.54499
2162 | 0.54375
2163 | 0.50733
2164 | 0.48575
2165 | 0.49232
2166 | 0.51738
2167 | 0.55819
2168 | 0.57194
2169 | 0.54893
2170 | 0.50477
2171 | 0.47389
2172 | 0.43277
2173 | 0.39936
2174 | 0.383
2175 | 0.42032
2176 | 0.49524
2177 | 0.61693
2178 | 0.70002
2179 | 0.77412
2180 | 0.78219
2181 | 0.77538
2182 | 0.74606
2183 | 0.68893
2184 | 0.63995
2185 | 0.57129
2186 | 0.54286
2187 | 0.50685
2188 | 0.48382
2189 | 0.48848
2190 | 0.50223
2191 | 0.52803
2192 | 0.53946
2193 | 0.52974
2194 | 0.47891
2195 | 0.44383
2196 | 0.40303
2197 | 0.38276
2198 | 0.38459
2199 | 0.44168
2200 | 0.50376
2201 | 0.61341
2202 | 0.7027
2203 | 0.80067
2204 | 0.80775
2205 | 0.80575
2206 | 0.76729
2207 | 0.68551
2208 | 0.62043
2209 | 0.57016
2210 | 0.51939
2211 | 0.48856
2212 | 0.47637
2213 | 0.50193
2214 | 0.58102
2215 | 0.66755
2216 | 0.66397
2217 | 0.58697
2218 | 0.50595
2219 | 0.46698
2220 | 0.41764
2221 | 0.42048
2222 | 0.45992
2223 | 0.4965
2224 | 0.57235
2225 | 0.64258
2226 | 0.72229
2227 | 0.82573
2228 | 0.84419
2229 | 0.82179
2230 | 0.77184
2231 | 0.68624
2232 | 0.61892
2233 | 0.54875
2234 | 0.52527
2235 | 0.493
2236 | 0.47708
2237 | 0.50428
2238 | 0.58142
2239 | 0.66761
2240 | 0.65628
2241 | 0.60704
2242 | 0.54361
2243 | 0.48084
2244 | 0.43886
2245 | 0.42913
2246 | 0.42388
2247 | 0.44095
2248 | 0.5312
2249 | 0.62439
2250 | 0.71895
2251 | 0.80498
2252 | 0.83561
2253 | 0.81674
2254 | 0.76222
2255 | 0.67729
2256 | 0.61284
2257 | 0.55141
2258 | 0.51685
2259 | 0.47968
2260 | 0.46726
2261 | 0.49102
2262 | 0.56422
2263 | 0.64986
2264 | 0.64219
2265 | 0.56217
2266 | 0.50926
2267 | 0.45582
2268 | 0.43935
2269 | 0.43395
2270 | 0.3994
2271 | 0.44033
2272 | 0.49832
2273 | 0.61005
2274 | 0.695
2275 | 0.7872
2276 | 0.80745
2277 | 0.78752
2278 | 0.74256
2279 | 0.66781
2280 | 0.6015
2281 | 0.53444
2282 | 0.51494
2283 | 0.48318
2284 | 0.46777
2285 | 0.49477
2286 | 0.56586
2287 | 0.64995
2288 | 0.63279
2289 | 0.55924
2290 | 0.50465
2291 | 0.45877
2292 | 0.4103
2293 | 0.40203
2294 | 0.406
2295 | 0.42913
2296 | 0.48247
2297 | 0.59088
2298 | 0.68148
2299 | 0.78132
2300 | 0.81787
2301 | 0.80124
2302 | 0.75163
2303 | 0.66572
2304 | 0.59943
2305 | 0.53573
2306 | 0.5324
2307 | 0.49252
2308 | 0.4657
2309 | 0.47799
2310 | 0.49878
2311 | 0.53301
2312 | 0.53198
2313 | 0.53702
2314 | 0.50068
2315 | 0.45432
2316 | 0.40659
2317 | 0.40505
2318 | 0.40101
2319 | 0.47573
2320 | 0.5507
2321 | 0.60919
2322 | 0.67274
2323 | 0.72265
2324 | 0.73627
2325 | 0.72242
2326 | 0.70695
2327 | 0.64934
2328 | 0.59937
2329 | 0.55188
2330 | 0.51006
2331 | 0.47267
2332 | 0.45459
2333 | 0.4616
2334 | 0.47936
2335 | 0.51698
2336 | 0.53066
2337 | 0.51886
2338 | 0.47535
2339 | 0.42025
2340 | 0.38422
2341 | 0.37128
2342 | 0.35836
2343 | 0.37912
2344 | 0.44973
2345 | 0.5543
2346 | 0.63312
2347 | 0.72161
2348 | 0.74074
2349 | 0.7307
2350 | 0.69607
2351 | 0.6454
2352 | 0.59529
2353 | 0.53793
2354 | 0.51827
2355 | 0.48238
2356 | 0.45942
2357 | 0.46476
2358 | 0.47307
2359 | 0.49749
2360 | 0.49208
2361 | 0.46941
2362 | 0.41041
2363 | 0.35891
2364 | 0.32322
2365 | 0.32409
2366 | 0.31064
2367 | 0.35794
2368 | 0.4261
2369 | 0.5416
2370 | 0.64689
2371 | 0.75588
2372 | 0.7773
2373 | 0.77138
2374 | 0.72732
2375 | 0.64919
2376 | 0.58584
2377 | 0.54547
2378 | 0.50198
2379 | 0.47051
2380 | 0.46017
2381 | 0.48672
2382 | 0.56038
2383 | 0.64439
2384 | 0.6246
2385 | 0.53584
2386 | 0.46708
2387 | 0.42717
2388 | 0.39942
2389 | 0.40089
2390 | 0.40103
2391 | 0.43713
2392 | 0.5094
2393 | 0.60357
2394 | 0.68466
2395 | 0.79433
2396 | 0.82039
2397 | 0.7964
2398 | 0.74391
2399 | 0.66132
2400 | 0.59387
2401 | 0.53182
2402 | 0.51508
2403 | 0.48186
2404 | 0.46727
2405 | 0.49399
2406 | 0.56858
2407 | 0.65304
2408 | 0.64732
2409 | 0.58794
2410 | 0.50641
2411 | 0.47653
2412 | 0.43844
2413 | 0.41368
2414 | 0.39266
2415 | 0.41494
2416 | 0.49856
2417 | 0.61273
2418 | 0.69175
2419 | 0.78574
2420 | 0.82143
2421 | 0.80045
2422 | 0.74209
2423 | 0.66116
2424 | 0.59789
2425 | 0.53983
2426 | 0.50378
2427 | 0.46914
2428 | 0.45443
2429 | 0.48113
2430 | 0.5503
2431 | 0.63077
2432 | 0.61218
2433 | 0.54567
2434 | 0.4815
2435 | 0.4198
2436 | 0.3669
2437 | 0.37114
2438 | 0.36648
2439 | 0.39167
2440 | 0.4751
2441 | 0.56696
2442 | 0.67375
2443 | 0.76391
2444 | 0.79176
2445 | 0.77086
2446 | 0.72453
2447 | 0.64502
2448 | 0.58401
2449 | 0.52388
2450 | 0.51735
2451 | 0.48558
2452 | 0.47323
2453 | 0.49689
2454 | 0.57186
2455 | 0.65189
2456 | 0.63889
2457 | 0.5663
2458 | 0.50459
2459 | 0.43117
2460 | 0.38926
2461 | 0.39207
2462 | 0.39984
2463 | 0.44648
2464 | 0.52835
2465 | 0.63289
2466 | 0.69798
2467 | 0.78626
2468 | 0.82175
2469 | 0.8048
2470 | 0.75434
2471 | 0.66807
2472 | 0.60569
2473 | 0.53749
2474 | 0.51824
2475 | 0.48166
2476 | 0.46741
2477 | 0.49191
2478 | 0.56233
2479 | 0.64232
2480 | 0.63459
2481 | 0.59985
2482 | 0.52239
2483 | 0.47379
2484 | 0.44583
2485 | 0.44433
2486 | 0.44838
2487 | 0.48209
2488 | 0.55572
2489 | 0.63087
2490 | 0.699
2491 | 0.75941
2492 | 0.78427
2493 | 0.76459
2494 | 0.72971
2495 | 0.66819
2496 | 0.61359
2497 | 0.53872
2498 | 0.52845
2499 | 0.49135
2500 | 0.47188
2501 | 0.47878
2502 | 0.50042
2503 | 0.53891
2504 | 0.54346
2505 | 0.49793
2506 | 0.46382
2507 | 0.4082
2508 | 0.35668
2509 | 0.35021
2510 | 0.34125
2511 | 0.38744
2512 | 0.45132
2513 | 0.55779
2514 | 0.65436
2515 | 0.74565
2516 | 0.759
2517 | 0.75262
2518 | 0.71966
2519 | 0.66507
2520 | 0.6211
2521 | 0.55566
2522 | 0.53304
2523 | 0.49857
2524 | 0.47644
2525 | 0.48003
2526 | 0.4928
2527 | 0.51326
2528 | 0.51616
2529 | 0.49686
2530 | 0.45832
2531 | 0.42088
2532 | 0.38971
2533 | 0.38606
2534 | 0.37754
2535 | 0.40131
2536 | 0.46888
2537 | 0.57798
2538 | 0.67355
2539 | 0.76884
2540 | 0.78537
2541 | 0.79399
2542 | 0.75051
2543 | 0.66925
2544 | 0.60853
2545 | 0.56013
2546 | 0.52126
2547 | 0.48956
2548 | 0.47829
2549 | 0.50572
2550 | 0.58252
2551 | 0.65347
2552 | 0.65478
2553 | 0.6111
2554 | 0.55104
2555 | 0.51476
2556 | 0.49621
2557 | 0.47502
2558 | 0.48223
2559 | 0.50354
2560 | 0.57129
2561 | 0.66316
2562 | 0.72988
2563 | 0.82482
2564 | 0.8434
2565 | 0.82177
2566 | 0.76989
2567 | 0.68864
2568 | 0.6215
2569 | 0.55115
2570 | 0.52503
2571 | 0.49334
2572 | 0.47786
2573 | 0.50531
2574 | 0.58158
2575 | 0.66228
2576 | 0.6434
2577 | 0.56773
2578 | 0.50025
2579 | 0.44249
2580 | 0.40029
2581 | 0.39727
2582 | 0.39922
2583 | 0.42839
2584 | 0.50588
2585 | 0.61643
2586 | 0.70921
2587 | 0.8083
2588 | 0.83827
2589 | 0.81683
2590 | 0.75858
2591 | 0.67222
2592 | 0.61199
2593 | 0.55047
2594 | 0.52412
2595 | 0.488
2596 | 0.47551
2597 | 0.49967
2598 | 0.57634
2599 | 0.65462
2600 | 0.65506
2601 | 0.61891
2602 | 0.57109
2603 | 0.52161
2604 | 0.47374
2605 | 0.45749
2606 | 0.44692
2607 | 0.4915
2608 | 0.55157
2609 | 0.66172
2610 | 0.72987
2611 | 0.80241
2612 | 0.81947
2613 | 0.80067
2614 | 0.75585
2615 | 0.67637
2616 | 0.60802
2617 | 0.54316
2618 | 0.52186
2619 | 0.4908
2620 | 0.47756
2621 | 0.50445
2622 | 0.57777
2623 | 0.65556
2624 | 0.64502
2625 | 0.58466
2626 | 0.54653
2627 | 0.53615
2628 | 0.50184
2629 | 0.49245
2630 | 0.47376
2631 | 0.49887
2632 | 0.55883
2633 | 0.63874
2634 | 0.71663
2635 | 0.79667
2636 | 0.82844
2637 | 0.8117
2638 | 0.7629
2639 | 0.67401
2640 | 0.61191
2641 | 0.54311
2642 | 0.52456
2643 | 0.48862
2644 | 0.47355
2645 | 0.4992
2646 | 0.57086
2647 | 0.64532
2648 | 0.64209
2649 | 0.58091
2650 | 0.52646
2651 | 0.48388
2652 | 0.43962
2653 | 0.43311
2654 | 0.44832
2655 | 0.51147
2656 | 0.57268
2657 | 0.64678
2658 | 0.70145
2659 | 0.77283
2660 | 0.79292
2661 | 0.77267
2662 | 0.73865
2663 | 0.68192
2664 | 0.62006
2665 | 0.54742
2666 | 0.5356
2667 | 0.49889
2668 | 0.47844
2669 | 0.48624
2670 | 0.50948
2671 | 0.54444
2672 | 0.54293
2673 | 0.52609
2674 | 0.46542
2675 | 0.41225
2676 | 0.38454
2677 | 0.39484
2678 | 0.41248
2679 | 0.42996
2680 | 0.4888
2681 | 0.59789
2682 | 0.67692
2683 | 0.75872
2684 | 0.76975
2685 | 0.76174
2686 | 0.72951
2687 | 0.67931
2688 | 0.62834
2689 | 0.56365
2690 | 0.53664
2691 | 0.5018
2692 | 0.47933
2693 | 0.48486
2694 | 0.49664
2695 | 0.5197
2696 | 0.5182
2697 | 0.50037
2698 | 0.45819
2699 | 0.42429
2700 | 0.39149
2701 | 0.40045
2702 | 0.37397
2703 | 0.40791
2704 | 0.48747
2705 | 0.60774
2706 | 0.68845
2707 | 0.78956
2708 | 0.80056
2709 | 0.79671
2710 | 0.75429
2711 | 0.67845
2712 | 0.61089
2713 | 0.56789
2714 | 0.51876
2715 | 0.48729
2716 | 0.47527
2717 | 0.50253
2718 | 0.58242
2719 | 0.66234
2720 | 0.63637
2721 | 0.58576
2722 | 0.5193
2723 | 0.48494
2724 | 0.46414
2725 | 0.45789
2726 | 0.4486
2727 | 0.48237
2728 | 0.56131
2729 | 0.64121
2730 | 0.72223
2731 | 0.8233
2732 | 0.8453
2733 | 0.81841
2734 | 0.76693
2735 | 0.68389
2736 | 0.61719
2737 | 0.54942
2738 | 0.52389
2739 | 0.49184
2740 | 0.47806
2741 | 0.50657
2742 | 0.58297
2743 | 0.66623
2744 | 0.6418
2745 | 0.56238
2746 | 0.47934
2747 | 0.42764
2748 | 0.40007
2749 | 0.42171
2750 | 0.40301
2751 | 0.43596
2752 | 0.50135
2753 | 0.61113
2754 | 0.70618
2755 | 0.8086
2756 | 0.84033
2757 | 0.81575
2758 | 0.75621
2759 | 0.67018
2760 | 0.60722
2761 | 0.5516
2762 | 0.52247
2763 | 0.48814
2764 | 0.47303
2765 | 0.50149
2766 | 0.57427
2767 | 0.65387
2768 | 0.63439
2769 | 0.57113
2770 | 0.49642
2771 | 0.44734
2772 | 0.41688
2773 | 0.43225
2774 | 0.4323
2775 | 0.47718
2776 | 0.54197
2777 | 0.63712
2778 | 0.71667
2779 | 0.80284
2780 | 0.82465
2781 | 0.7986
2782 | 0.75261
2783 | 0.67393
2784 | 0.60665
2785 | 0.54117
2786 | 0.51691
2787 | 0.48497
2788 | 0.47295
2789 | 0.50057
2790 | 0.57537
2791 | 0.65252
2792 | 0.62952
2793 | 0.57185
2794 | 0.51414
2795 | 0.46833
2796 | 0.44718
2797 | 0.46198
2798 | 0.46457
2799 | 0.50344
2800 | 0.5618
2801 | 0.65226
2802 | 0.71661
2803 | 0.79877
2804 | 0.82767
2805 | 0.80462
2806 | 0.75281
2807 | 0.66783
2808 | 0.60541
2809 | 0.53429
2810 | 0.51641
2811 | 0.47771
2812 | 0.46423
2813 | 0.49092
2814 | 0.56051
2815 | 0.63124
2816 | 0.61566
2817 | 0.57349
2818 | 0.50407
2819 | 0.4678
2820 | 0.43377
2821 | 0.42631
2822 | 0.42625
2823 | 0.47762
2824 | 0.53313
2825 | 0.62079
2826 | 0.69136
2827 | 0.75679
2828 | 0.78313
2829 | 0.7566
2830 | 0.72226
2831 | 0.66568
2832 | 0.60514
2833 | 0.534
2834 | 0.52492
2835 | 0.4866
2836 | 0.46785
2837 | 0.47601
2838 | 0.49776
2839 | 0.52879
2840 | 0.51938
2841 | 0.48879
2842 | 0.4419
2843 | 0.41642
2844 | 0.361
2845 | 0.3807
2846 | 0.37193
2847 | 0.41718
2848 | 0.49723
2849 | 0.59253
2850 | 0.66146
2851 | 0.74156
2852 | 0.75956
2853 | 0.74488
2854 | 0.70989
2855 | 0.66091
2856 | 0.61123
2857 | 0.54862
2858 | 0.52833
2859 | 0.48959
2860 | 0.46838
2861 | 0.47477
2862 | 0.48652
2863 | 0.50348
2864 | 0.50726
2865 | 0.49956
2866 | 0.46964
2867 | 0.43738
2868 | 0.38945
2869 | 0.37656
2870 | 0.36892
2871 | 0.38569
2872 | 0.46596
2873 | 0.57141
2874 | 0.65464
2875 | 0.7579
2876 | 0.77508
2877 | 0.78299
2878 | 0.73825
2879 | 0.65849
2880 | 0.59487
2881 | 0.55189
2882 | 0.5208
2883 | 0.49758
2884 | 0.49187
2885 | 0.51643
2886 | 0.58216
2887 | 0.63077
2888 | 0.59974
2889 | 0.52847
2890 | 0.44924
2891 | 0.43232
2892 | 0.40491
2893 | 0.41108
2894 | 0.41786
2895 | 0.4665
2896 | 0.52494
2897 | 0.62654
2898 | 0.71217
2899 | 0.78775
2900 | 0.81523
2901 | 0.7867
2902 | 0.74034
2903 | 0.68
2904 | 0.61064
2905 | 0.55766
2906 | 0.53058
2907 | 0.50694
2908 | 0.49778
2909 | 0.52293
2910 | 0.58857
2911 | 0.65529
2912 | 0.6198
2913 | 0.56971
2914 | 0.50652
2915 | 0.46546
2916 | 0.4302
2917 | 0.44046
2918 | 0.44334
2919 | 0.46992
2920 | 0.52451
2921 | 0.60214
2922 | 0.70269
2923 | 0.78426
2924 | 0.8213
2925 | 0.79553
2926 | 0.74164
2927 | 0.67698
2928 | 0.61099
2929 | 0.56673
2930 | 0.52749
2931 | 0.50302
2932 | 0.49479
2933 | 0.51742
2934 | 0.58365
2935 | 0.64594
2936 | 0.61781
2937 | 0.56388
2938 | 0.5167
2939 | 0.47899
2940 | 0.43249
2941 | 0.4396
2942 | 0.46727
2943 | 0.50447
2944 | 0.55594
2945 | 0.63089
2946 | 0.70347
2947 | 0.77995
2948 | 0.8054
2949 | 0.78119
2950 | 0.73759
2951 | 0.68348
2952 | 0.61202
2953 | 0.55506
2954 | 0.52835
2955 | 0.50962
2956 | 0.50118
2957 | 0.52625
2958 | 0.59234
2959 | 0.65448
2960 | 0.62401
2961 | 0.60303
2962 | 0.54231
2963 | 0.50004
2964 | 0.52795
2965 | 0.52954
2966 | 0.48621
2967 | 0.51514
2968 | 0.57393
2969 | 0.65682
2970 | 0.73173
2971 | 0.78774
2972 | 0.82234
2973 | 0.79732
2974 | 0.75135
2975 | 0.68581
2976 | 0.62143
2977 | 0.56162
2978 | 0.53954
2979 | 0.51674
2980 | 0.50467
2981 | 0.52859
2982 | 0.59315
2983 | 0.65606
2984 | 0.63675
2985 | 0.58633
2986 | 0.52401
2987 | 0.48049
2988 | 0.43543
2989 | 0.43471
2990 | 0.43143
2991 | 0.47504
2992 | 0.54142
2993 | 0.61986
2994 | 0.7084
2995 | 0.77411
2996 | 0.79717
2997 | 0.77012
2998 | 0.73952
2999 | 0.6966
3000 | 0.63564
3001 | 0.57176
3002 | 0.54276
3003 | 0.51954
3004 | 0.50407
3005 | 0.51116
3006 | 0.53055
3007 | 0.55256
3008 | 0.53938
3009 | 0.49659
3010 | 0.44966
3011 | 0.38006
3012 | 0.34557
3013 | 0.35293
3014 | 0.35461
3015 | 0.38387
3016 | 0.46576
3017 | 0.56307
3018 | 0.67436
3019 | 0.74629
3020 | 0.76852
3021 | 0.75084
3022 | 0.71973
3023 | 0.69055
3024 | 0.63598
3025 | 0.58238
3026 | 0.54288
3027 | 0.52149
3028 | 0.50149
3029 | 0.50674
3030 | 0.5162
3031 | 0.524
3032 | 0.50978
3033 | 0.48928
3034 | 0.4358
3035 | 0.41381
3036 | 0.3871
3037 | 0.36155
3038 | 0.34967
3039 | 0.3929
3040 | 0.46756
3041 | 0.58275
3042 | 0.68579
3043 | 0.76932
3044 | 0.79386
3045 | 0.78177
3046 | 0.74186
3047 | 0.68629
3048 | 0.61819
3049 | 0.58224
3050 | 0.53005
3051 | 0.51222
3052 | 0.50459
3053 | 0.52975
3054 | 0.59807
3055 | 0.66238
3056 | 0.64086
3057 | 0.57468
3058 | 0.52963
3059 | 0.50112
3060 | 0.50222
3061 | 0.53114
3062 | 0.54243
3063 | 0.57358
3064 | 0.63247
3065 | 0.67923
3066 | 0.72957
3067 | 0.80568
3068 | 0.82921
3069 | 0.80843
3070 | 0.75945
3071 | 0.69655
3072 | 0.62857
3073 | 0.5706
3074 | 0.52963
3075 | 0.50836
3076 | 0.49821
3077 | 0.52405
3078 | 0.59016
3079 | 0.64875
3080 | 0.62437
3081 | 0.56441
3082 | 0.4949
3083 | 0.45535
3084 | 0.43695
3085 | 0.42727
3086 | 0.42951
3087 | 0.44748
3088 | 0.52437
3089 | 0.61265
3090 | 0.70935
3091 | 0.78234
3092 | 0.82113
3093 | 0.79844
3094 | 0.7434
3095 | 0.67884
3096 | 0.61123
3097 | 0.56635
3098 | 0.531
3099 | 0.51046
3100 | 0.50156
3101 | 0.52604
3102 | 0.59064
3103 | 0.65931
3104 | 0.6511
3105 | 0.58908
3106 | 0.50046
3107 | 0.45658
3108 | 0.42285
3109 | 0.42236
3110 | 0.42572
3111 | 0.46243
3112 | 0.53083
3113 | 0.60591
3114 | 0.69792
3115 | 0.7701
3116 | 0.80777
3117 | 0.79134
3118 | 0.75113
3119 | 0.69104
3120 | 0.62203
3121 | 0.56287
3122 | 0.52706
3123 | 0.5051
3124 | 0.49989
3125 | 0.52471
3126 | 0.59096
3127 | 0.63694
3128 | 0.6086
3129 | 0.54697
3130 | 0.48512
3131 | 0.44841
3132 | 0.42505
3133 | 0.44115
3134 | 0.44246
3135 | 0.45703
3136 | 0.51578
3137 | 0.61657
3138 | 0.70099
3139 | 0.77835
3140 | 0.82181
3141 | 0.80016
3142 | 0.75193
3143 | 0.68415
3144 | 0.61843
3145 | 0.56165
3146 | 0.51817
3147 | 0.49258
3148 | 0.48658
3149 | 0.50844
3150 | 0.56935
3151 | 0.626
3152 | 0.58598
3153 | 0.52226
3154 | 0.46642
3155 | 0.41928
3156 | 0.36123
3157 | 0.36482
3158 | 0.37161
3159 | 0.41883
3160 | 0.49007
3161 | 0.57219
3162 | 0.66829
3163 | 0.73278
3164 | 0.77231
3165 | 0.74551
3166 | 0.71261
3167 | 0.66604
3168 | 0.60744
3169 | 0.55128
3170 | 0.52923
3171 | 0.50147
3172 | 0.49104
3173 | 0.49677
3174 | 0.51341
3175 | 0.53021
3176 | 0.5057
3177 | 0.4495
3178 | 0.4213
3179 | 0.36926
3180 | 0.33011
3181 | 0.33953
3182 | 0.32102
3183 | 0.35451
3184 | 0.42686
3185 | 0.53474
3186 | 0.63918
3187 | 0.7197
3188 | 0.7525
3189 | 0.73433
3190 | 0.70165
3191 | 0.66708
3192 | 0.61441
3193 | 0.56771
3194 | 0.52975
3195 | 0.50434
3196 | 0.49221
3197 | 0.49364
3198 | 0.50038
3199 | 0.50481
3200 | 0.48566
3201 | 0.46375
3202 | 0.42089
3203 | 0.40056
3204 | 0.38017
3205 | 0.3725
3206 | 0.33957
3207 | 0.38519
3208 | 0.4437
3209 | 0.54497
3210 | 0.64664
3211 | 0.74241
3212 | 0.77595
3213 | 0.76674
3214 | 0.72416
3215 | 0.66634
3216 | 0.59821
3217 | 0.56822
3218 | 0.52352
3219 | 0.50148
3220 | 0.49905
3221 | 0.52321
3222 | 0.59182
3223 | 0.65406
3224 | 0.61236
3225 | 0.54361
3226 | 0.47941
3227 | 0.43143
3228 | 0.41566
3229 | 0.41742
3230 | 0.41279
3231 | 0.44655
3232 | 0.50118
3233 | 0.59648
3234 | 0.70632
3235 | 0.79657
3236 | 0.82698
3237 | 0.80154
3238 | 0.75073
3239 | 0.68943
3240 | 0.61792
3241 | 0.56437
3242 | 0.53852
3243 | 0.51725
3244 | 0.50872
3245 | 0.53346
3246 | 0.60252
3247 | 0.66357
3248 | 0.63717
3249 | 0.58369
3250 | 0.50735
3251 | 0.45362
3252 | 0.41631
3253 | 0.44045
3254 | 0.42892
3255 | 0.44846
3256 | 0.51591
3257 | 0.60936
3258 | 0.7018
3259 | 0.7906
3260 | 0.83375
3261 | 0.81259
3262 | 0.76025
3263 | 0.69429
3264 | 0.62603
3265 | 0.57532
3266 | 0.5261
3267 | 0.50108
3268 | 0.49613
3269 | 0.52049
3270 | 0.58646
3271 | 0.64657
3272 | 0.63007
3273 | 0.57249
3274 | 0.52152
3275 | 0.45584
3276 | 0.42127
3277 | 0.42423
3278 | 0.42582
3279 | 0.46927
3280 | 0.54087
3281 | 0.59963
3282 | 0.69326
3283 | 0.77553
3284 | 0.80285
3285 | 0.78588
3286 | 0.74457
3287 | 0.69062
3288 | 0.61507
3289 | 0.55772
3290 | 0.52485
3291 | 0.50147
3292 | 0.49329
3293 | 0.52119
3294 | 0.5871
3295 | 0.64721
3296 | 0.61691
3297 | 0.55368
3298 | 0.49413
3299 | 0.44205
3300 | 0.40482
3301 | 0.41699
3302 | 0.4112
3303 | 0.4464
3304 | 0.5134
3305 | 0.6059
3306 | 0.69247
3307 | 0.77158
3308 | 0.81878
3309 | 0.79931
3310 | 0.75273
3311 | 0.68226
3312 | 0.61573
3313 | 0.55866
3314 | 0.53096
3315 | 0.50494
3316 | 0.49603
3317 | 0.52273
3318 | 0.58389
3319 | 0.63834
3320 | 0.58966
3321 | 0.53189
3322 | 0.46595
3323 | 0.41913
3324 | 0.39006
3325 | 0.40604
3326 | 0.39104
3327 | 0.4432
3328 | 0.51019
3329 | 0.58743
3330 | 0.67817
3331 | 0.75252
3332 | 0.78958
3333 | 0.76597
3334 | 0.73407
3335 | 0.68842
3336 | 0.62619
3337 | 0.56276
3338 | 0.53935
3339 | 0.51292
3340 | 0.498
3341 | 0.50799
3342 | 0.52546
3343 | 0.54225
3344 | 0.5152
3345 | 0.47
3346 | 0.43518
3347 | 0.39555
3348 | 0.39001
3349 | 0.39703
3350 | 0.36521
3351 | 0.39227
3352 | 0.45712
3353 | 0.55096
3354 | 0.66042
3355 | 0.73976
3356 | 0.76696
3357 | 0.7524
3358 | 0.72042
3359 | 0.68511
3360 | 0.62965
3361 | 0.5773
3362 | 0.53755
3363 | 0.51275
3364 | 0.49673
3365 | 0.50516
3366 | 0.51138
3367 | 0.51057
3368 | 0.47602
3369 | 0.44413
3370 | 0.41204
3371 | 0.37384
3372 | 0.34796
3373 | 0.3569
3374 | 0.32514
3375 | 0.38156
3376 | 0.45505
3377 | 0.59489
3378 | 0.67024
3379 | 0.75851
3380 | 0.79119
3381 | 0.77904
3382 | 0.74096
3383 | 0.6814
3384 | 0.60959
3385 | 0.57518
3386 | 0.52912
3387 | 0.50703
3388 | 0.50079
3389 | 0.52985
3390 | 0.59871
3391 | 0.65507
3392 | 0.61672
3393 | 0.54351
3394 | 0.48155
3395 | 0.44766
3396 | 0.44561
3397 | 0.46621
3398 | 0.48941
3399 | 0.52644
3400 | 0.58653
3401 | 0.63406
3402 | 0.7216
3403 | 0.80171
3404 | 0.83574
3405 | 0.81084
3406 | 0.76253
3407 | 0.70227
3408 | 0.62577
3409 | 0.56871
3410 | 0.54168
3411 | 0.52035
3412 | 0.51078
3413 | 0.5382
3414 | 0.60665
3415 | 0.66561
3416 | 0.6322
3417 | 0.57595
3418 | 0.51373
3419 | 0.45979
3420 | 0.42228
3421 | 0.44058
3422 | 0.43577
3423 | 0.4643
3424 | 0.521
3425 | 0.60961
3426 | 0.71706
3427 | 0.80185
3428 | 0.8406
3429 | 0.81989
3430 | 0.76738
3431 | 0.70461
3432 | 0.63432
3433 | 0.5796
3434 | 0.52383
3435 | 0.49835
3436 | 0.48933
3437 | 0.51718
3438 | 0.58215
3439 | 0.63856
3440 | 0.60673
3441 | 0.57519
3442 | 0.52154
3443 | 0.47655
3444 | 0.43938
3445 | 0.4465
3446 | 0.43015
3447 | 0.46276
3448 | 0.52147
3449 | 0.61622
3450 | 0.69174
3451 | 0.76772
3452 | 0.8049
3453 | 0.77733
3454 | 0.74328
3455 | 0.68415
3456 | 0.61601
3457 | 0.55543
3458 | 0.51406
3459 | 0.49063
3460 | 0.48227
3461 | 0.50677
3462 | 0.57336
3463 | 0.62842
3464 | 0.57992
3465 | 0.50984
3466 | 0.45306
3467 | 0.41467
3468 | 0.3957
3469 | 0.44381
3470 | 0.48035
3471 | 0.49244
3472 | 0.5647
3473 | 0.62213
3474 | 0.68711
3475 | 0.75443
3476 | 0.805
3477 | 0.78444
3478 | 0.73859
3479 | 0.67073
3480 | 0.60148
3481 | 0.54801
3482 | 0.52642
3483 | 0.50163
3484 | 0.49273
3485 | 0.51823
3486 | 0.58415
3487 | 0.63141
3488 | 0.59628
3489 | 0.53087
3490 | 0.47658
3491 | 0.45931
3492 | 0.4719
3493 | 0.52802
3494 | 0.53498
3495 | 0.57167
3496 | 0.61671
3497 | 0.66096
3498 | 0.69926
3499 | 0.75287
3500 | 0.78869
3501 | 0.76371
3502 | 0.7323
3503 | 0.68739
3504 | 0.62373
3505 | 0.56026
3506 | 0.54113
3507 | 0.5159
3508 | 0.50201
3509 | 0.50881
3510 | 0.53209
3511 | 0.54414
3512 | 0.51734
3513 | 0.48535
3514 | 0.4467
3515 | 0.43775
3516 | 0.4516
3517 | 0.47639
3518 | 0.47147
3519 | 0.45914
3520 | 0.53183
3521 | 0.62855
3522 | 0.69598
3523 | 0.74869
3524 | 0.77431
3525 | 0.75961
3526 | 0.72921
3527 | 0.69442
3528 | 0.63589
3529 | 0.58067
3530 | 0.54018
3531 | 0.51689
3532 | 0.50104
3533 | 0.50619
3534 | 0.51895
3535 | 0.5126
3536 | 0.48827
3537 | 0.46661
3538 | 0.44418
3539 | 0.41034
3540 | 0.41067
3541 | 0.41945
3542 | 0.42183
3543 | 0.50175
3544 | 0.55786
3545 | 0.62814
3546 | 0.69134
3547 | 0.77121
3548 | 0.79858
3549 | 0.78916
3550 | 0.74897
3551 | 0.69466
3552 | 0.61893
3553 | 0.58018
3554 | 0.54457
3555 | 0.52135
3556 | 0.50481
3557 | 0.51946
3558 | 0.55241
3559 | 0.56343
3560 | 0.52769
3561 | 0.49981
3562 | 0.46892
3563 | 0.45478
3564 | 0.43545
3565 | 0.45845
3566 | 0.49219
3567 | 0.54027
3568 | 0.59985
3569 | 0.65227
3570 | 0.71075
3571 | 0.77492
3572 | 0.801
3573 | 0.77873
3574 | 0.75012
3575 | 0.68858
3576 | 0.62293
3577 | 0.58492
3578 | 0.53152
3579 | 0.5108
3580 | 0.50298
3581 | 0.53032
3582 | 0.60038
3583 | 0.65803
3584 | 0.62236
3585 | 0.56219
3586 | 0.5095
3587 | 0.46813
3588 | 0.47369
3589 | 0.48102
3590 | 0.48818
3591 | 0.50646
3592 | 0.55789
3593 | 0.63034
3594 | 0.71097
3595 | 0.79413
3596 | 0.83421
3597 | 0.81085
3598 | 0.75788
3599 | 0.69338
3600 | 0.62632
3601 | 0.56981
3602 | 0.53238
3603 | 0.50671
3604 | 0.49774
3605 | 0.52198
3606 | 0.59328
3607 | 0.64992
3608 | 0.62189
3609 | 0.57881
3610 | 0.55003
3611 | 0.51086
3612 | 0.49436
3613 | 0.48367
3614 | 0.45304
3615 | 0.5194
3616 | 0.57592
3617 | 0.64743
3618 | 0.72029
3619 | 0.78948
3620 | 0.81829
3621 | 0.7944
3622 | 0.74815
3623 | 0.70004
3624 | 0.62815
3625 | 0.56626
3626 | 0.53722
3627 | 0.50819
3628 | 0.49865
3629 | 0.52277
3630 | 0.59569
3631 | 0.6707
3632 | 0.65149
3633 | 0.61984
3634 | 0.58079
3635 | 0.56062
3636 | 0.56484
3637 | 0.57262
3638 | 0.53431
3639 | 0.57142
3640 | 0.65121
3641 | 0.72472
3642 | 0.7718
3643 | 0.83131
3644 | 0.86927
3645 | 0.85078
3646 | 0.80356
3647 | 0.74344
3648 | 0.66285
3649 | 0.57875
3650 | 0.53859
3651 | 0.5049
3652 | 0.49567
3653 | 0.52022
3654 | 0.58952
3655 | 0.65847
3656 | 0.64884
3657 | 0.61403
3658 | 0.56225
3659 | 0.51052
3660 | 0.48313
3661 | 0.47558
3662 | 0.46089
3663 | 0.50508
3664 | 0.57618
3665 | 0.64947
3666 | 0.73229
3667 | 0.79372
3668 | 0.82814
3669 | 0.80844
3670 | 0.77726
3671 | 0.73927
3672 | 0.66441
3673 | 0.57744
3674 | 0.54697
3675 | 0.51288
3676 | 0.49796
3677 | 0.50169
3678 | 0.51609
3679 | 0.54141
3680 | 0.53761
3681 | 0.54133
3682 | 0.52715
3683 | 0.47421
3684 | 0.45083
3685 | 0.43875
3686 | 0.43176
3687 | 0.46235
3688 | 0.54543
3689 | 0.63217
3690 | 0.71616
3691 | 0.77467
3692 | 0.79941
3693 | 0.79048
3694 | 0.76072
3695 | 0.73436
3696 | 0.67001
3697 | 0.5929
3698 | 0.54948
3699 | 0.51727
3700 | 0.49977
3701 | 0.5009
3702 | 0.50324
3703 | 0.51076
3704 | 0.5143
3705 | 0.53793
3706 | 0.53951
3707 | 0.51953
3708 | 0.51087
3709 | 0.48619
3710 | 0.44548
3711 | 0.49913
3712 | 0.57911
3713 | 0.6525
3714 | 0.7324
3715 | 0.81348
3716 | 0.8327
3717 | 0.82919
3718 | 0.78806
3719 | 0.73732
3720 | 0.65479
3721 | 0.59528
3722 | 0.52967
3723 | 0.50138
3724 | 0.49621
3725 | 0.52175
3726 | 0.59705
3727 | 0.6737
3728 | 0.6696
3729 | 0.63024
3730 | 0.57787
3731 | 0.5567
3732 | 0.5339
3733 | 0.51254
3734 | 0.49192
3735 | 0.53034
3736 | 0.60696
3737 | 0.7048
3738 | 0.77005
3739 | 0.84762
3740 | 0.87988
3741 | 0.85485
3742 | 0.80151
3743 | 0.74444
3744 | 0.65989
3745 | 0.57731
3746 | 0.53206
3747 | 0.50284
3748 | 0.49386
3749 | 0.52111
3750 | 0.5934
3751 | 0.66615
3752 | 0.65709
3753 | 0.61385
3754 | 0.57065
3755 | 0.52726
3756 | 0.52948
3757 | 0.54776
3758 | 0.53039
3759 | 0.58168
3760 | 0.67995
3761 | 0.70256
3762 | 0.76329
3763 | 0.82605
3764 | 0.86773
3765 | 0.84313
3766 | 0.78563
3767 | 0.72597
3768 | 0.64784
3769 | 0.57667
3770 | 0.53748
3771 | 0.50386
3772 | 0.49303
3773 | 0.51735
3774 | 0.58743
3775 | 0.65912
3776 | 0.64209
3777 | 0.59774
3778 | 0.53947
3779 | 0.5001
3780 | 0.47368
3781 | 0.47943
3782 | 0.47492
3783 | 0.4959
3784 | 0.56862
3785 | 0.65553
3786 | 0.7396
3787 | 0.82063
3788 | 0.853
3789 | 0.83115
3790 | 0.78758
3791 | 0.73159
3792 | 0.65687
3793 | 0.57529
3794 | 0.53401
3795 | 0.50046
3796 | 0.49143
3797 | 0.51561
3798 | 0.5853
3799 | 0.65318
3800 | 0.63004
3801 | 0.59292
3802 | 0.55193
3803 | 0.51903
3804 | 0.51143
3805 | 0.50045
3806 | 0.47652
3807 | 0.50127
3808 | 0.5744
3809 | 0.644
3810 | 0.73216
3811 | 0.8095
3812 | 0.85753
3813 | 0.8387
3814 | 0.79194
3815 | 0.72892
3816 | 0.65343
3817 | 0.57203
3818 | 0.5386
3819 | 0.50376
3820 | 0.49292
3821 | 0.51834
3822 | 0.58627
3823 | 0.65435
3824 | 0.64452
3825 | 0.61522
3826 | 0.57221
3827 | 0.53811
3828 | 0.52548
3829 | 0.51209
3830 | 0.50329
3831 | 0.55961
3832 | 0.63834
3833 | 0.69646
3834 | 0.73866
3835 | 0.79736
3836 | 0.82524
3837 | 0.80448
3838 | 0.77536
3839 | 0.73811
3840 | 0.66788
3841 | 0.58068
3842 | 0.54762
3843 | 0.51206
3844 | 0.49575
3845 | 0.50028
3846 | 0.51542
3847 | 0.53709
3848 | 0.5509
3849 | 0.55554
3850 | 0.54132
3851 | 0.5168
3852 | 0.48817
3853 | 0.45685
3854 | 0.41881
3855 | 0.46976
3856 | 0.56237
3857 | 0.62961
3858 | 0.70871
3859 | 0.77503
3860 | 0.79588
3861 | 0.78639
3862 | 0.75878
3863 | 0.73337
3864 | 0.67101
3865 | 0.59471
3866 | 0.55514
3867 | 0.52188
3868 | 0.50224
3869 | 0.50474
3870 | 0.5079
3871 | 0.51528
3872 | 0.51965
3873 | 0.52141
3874 | 0.48605
3875 | 0.43874
3876 | 0.41558
3877 | 0.40878
3878 | 0.40403
3879 | 0.44455
3880 | 0.52296
3881 | 0.61028
3882 | 0.70748
3883 | 0.80736
3884 | 0.83475
3885 | 0.83578
3886 | 0.79541
3887 | 0.74103
3888 | 0.66195
3889 | 0.60321
3890 | 0.5554
3891 | 0.52196
3892 | 0.50278
3893 | 0.5161
3894 | 0.53812
3895 | 0.55438
3896 | 0.54145
3897 | 0.54786
3898 | 0.52789
3899 | 0.50439
3900 | 0.47524
3901 | 0.46124
3902 | 0.46225
3903 | 0.47424
3904 | 0.57706
3905 | 0.66049
3906 | 0.74172
3907 | 0.81596
3908 | 0.83533
3909 | 0.8194
3910 | 0.79032
3911 | 0.7331
3912 | 0.66032
3913 | 0.60382
3914 | 0.54025
3915 | 0.50826
3916 | 0.49781
3917 | 0.52529
3918 | 0.5978
3919 | 0.6678
3920 | 0.64692
3921 | 0.61349
3922 | 0.55791
3923 | 0.51566
3924 | 0.48913
3925 | 0.49528
3926 | 0.49471
3927 | 0.5202
3928 | 0.59949
3929 | 0.67249
3930 | 0.75999
3931 | 0.82916
3932 | 0.87103
3933 | 0.85041
3934 | 0.79246
3935 | 0.7342
3936 | 0.65592
3937 | 0.58529
3938 | 0.54089
3939 | 0.50637
3940 | 0.49454
3941 | 0.51727
3942 | 0.58799
3943 | 0.66139
3944 | 0.64446
3945 | 0.61285
3946 | 0.5733
3947 | 0.52766
3948 | 0.50288
3949 | 0.49636
3950 | 0.48441
3951 | 0.52304
3952 | 0.60733
3953 | 0.68409
3954 | 0.75638
3955 | 0.8275
3956 | 0.85352
3957 | 0.83224
3958 | 0.78804
3959 | 0.7402
3960 | 0.65326
3961 | 0.57686
3962 | 0.5336
3963 | 0.50388
3964 | 0.49103
3965 | 0.51475
3966 | 0.58512
3967 | 0.6559
3968 | 0.64924
3969 | 0.629
3970 | 0.60525
3971 | 0.55261
3972 | 0.5597
3973 | 0.57442
3974 | 0.54024
3975 | 0.5309
3976 | 0.58224
3977 | 0.66062
3978 | 0.7375
3979 | 0.81458
3980 | 0.85602
3981 | 0.83682
3982 | 0.78895
3983 | 0.72747
3984 | 0.65312
3985 | 0.5725
3986 | 0.53964
3987 | 0.50085
3988 | 0.48898
3989 | 0.51245
3990 | 0.58107
3991 | 0.64936
3992 | 0.63347
3993 | 0.60634
3994 | 0.56135
3995 | 0.50738
3996 | 0.47419
3997 | 0.47153
3998 | 0.46616
3999 | 0.52685
4000 | 0.60417
4001 | 0.67069
4002 | 0.74182
4003 | 0.78828
4004 | 0.82188
4005 | 0.7955
4006 | 0.76641
4007 | 0.73197
4008 | 0.66181
4009 | 0.57869
4010 | 0.54316
4011 | 0.50565
4012 | 0.48817
4013 | 0.49133
4014 | 0.50595
4015 | 0.52933
4016 | 0.54689
4017 | 0.56783
4018 | 0.55899
4019 | 0.52825
4020 | 0.47193
4021 | 0.43586
4022 | 0.40286
4023 | 0.43371
4024 | 0.50423
4025 | 0.58376
4026 | 0.68564
4027 | 0.76026
4028 | 0.78607
4029 | 0.77374
4030 | 0.74476
4031 | 0.71897
4032 | 0.65996
4033 | 0.58943
4034 | 0.55223
4035 | 0.51662
4036 | 0.49605
4037 | 0.49654
4038 | 0.49979
4039 | 0.50918
4040 | 0.51634
4041 | 0.53579
4042 | 0.50041
4043 | 0.45693
4044 | 0.43293
4045 | 0.39231
4046 | 0.37773
4047 | 0.41658
4048 | 0.51463
4049 | 0.62609
4050 | 0.7095
4051 | 0.79917
4052 | 0.82614
4053 | 0.82286
4054 | 0.78498
4055 | 0.72967
4056 | 0.65267
4057 | 0.59881
4058 | 0.53026
4059 | 0.49785
4060 | 0.4897
4061 | 0.51546
4062 | 0.59044
4063 | 0.66634
4064 | 0.64612
4065 | 0.60724
4066 | 0.54612
4067 | 0.51308
4068 | 0.49481
4069 | 0.50261
4070 | 0.48459
4071 | 0.50359
4072 | 0.5895
4073 | 0.65056
4074 | 0.73079
4075 | 0.82823
4076 | 0.8662
4077 | 0.84271
4078 | 0.7931
4079 | 0.7332
4080 | 0.65324
4081 | 0.57698
4082 | 0.52964
4083 | 0.49675
4084 | 0.48459
4085 | 0.51083
4086 | 0.58195
4087 | 0.64994
4088 | 0.64104
4089 | 0.6223
4090 | 0.57708
4091 | 0.51935
4092 | 0.51684
4093 | 0.51942
4094 | 0.48841
4095 | 0.48888
4096 | 0.55359
4097 | 0.62346
4098 | 0.71839
4099 | 0.80306
4100 | 0.853
4101 | 0.83038
4102 | 0.77287
4103 | 0.70937
4104 | 0.63582
4105 | 0.57273
4106 | 0.53202
4107 | 0.49951
4108 | 0.48757
4109 | 0.50983
4110 | 0.57935
4111 | 0.6522
4112 | 0.62748
4113 | 0.58493
4114 | 0.5474
4115 | 0.51539
4116 | 0.49583
4117 | 0.49772
4118 | 0.47105
4119 | 0.49679
4120 | 0.56723
4121 | 0.62938
4122 | 0.72042
4123 | 0.7997
4124 | 0.83744
4125 | 0.81835
4126 | 0.77516
4127 | 0.72075
4128 | 0.64389
4129 | 0.56787
4130 | 0.53363
4131 | 0.50338
4132 | 0.49412
4133 | 0.51453
4134 | 0.58434
4135 | 0.65149
4136 | 0.6246
4137 | 0.57757
4138 | 0.54373
4139 | 0.50945
4140 | 0.48046
4141 | 0.46948
4142 | 0.46852
4143 | 0.49203
4144 | 0.55512
4145 | 0.63939
4146 | 0.7282
4147 | 0.80494
4148 | 0.85219
4149 | 0.8333
4150 | 0.78617
4151 | 0.72266
4152 | 0.64872
4153 | 0.56555
4154 | 0.53872
4155 | 0.50286
4156 | 0.48764
4157 | 0.50981
4158 | 0.57595
4159 | 0.64708
4160 | 0.63655
4161 | 0.61156
4162 | 0.55651
4163 | 0.50808
4164 | 0.47196
4165 | 0.46601
4166 | 0.461
4167 | 0.48501
4168 | 0.55716
4169 | 0.62205
4170 | 0.70402
4171 | 0.77672
4172 | 0.81537
4173 | 0.79319
4174 | 0.75931
4175 | 0.72301
4176 | 0.65371
4177 | 0.57484
4178 | 0.55697
4179 | 0.52059
4180 | 0.5013
4181 | 0.50293
4182 | 0.51839
4183 | 0.54443
4184 | 0.55158
4185 | 0.55669
4186 | 0.55467
4187 | 0.5339
4188 | 0.5156
4189 | 0.50189
4190 | 0.46742
4191 | 0.49953
4192 | 0.5783
4193 | 0.62719
4194 | 0.7188
4195 | 0.78219
4196 | 0.80074
4197 | 0.78919
4198 | 0.75795
4199 | 0.73678
4200 | 0.67556
4201 | 0.60136
4202 | 0.55466
4203 | 0.52015
4204 | 0.4972
4205 | 0.49657
4206 | 0.49785
4207 | 0.50674
4208 | 0.51176
4209 | 0.51951
4210 | 0.49814
4211 | 0.44528
4212 | 0.39533
4213 | 0.37607
4214 | 0.37713
4215 | 0.41834
4216 | 0.50584
4217 | 0.60158
4218 | 0.70019
4219 | 0.79638
4220 | 0.82419
4221 | 0.82194
4222 | 0.78118
4223 | 0.72706
4224 | 0.65176
4225 | 0.59856
4226 | 0.52489
4227 | 0.49492
4228 | 0.48473
4229 | 0.50837
4230 | 0.58384
4231 | 0.66055
4232 | 0.64467
4233 | 0.59897
4234 | 0.57747
4235 | 0.53794
4236 | 0.51761
4237 | 0.50877
4238 | 0.49568
4239 | 0.48937
4240 | 0.57121
4241 | 0.65959
4242 | 0.74033
4243 | 0.82944
4244 | 0.86475
4245 | 0.83408
4246 | 0.78153
4247 | 0.72263
4248 | 0.64458
4249 | 0.56997
4250 | 0.54214
4251 | 0.51206
4252 | 0.49806
4253 | 0.52186
4254 | 0.5976
4255 | 0.67333
4256 | 0.65469
4257 | 0.61105
4258 | 0.54891
4259 | 0.50921
4260 | 0.47972
4261 | 0.48089
4262 | 0.49095
4263 | 0.53509
4264 | 0.62631
4265 | 0.69322
4266 | 0.75902
4267 | 0.83429
4268 | 0.87237
4269 | 0.84617
4270 | 0.78892
4271 | 0.72975
4272 | 0.65171
4273 | 0.5829
4274 | 0.54117
4275 | 0.50928
4276 | 0.4987
4277 | 0.52047
4278 | 0.58957
4279 | 0.66152
4280 | 0.65647
4281 | 0.61828
4282 | 0.58592
4283 | 0.54287
4284 | 0.52164
4285 | 0.53381
4286 | 0.52241
4287 | 0.55113
4288 | 0.6371
4289 | 0.70124
4290 | 0.76455
4291 | 0.82512
4292 | 0.85162
4293 | 0.82964
4294 | 0.78702
4295 | 0.73501
4296 | 0.65453
4297 | 0.57582
4298 | 0.53686
4299 | 0.51381
4300 | 0.50268
4301 | 0.52672
4302 | 0.59541
4303 | 0.66982
4304 | 0.65028
4305 | 0.60853
4306 | 0.5747
4307 | 0.54059
4308 | 0.51581
4309 | 0.50939
4310 | 0.50579
4311 | 0.5466
4312 | 0.63242
4313 | 0.68082
4314 | 0.74901
4315 | 0.82523
4316 | 0.86577
4317 | 0.84708
4318 | 0.79838
4319 | 0.73512
4320 | 0.65976
4321 | 0.57889
4322 | 0.54469
4323 | 0.51217
4324 | 0.49874
4325 | 0.51758
4326 | 0.58459
4327 | 0.65524
4328 | 0.65053
4329 | 0.62879
4330 | 0.58427
4331 | 0.52969
4332 | 0.48677
4333 | 0.47275
4334 | 0.4665
4335 | 0.54405
4336 | 0.60375
4337 | 0.68042
4338 | 0.74166
4339 | 0.79318
4340 | 0.82471
4341 | 0.80032
4342 | 0.76953
4343 | 0.73292
4344 | 0.66451
4345 | 0.57994
4346 | 0.59254
4347 | 0.55637
4348 | 0.53634
4349 | 0.53294
4350 | 0.54488
4351 | 0.56708
4352 | 0.58118
4353 | 0.58365
4354 | 0.5703
4355 | 0.54478
4356 | 0.5064
4357 | 0.5169
4358 | 0.53183
4359 | 0.56112
4360 | 0.62107
4361 | 0.70755
4362 | 0.78154
4363 | 0.8283
4364 | 0.85684
4365 | 0.8365
4366 | 0.8075
4367 | 0.77315
4368 | 0.70783
4369 | 0.63491
4370 | 0.59866
4371 | 0.56512
4372 | 0.54188
4373 | 0.53498
4374 | 0.53308
4375 | 0.53903
4376 | 0.5524
4377 | 0.55853
4378 | 0.53395
4379 | 0.51397
4380 | 0.48542
4381 | 0.47207
4382 | 0.46365
4383 | 0.51029
4384 | 0.58698
4385 | 0.68866
4386 | 0.7852
4387 | 0.86486
4388 | 0.89515
4389 | 0.88386
4390 | 0.84435
4391 | 0.7804
4392 | 0.69555
4393 | 0.64131
4394 | 0.5724
4395 | 0.54327
4396 | 0.53511
4397 | 0.55537
4398 | 0.63311
4399 | 0.71889
4400 | 0.72881
4401 | 0.71403
4402 | 0.67551
4403 | 0.65277
4404 | 0.62165
4405 | 0.60592
4406 | 0.59747
4407 | 0.61602
4408 | 0.66933
4409 | 0.74618
4410 | 0.82953
4411 | 0.90675
4412 | 0.94472
4413 | 0.90906
4414 | 0.85673
4415 | 0.78193
4416 | 0.69626
4417 | 0.61708
4418 | 0.59909
4419 | 0.5661
4420 | 0.54085
4421 | 0.54803
4422 | 0.56699
4423 | 0.5921
4424 | 0.58577
4425 | 0.59062
4426 | 0.58166
4427 | 0.54913
4428 | 0.51323
4429 | 0.50373
4430 | 0.49395
4431 | 0.51598
4432 | 0.59565
4433 | 0.68257
4434 | 0.78502
4435 | 0.84451
4436 | 0.88557
4437 | 0.8621
4438 | 0.82424
4439 | 0.74923
4440 | 0.67755
4441 | 0.6392
4442 | 0.5699
4443 | 0.53822
4444 | 0.52786
4445 | 0.55013
4446 | 0.62363
4447 | 0.70197
4448 | 0.70715
4449 | 0.65781
4450 | 0.61761
4451 | 0.59989
4452 | 0.56884
4453 | 0.57331
4454 | 0.56776
4455 | 0.59572
4456 | 0.66023
4457 | 0.75251
4458 | 0.81901
4459 | 0.87491
4460 | 0.91219
4461 | 0.87848
4462 | 0.83628
4463 | 0.7731
4464 | 0.68426
4465 | 0.60353
4466 | 0.56616
4467 | 0.531
4468 | 0.52754
4469 | 0.54896
4470 | 0.62336
4471 | 0.70136
4472 | 0.70266
4473 | 0.66217
4474 | 0.63843
4475 | 0.62303
4476 | 0.5933
4477 | 0.56388
4478 | 0.56212
4479 | 0.57884
4480 | 0.64988
4481 | 0.71229
4482 | 0.79351
4483 | 0.85743
4484 | 0.91557
4485 | 0.88666
4486 | 0.83787
4487 | 0.75992
4488 | 0.67881
4489 | 0.60036
4490 | 0.57453
4491 | 0.54164
4492 | 0.53112
4493 | 0.55112
4494 | 0.61784
4495 | 0.69368
4496 | 0.70433
4497 | 0.66151
4498 | 0.62772
4499 | 0.59569
4500 | 0.55904
4501 | 0.54596
4502 | 0.55401
4503 | 0.58595
4504 | 0.65206
4505 | 0.70947
4506 | 0.78924
4507 | 0.83964
4508 | 0.88208
4509 | 0.84744
4510 | 0.81712
4511 | 0.77055
4512 | 0.69252
4513 | 0.60817
4514 | 0.59335
4515 | 0.55804
4516 | 0.54013
4517 | 0.53706
4518 | 0.54791
4519 | 0.57282
4520 | 0.59651
4521 | 0.60831
4522 | 0.59039
4523 | 0.55014
4524 | 0.52548
4525 | 0.50911
4526 | 0.49998
4527 | 0.50547
4528 | 0.56636
4529 | 0.6491
4530 | 0.75401
4531 | 0.82396
4532 | 0.85878
4533 | 0.83975
4534 | 0.80973
4535 | 0.77321
4536 | 0.70666
4537 | 0.63401
4538 | 0.58335
4539 | 0.54953
4540 | 0.52967
4541 | 0.5238
4542 | 0.51775
4543 | 0.52465
4544 | 0.53592
4545 | 0.53676
4546 | 0.51256
4547 | 0.48115
4548 | 0.4423
4549 | 0.42144
4550 | 0.42543
4551 | 0.46435
4552 | 0.5486
4553 | 0.66661
4554 | 0.76177
4555 | 0.84151
4556 | 0.87926
4557 | 0.86679
4558 | 0.82528
4559 | 0.75837
4560 | 0.67348
4561 | 0.62374
4562 | 0.56895
4563 | 0.53917
4564 | 0.53238
4565 | 0.55556
4566 | 0.63096
4567 | 0.71342
4568 | 0.71943
4569 | 0.67629
4570 | 0.63788
4571 | 0.61712
4572 | 0.59028
4573 | 0.57411
4574 | 0.57034
4575 | 0.62386
4576 | 0.68141
4577 | 0.7693
4578 | 0.82503
4579 | 0.90209
4580 | 0.94059
4581 | 0.90336
4582 | 0.85095
4583 | 0.77808
4584 | 0.68896
4585 | 0.61203
4586 | 0.5752
4587 | 0.54422
4588 | 0.53454
4589 | 0.55815
4590 | 0.63305
4591 | 0.71839
4592 | 0.72609
4593 | 0.70202
4594 | 0.65303
4595 | 0.62676
4596 | 0.61094
4597 | 0.59199
4598 | 0.56525
4599 | 0.57845
4600 | 0.63948
4601 | 0.71592
4602 | 0.81092
4603 | 0.8829
4604 | 0.93405
4605 | 0.90141
4606 | 0.84001
4607 | 0.76446
4608 | 0.68141
4609 | 0.6139
4610 | 0.57873
4611 | 0.54686
4612 | 0.53713
4613 | 0.5591
4614 | 0.63556
4615 | 0.71596
4616 | 0.72222
4617 | 0.66884
4618 | 0.63859
4619 | 0.60794
4620 | 0.57824
4621 | 0.58341
4622 | 0.61912
4623 | 0.66657
4624 | 0.75333
4625 | 0.80542
4626 | 0.8504
4627 | 0.89389
4628 | 0.92448
4629 | 0.89086
4630 | 0.8466
4631 | 0.78295
4632 | 0.69505
4633 | 0.61264
4634 | 0.57324
4635 | 0.54385
4636 | 0.52996
4637 | 0.55878
4638 | 0.63417
4639 | 0.71549
4640 | 0.71909
4641 | 0.70571
4642 | 0.6998
4643 | 0.67145
4644 | 0.62381
4645 | 0.61574
4646 | 0.59417
4647 | 0.60612
4648 | 0.66783
4649 | 0.7506
4650 | 0.82904
4651 | 0.879
4652 | 0.92801
4653 | 0.90036
4654 | 0.85024
4655 | 0.77432
4656 | 0.69058
4657 | 0.60865
4658 | 0.5876
4659 | 0.55514
4660 | 0.54477
4661 | 0.5678
4662 | 0.63955
4663 | 0.71718
4664 | 0.72787
4665 | 0.70091
4666 | 0.66271
4667 | 0.62331
4668 | 0.58986
4669 | 0.5809
4670 | 0.58047
4671 | 0.61794
4672 | 0.7012
4673 | 0.76524
4674 | 0.82569
4675 | 0.86701
4676 | 0.90243
4677 | 0.86905
4678 | 0.83846
4679 | 0.78945
4680 | 0.71268
4681 | 0.62305
4682 | 0.5989
4683 | 0.56647
4684 | 0.54856
4685 | 0.54786
4686 | 0.56079
4687 | 0.58681
4688 | 0.61134
4689 | 0.60077
4690 | 0.57435
4691 | 0.54679
4692 | 0.52552
4693 | 0.52974
4694 | 0.5297
4695 | 0.55931
4696 | 0.631
4697 | 0.69761
4698 | 0.78059
4699 | 0.84404
4700 | 0.87232
4701 | 0.85363
4702 | 0.82479
4703 | 0.78725
4704 | 0.72075
4705 | 0.63973
4706 | 0.5969
4707 | 0.56581
4708 | 0.54498
4709 | 0.54171
4710 | 0.53986
4711 | 0.54688
4712 | 0.56734
4713 | 0.58186
4714 | 0.55153
4715 | 0.50176
4716 | 0.47779
4717 | 0.46664
4718 | 0.47751
4719 | 0.53111
4720 | 0.60463
4721 | 0.68786
4722 | 0.78484
4723 | 0.86967
4724 | 0.89887
4725 | 0.88924
4726 | 0.8483
4727 | 0.78387
4728 | 0.69619
4729 | 0.6377
4730 | 0.56737
4731 | 0.53825
4732 | 0.53159
4733 | 0.55558
4734 | 0.63433
4735 | 0.71792
4736 | 0.73465
4737 | 0.68996
4738 | 0.66713
4739 | 0.6435
4740 | 0.63217
4741 | 0.61877
4742 | 0.63499
4743 | 0.65272
4744 | 0.71029
4745 | 0.77536
4746 | 0.83914
4747 | 0.90104
4748 | 0.93892
4749 | 0.90198
4750 | 0.85034
4751 | 0.77816
4752 | 0.68827
4753 | 0.6082
4754 | 0.57143
4755 | 0.54256
4756 | 0.53157
4757 | 0.55746
4758 | 0.63404
4759 | 0.71628
4760 | 0.7222
4761 | 0.69265
4762 | 0.63868
4763 | 0.62765
4764 | 0.62779
4765 | 0.64609
4766 | 0.63452
4767 | 0.6522
4768 | 0.72069
4769 | 0.78256
4770 | 0.82951
4771 | 0.87846
4772 | 0.92928
4773 | 0.89865
4774 | 0.83916
4775 | 0.76342
4776 | 0.67837
4777 | 0.60983
4778 | 0.57679
4779 | 0.54348
4780 | 0.53357
4781 | 0.55716
4782 | 0.63412
4783 | 0.71876
4784 | 0.72659
4785 | 0.6768
4786 | 0.63623
4787 | 0.61209
4788 | 0.58913
4789 | 0.57477
4790 | 0.58401
4791 | 0.61025
4792 | 0.66951
4793 | 0.75217
4794 | 0.82739
4795 | 0.88811
4796 | 0.91946
4797 | 0.88815
4798 | 0.8444
4799 | 0.77839
4800 | 0.69041
4801 | 0.6078
4802 | 0.56484
4803 | 0.53459
4804 | 0.52673
4805 | 0.54491
4806 | 0.62616
4807 | 0.70687
4808 | 0.70994
4809 | 0.65092
4810 | 0.61118
4811 | 0.58467
4812 | 0.53908
4813 | 0.54375
4814 | 0.55846
4815 | 0.59439
4816 | 0.65907
4817 | 0.7212
4818 | 0.80483
4819 | 0.86538
4820 | 0.91741
4821 | 0.88626
4822 | 0.83912
4823 | 0.76109
4824 | 0.67865
4825 | 0.59954
4826 | 0.58354
4827 | 0.54975
4828 | 0.53967
4829 | 0.56372
4830 | 0.63855
4831 | 0.71866
4832 | 0.71787
4833 | 0.68255
4834 | 0.62994
4835 | 0.58962
4836 | 0.55734
4837 | 0.55522
4838 | 0.57194
4839 | 0.62103
4840 | 0.69902
4841 | 0.75904
4842 | 0.82052
4843 | 0.86299
4844 | 0.89683
4845 | 0.86391
4846 | 0.83519
4847 | 0.78754
4848 | 0.70946
4849 | 0.61782
4850 | 0.597
4851 | 0.56443
4852 | 0.54861
4853 | 0.54872
4854 | 0.56438
4855 | 0.59276
4856 | 0.63268
4857 | 0.63844
4858 | 0.5949
4859 | 0.55721
4860 | 0.52418
4861 | 0.51078
4862 | 0.50424
4863 | 0.5448
4864 | 0.64791
4865 | 0.74619
4866 | 0.80564
4867 | 0.84986
4868 | 0.8716
4869 | 0.85241
4870 | 0.82521
4871 | 0.79429
4872 | 0.72137
4873 | 0.64225
4874 | 0.58802
4875 | 0.55657
4876 | 0.53833
4877 | 0.53524
4878 | 0.53524
4879 | 0.54414
4880 | 0.562
4881 | 0.58204
4882 | 0.56755
4883 | 0.53414
4884 | 0.49846
4885 | 0.48248
4886 | 0.49535
4887 | 0.53773
4888 | 0.60361
4889 | 0.69302
4890 | 0.78403
4891 | 0.85871
4892 | 0.89184
4893 | 0.87975
4894 | 0.84051
4895 | 0.77149
4896 | 0.68741
4897 | 0.63263
4898 | 0.56551
4899 | 0.53916
4900 | 0.53309
4901 | 0.55723
4902 | 0.63712
4903 | 0.72548
4904 | 0.74987
4905 | 0.73413
4906 | 0.70706
4907 | 0.69009
4908 | 0.68225
4909 | 0.68597
4910 | 0.66743
4911 | 0.67819
4912 | 0.72276
4913 | 0.78032
4914 | 0.83398
4915 | 0.908
4916 | 0.94216
4917 | 0.90504
4918 | 0.85358
4919 | 0.7799
4920 | 0.69083
4921 | 0.6108
4922 | 0.57066
4923 | 0.542
4924 | 0.53329
4925 | 0.55781
4926 | 0.63573
4927 | 0.72045
4928 | 0.72171
4929 | 0.67606
4930 | 0.62617
4931 | 0.60162
4932 | 0.57625
4933 | 0.57919
4934 | 0.58349
4935 | 0.59846
4936 | 0.68338
4937 | 0.76101
4938 | 0.83147
4939 | 0.88396
4940 | 0.92987
4941 | 0.89871
4942 | 0.84143
4943 | 0.76612
4944 | 0.67945
4945 | 0.61181
4946 | 0.56955
4947 | 0.53872
4948 | 0.52748
4949 | 0.54992
4950 | 0.62608
4951 | 0.71033
4952 | 0.71917
4953 | 0.68957
4954 | 0.65275
4955 | 0.61676
4956 | 0.60211
4957 | 0.57316
4958 | 0.56554
4959 | 0.60025
4960 | 0.67296
4961 | 0.75846
4962 | 0.82812
4963 | 0.87751
4964 | 0.91236
4965 | 0.87918
4966 | 0.83873
4967 | 0.77304
4968 | 0.68442
4969 | 0.60328
4970 | 0.57284
4971 | 0.54374
4972 | 0.5336
4973 | 0.55707
4974 | 0.62959
4975 | 0.72058
4976 | 0.72944
4977 | 0.6853
4978 | 0.66064
4979 | 0.62025
4980 | 0.58149
4981 | 0.5678
4982 | 0.56698
4983 | 0.58754
4984 | 0.66223
4985 | 0.74044
4986 | 0.82001
4987 | 0.88371
4988 | 0.92674
4989 | 0.90163
4990 | 0.85281
4991 | 0.77741
4992 | 0.69379
4993 | 0.60839
4994 | 0.58176
4995 | 0.54863
4996 | 0.53661
4997 | 0.55999
4998 | 0.63531
4999 | 0.71758
5000 | 0.72384
5001 | 0.68851
5002 | 0.63459
5003 | 0.59052
5004 | 0.5684
5005 | 0.57016
5006 | 0.56008
5007 | 0.59587
5008 | 0.67625
5009 | 0.74183
5010 | 0.81596
5011 | 0.85938
5012 | 0.89363
5013 | 0.86247
5014 | 0.83528
5015 | 0.78748
5016 | 0.70988
5017 | 0.61843
5018 | 0.58579
5019 | 0.54808
5020 | 0.53262
5021 | 0.53412
5022 | 0.5474
5023 | 0.57668
5024 | 0.59353
5025 | 0.57081
5026 | 0.55264
5027 | 0.50927
5028 | 0.45901
5029 | 0.45398
5030 | 0.46009
5031 | 0.49067
5032 | 0.56643
5033 | 0.6585
5034 | 0.75922
5035 | 0.82254
5036 | 0.8517
5037 | 0.83439
5038 | 0.80664
5039 | 0.77361
5040 | 0.70466
5041 | 0.62767
5042 | 0.58416
5043 | 0.54844
5044 | 0.53038
5045 | 0.52848
5046 | 0.52728
5047 | 0.53798
5048 | 0.55475
5049 | 0.54176
5050 | 0.50405
5051 | 0.4796
5052 | 0.45261
5053 | 0.42642
5054 | 0.43315
5055 | 0.49039
5056 | 0.55296
5057 | 0.6664
5058 | 0.7593
5059 | 0.85307
5060 | 0.88131
5061 | 0.87206
5062 | 0.83335
5063 | 0.76707
5064 | 0.6814
5065 | 0.62708
5066 | 0.56926
5067 | 0.53874
5068 | 0.53438
5069 | 0.55865
5070 | 0.63725
5071 | 0.72535
5072 | 0.74211
5073 | 0.69782
5074 | 0.64373
5075 | 0.63024
5076 | 0.63658
5077 | 0.62277
5078 | 0.64693
5079 | 0.70668
5080 | 0.74731
5081 | 0.80598
5082 | 0.85775
5083 | 0.90327
5084 | 0.94227
5085 | 0.90651
5086 | 0.8556
5087 | 0.78797
5088 | 0.69421
5089 | 0.61369
5090 | 0.62708
5091 | 0.59356
5092 | 0.58606
5093 | 0.61577
5094 | 0.703
5095 | 0.79596
5096 | 0.80164
5097 | 0.7747
5098 | 0.73785
5099 | 0.69678
5100 | 0.67619
5101 | 0.66702
5102 | 0.6609
5103 | 0.65226
5104 | 0.71143
5105 | 0.78815
5106 | 0.87803
5107 | 0.9528
5108 | 0.99837
5109 | 0.96684
5110 | 0.90361
5111 | 0.82249
5112 | 0.73918
5113 | 0.67294
5114 | 0.62613
5115 | 0.59043
5116 | 0.58362
5117 | 0.609
5118 | 0.69638
5119 | 0.78773
5120 | 0.77649
5121 | 0.73079
5122 | 0.6834
5123 | 0.64361
5124 | 0.62326
5125 | 0.63275
5126 | 0.62708
5127 | 0.66626
5128 | 0.72072
5129 | 0.81031
5130 | 0.89095
5131 | 0.94913
5132 | 0.98058
5133 | 0.94913
5134 | 0.89906
5135 | 0.83135
5136 | 0.74312
5137 | 0.66429
5138 | 0.61814
5139 | 0.58612
5140 | 0.57837
5141 | 0.60511
5142 | 0.69279
5143 | 0.7774
5144 | 0.76296
5145 | 0.69399
5146 | 0.6487
5147 | 0.61647
5148 | 0.57931
5149 | 0.59987
5150 | 0.60258
5151 | 0.62503
5152 | 0.69969
5153 | 0.78392
5154 | 0.87415
5155 | 0.93535
5156 | 0.98331
5157 | 0.95245
5158 | 0.90003
5159 | 0.81802
5160 | 0.73565
5161 | 0.65824
5162 | 0.62676
5163 | 0.58861
5164 | 0.5799
5165 | 0.6062
5166 | 0.69025
5167 | 0.77802
5168 | 0.77598
5169 | 0.72277
5170 | 0.66297
5171 | 0.64796
5172 | 0.60541
5173 | 0.59944
5174 | 0.59618
5175 | 0.62051
5176 | 0.69065
5177 | 0.77015
5178 | 0.86403
5179 | 0.90978
5180 | 0.94813
5181 | 0.91394
5182 | 0.87817
5183 | 0.82658
5184 | 0.75061
5185 | 0.66713
5186 | 0.63158
5187 | 0.5947
5188 | 0.57692
5189 | 0.58326
5190 | 0.61143
5191 | 0.64978
5192 | 0.65552
5193 | 0.64275
5194 | 0.62759
5195 | 0.58205
5196 | 0.56604
5197 | 0.5787
5198 | 0.54957
5199 | 0.58312
5200 | 0.66245
5201 | 0.74768
5202 | 0.82583
5203 | 0.88081
5204 | 0.91383
5205 | 0.89204
5206 | 0.8576
5207 | 0.81695
5208 | 0.74961
5209 | 0.68085
5210 | 0.62954
5211 | 0.59297
5212 | 0.57341
5213 | 0.5768
5214 | 0.59044
5215 | 0.61214
5216 | 0.62297
5217 | 0.63232
5218 | 0.61961
5219 | 0.56285
5220 | 0.54096
5221 | 0.54975
5222 | 0.52683
5223 | 0.57356
5224 | 0.64243
5225 | 0.7418
5226 | 0.8261
5227 | 0.90826
5228 | 0.94126
5229 | 0.92616
5230 | 0.88027
5231 | 0.81072
5232 | 0.72504
5233 | 0.679
5234 | 0.61648
5235 | 0.58447
5236 | 0.57801
5237 | 0.60841
5238 | 0.69842
5239 | 0.79249
5240 | 0.79623
5241 | 0.76632
5242 | 0.70288
5243 | 0.66508
5244 | 0.64068
5245 | 0.6576
5246 | 0.6561
5247 | 0.67793
5248 | 0.73246
5249 | 0.81817
5250 | 0.89803
5251 | 0.96806
5252 | 1
5253 | 0.96218
5254 | 0.90511
5255 | 0.8308
5256 | 0.73941
5257 | 0.66738
5258 | 0.62322
5259 | 0.59035
5260 | 0.58046
5261 | 0.61022
5262 | 0.69988
5263 | 0.79155
5264 | 0.78033
5265 | 0.72582
5266 | 0.67604
5267 | 0.62015
5268 | 0.58811
5269 | 0.60581
5270 | 0.60037
5271 | 0.62254
5272 | 0.68889
5273 | 0.80135
5274 | 0.89156
5275 | 0.95067
5276 | 0.99323
5277 | 0.9608
5278 | 0.898
5279 | 0.81662
5280 | 0.73389
5281 | 0.66974
5282 | 0.62054
5283 | 0.5852
5284 | 0.57586
5285 | 0.60352
5286 | 0.6897
5287 | 0.78358
5288 | 0.79537
5289 | 0.76119
5290 | 0.70236
5291 | 0.66179
5292 | 0.6376
5293 | 0.65421
5294 | 0.64182
5295 | 0.66846
5296 | 0.74523
5297 | 0.8265
5298 | 0.89558
5299 | 0.93816
5300 | 0.97565
5301 | 0.94064
5302 | 0.89386
5303 | 0.82336
5304 | 0.73496
5305 | 0.66131
5306 | 0.61825
5307 | 0.58612
5308 | 0.57857
5309 | 0.60537
5310 | 0.69283
5311 | 0.78352
5312 | 0.77105
5313 | 0.73547
5314 | 0.69149
5315 | 0.65589
5316 | 0.63542
5317 | 0.62084
5318 | 0.613
5319 | 0.62697
5320 | 0.67078
5321 | 0.76545
5322 | 0.86682
5323 | 0.93642
5324 | 0.98409
5325 | 0.95509
5326 | 0.90031
5327 | 0.82048
5328 | 0.73474
5329 | 0.66043
5330 | 0.6119
5331 | 0.57384
5332 | 0.56427
5333 | 0.59059
5334 | 0.67193
5335 | 0.76041
5336 | 0.75082
5337 | 0.6957
5338 | 0.64582
5339 | 0.61043
5340 | 0.57023
5341 | 0.55585
5342 | 0.56421
5343 | 0.60916
5344 | 0.68231
5345 | 0.77743
5346 | 0.84739
5347 | 0.88928
5348 | 0.92672
5349 | 0.89253
5350 | 0.85682
5351 | 0.80539
5352 | 0.73005
5353 | 0.65285
5354 | 0.62912
5355 | 0.58903
5356 | 0.57474
5357 | 0.57636
5358 | 0.60366
5359 | 0.64372
5360 | 0.64447
5361 | 0.62552
5362 | 0.59523
5363 | 0.56537
5364 | 0.51521
5365 | 0.50513
5366 | 0.49318
5367 | 0.52989
5368 | 0.61108
5369 | 0.71713
5370 | 0.8096
5371 | 0.87058
5372 | 0.90595
5373 | 0.88499
5374 | 0.85004
5375 | 0.81136
5376 | 0.74217
5377 | 0.67769
5378 | 0.63501
5379 | 0.5969
5380 | 0.5783
5381 | 0.57786
5382 | 0.59167
5383 | 0.61684
5384 | 0.62198
5385 | 0.62056
5386 | 0.58561
5387 | 0.53431
5388 | 0.50144
5389 | 0.49427
5390 | 0.49742
5391 | 0.5489
5392 | 0.62463
5393 | 0.73931
5394 | 0.83622
5395 | 0.91712
5396 | 0.94502
5397 | 0.93328
5398 | 0.88504
5399 | 0.8177
5400 | 0.73016
5401 | 0.68308
5402 | 0.61304
5403 | 0.57937
5404 | 0.57399
5405 | 0.60018
5406 | 0.69152
5407 | 0.78474
5408 | 0.78917
5409 | 0.7463
5410 | 0.67834
5411 | 0.63599
5412 | 0.61486
5413 | 0.62704
5414 | 0.64219
5415 | 0.68958
5416 | 0.76127
5417 | 0.83438
5418 | 0.89992
5419 | 0.96397
5420 | 0.99455
5421 | 0.95668
5422 | 0.9001
5423 | 0.82443
5424 | 0.73345
5425 | 0.66314
5426 | 0.61441
5427 | 0.58001
5428 | 0.5711
5429 | 0.59842
5430 | 0.68592
5431 | 0.78014
5432 | 0.77077
5433 | 0.72134
5434 | 0.64864
5435 | 0.61008
5436 | 0.57058
5437 | 0.59804
5438 | 0.60088
5439 | 0.61618
5440 | 0.68442
5441 | 0.8071
5442 | 0.87465
5443 | 0.93668
5444 | 0.98089
5445 | 0.94729
5446 | 0.88363
5447 | 0.80513
5448 | 0.72048
5449 | 0.65986
5450 | 0.62046
5451 | 0.58256
5452 | 0.57385
5453 | 0.59889
5454 | 0.68781
5455 | 0.77858
5456 | 0.76627
5457 | 0.70329
5458 | 0.67028
5459 | 0.64494
5460 | 0.62712
5461 | 0.61369
5462 | 0.62229
5463 | 0.68445
5464 | 0.76223
5465 | 0.8405
5466 | 0.91172
5467 | 0.947
5468 | 0.97059
5469 | 0.93921
5470 | 0.88882
5471 | 0.82258
5472 | 0.7327
5473 | 0.65978
5474 | 0.61569
5475 | 0.58133
5476 | 0.57354
5477 | 0.60072
5478 | 0.68729
5479 | 0.7787
5480 | 0.75988
5481 | 0.69952
5482 | 0.65802
5483 | 0.62548
5484 | 0.58711
5485 | 0.60016
5486 | 0.62308
5487 | 0.64995
5488 | 0.69825
5489 | 0.79211
5490 | 0.88211
5491 | 0.93697
5492 | 0.98001
5493 | 0.94964
5494 | 0.89615
5495 | 0.81261
5496 | 0.73208
5497 | 0.65664
5498 | 0.6477
5499 | 0.60551
5500 | 0.58284
5501 | 0.59265
5502 | 0.62107
5503 | 0.65409
5504 | 0.63605
5505 | 0.63716
5506 | 0.62696
5507 | 0.59856
5508 | 0.55837
5509 | 0.55614
5510 | 0.56826
5511 | 0.6236
5512 | 0.71232
5513 | 0.78337
5514 | 0.85555
5515 | 0.88093
5516 | 0.89675
5517 | 0.87202
5518 | 0.85984
5519 | 0.80936
5520 | 0.74189
5521 | 0.68633
5522 | 0.62701
5523 | 0.58805
5524 | 0.57183
5525 | 0.57707
5526 | 0.59937
5527 | 0.64007
5528 | 0.65162
5529 | 0.63544
5530 | 0.61206
5531 | 0.5822
5532 | 0.54144
5533 | 0.50722
5534 | 0.50469
5535 | 0.53605
5536 | 0.61303
5537 | 0.72592
5538 | 0.82468
5539 | 0.88079
5540 | 0.90433
5541 | 0.88303
5542 | 0.84922
5543 | 0.81137
5544 | 0.74138
5545 | 0.67602
5546 | 0.63291
5547 | 0.59585
5548 | 0.57572
5549 | 0.57652
5550 | 0.58606
5551 | 0.61399
5552 | 0.61471
5553 | 0.60557
5554 | 0.57728
5555 | 0.54018
5556 | 0.50765
5557 | 0.50198
5558 | 0.49334
5559 | 0.5566
5560 | 0.66386
5561 | 0.76422
5562 | 0.85336
5563 | 0.9204
5564 | 0.94235
5565 | 0.9302
5566 | 0.88342
5567 | 0.81302
5568 | 0.7274
5569 | 0.68089
5570 | 0.61265
5571 | 0.5792
5572 | 0.57264
5573 | 0.59961
5574 | 0.68643
5575 | 0.78446
5576 | 0.78305
5577 | 0.73049
5578 | 0.70145
5579 | 0.6767
5580 | 0.64553
5581 | 0.6352
5582 | 0.62671
5583 | 0.65023
5584 | 0.71436
5585 | 0.80148
5586 | 0.88866
5587 | 0.96392
5588 | 0.99256
5589 | 0.95476
5590 | 0.89724
5591 | 0.82405
5592 | 0.73292
5593 | 0.66161
5594 | 0.62131
5595 | 0.58796
5596 | 0.57772
5597 | 0.60485
5598 | 0.69199
5599 | 0.78811
5600 | 0.78275
5601 | 0.74188
5602 | 0.70234
5603 | 0.65636
5604 | 0.65216
5605 | 0.66398
5606 | 0.66281
5607 | 0.70685
5608 | 0.75852
5609 | 0.83802
5610 | 0.91067
5611 | 0.9515
5612 | 0.98959
5613 | 0.95724
5614 | 0.89361
5615 | 0.81644
5616 | 0.73041
5617 | 0.66634
5618 | 0.61741
5619 | 0.58031
5620 | 0.56956
5621 | 0.59493
5622 | 0.67933
5623 | 0.77513
5624 | 0.78889
5625 | 0.75892
5626 | 0.76435
5627 | 0.74469
5628 | 0.72018
5629 | 0.7224
5630 | 0.74255
5631 | 0.774
5632 | 0.82906
5633 | 0.87977
5634 | 0.91527
5635 | 0.93918
5636 | 0.96613
5637 | 0.9313
5638 | 0.88499
5639 | 0.817
5640 | 0.72933
5641 | 0.65577
5642 | 0.61192
5643 | 0.57839
5644 | 0.56886
5645 | 0.59499
5646 | 0.67985
5647 | 0.77548
5648 | 0.79746
5649 | 0.77418
5650 | 0.74326
5651 | 0.72377
5652 | 0.7038
5653 | 0.69705
5654 | 0.69366
5655 | 0.72923
5656 | 0.7811
5657 | 0.85005
5658 | 0.90308
5659 | 0.93497
5660 | 0.97099
5661 | 0.94237
5662 | 0.88976
5663 | 0.8143
5664 | 0.72538
5665 | 0.6532
5666 | 0.62394
5667 | 0.58709
5668 | 0.57633
5669 | 0.60162
5670 | 0.682
5671 | 0.77125
5672 | 0.76933
5673 | 0.7546
5674 | 0.70315
5675 | 0.67744
5676 | 0.66714
5677 | 0.66149
5678 | 0.67985
5679 | 0.71777
5680 | 0.78015
5681 | 0.83975
5682 | 0.89142
5683 | 0.91307
5684 | 0.93611
5685 | 0.90738
5686 | 0.87381
5687 | 0.82766
5688 | 0.74559
5689 | 0.66703
5690 | 0.63027
5691 | 0.59139
5692 | 0.5752
5693 | 0.57614
5694 | 0.60103
5695 | 0.63692
5696 | 0.65514
5697 | 0.63443
5698 | 0.63321
5699 | 0.58553
5700 | 0.55169
5701 | 0.54889
5702 | 0.5445
5703 | 0.62397
5704 | 0.71884
5705 | 0.78725
5706 | 0.83669
5707 | 0.87826
5708 | 0.8972
5709 | 0.88235
5710 | 0.84949
5711 | 0.81348
5712 | 0.74306
5713 | 0.67722
5714 | 0.62916
5715 | 0.59223
5716 | 0.57319
5717 | 0.57182
5718 | 0.5843
5719 | 0.60222
5720 | 0.61454
5721 | 0.62657
5722 | 0.61497
5723 | 0.58173
5724 | 0.5588
5725 | 0.53506
5726 | 0.54715
5727 | 0.62968
5728 | 0.69157
5729 | 0.76965
5730 | 0.83706
5731 | 0.91171
5732 | 0.93362
5733 | 0.9233
5734 | 0.87909
5735 | 0.80812
5736 | 0.72239
5737 | 0.67763
5738 | 0.60242
5739 | 0.56985
5740 | 0.56468
5741 | 0.58966
5742 | 0.67687
5743 | 0.77075
5744 | 0.77634
5745 | 0.70791
5746 | 0.6737
5747 | 0.65608
5748 | 0.63112
5749 | 0.6589
5750 | 0.63649
5751 | 0.66129
5752 | 0.72114
5753 | 0.81507
5754 | 0.88708
5755 | 0.95275
5756 | 0.98191
5757 | 0.94368
5758 | 0.88555
5759 | 0.80975
5760 | 0.7208
5761 | 0.65218
5762 | 0.61356
5763 | 0.58047
5764 | 0.57164
5765 | 0.59711
5766 | 0.68053
5767 | 0.77348
5768 | 0.76089
5769 | 0.70576
5770 | 0.64189
5771 | 0.6031
5772 | 0.5757
5773 | 0.58903
5774 | 0.61494
5775 | 0.64901
5776 | 0.72039
5777 | 0.82164
5778 | 0.8835
5779 | 0.93103
5780 | 0.97112
5781 | 0.94525
5782 | 0.88287
5783 | 0.80212
5784 | 0.71934
5785 | 0.65936
5786 | 0.61855
5787 | 0.58275
5788 | 0.57312
5789 | 0.59553
5790 | 0.67878
5791 | 0.77271
5792 | 0.76237
5793 | 0.70624
5794 | 0.66682
5795 | 0.63806
5796 | 0.60988
5797 | 0.60947
5798 | 0.61808
5799 | 0.65465
5800 | 0.7175
5801 | 0.81207
5802 | 0.88381
5803 | 0.93607
5804 | 0.96083
5805 | 0.93459
5806 | 0.88529
5807 | 0.81833
5808 | 0.72974
5809 | 0.6569
5810 | 0.6091
5811 | 0.57558
5812 | 0.5683
5813 | 0.59145
5814 | 0.67414
5815 | 0.76526
5816 | 0.76741
5817 | 0.7193
5818 | 0.67277
5819 | 0.62651
5820 | 0.60292
5821 | 0.6024
5822 | 0.61385
5823 | 0.61666
5824 | 0.67323
5825 | 0.75481
5826 | 0.82438
5827 | 0.90319
5828 | 0.96164
5829 | 0.93747
5830 | 0.88531
5831 | 0.8034
5832 | 0.72037
5833 | 0.65232
5834 | 0.62449
5835 | 0.58955
5836 | 0.58215
5837 | 0.60605
5838 | 0.68998
5839 | 0.78041
5840 | 0.76635
5841 | 0.72658
5842 | 0.64508
5843 | 0.61959
5844 | 0.60868
5845 | 0.62639
5846 | 0.61703
5847 | 0.62744
5848 | 0.67949
5849 | 0.77153
5850 | 0.84167
5851 | 0.91813
5852 | 0.93709
5853 | 0.89338
5854 | 0.85615
5855 | 0.80512
5856 | 0.73474
5857 | 0.65917
5858 | 0.64003
5859 | 0.60774
5860 | 0.59222
5861 | 0.59544
5862 | 0.62485
5863 | 0.66795
5864 | 0.66063
5865 | 0.64964
5866 | 0.63032
5867 | 0.60988
5868 | 0.59113
5869 | 0.57321
5870 | 0.54861
5871 | 0.56495
5872 | 0.64029
5873 | 0.74018
5874 | 0.82787
5875 | 0.90738
5876 | 0.9182
5877 | 0.88583
5878 | 0.84986
5879 | 0.81059
5880 | 0.74745
5881 | 0.68342
5882 | 0.63863
5883 | 0.60658
5884 | 0.58927
5885 | 0.59041
5886 | 0.60549
5887 | 0.63347
5888 | 0.63854
5889 | 0.66378
5890 | 0.65539
5891 | 0.64961
5892 | 0.64979
5893 | 0.63287
5894 | 0.61439
5895 | 0.62304
5896 | 0.66575
5897 | 0.7603
5898 | 0.83081
5899 | 0.93445
5900 | 0.94506
5901 | 0.91967
5902 | 0.87522
5903 | 0.81086
5904 | 0.72672
5905 | 0.68251
5906 | 0.64282
5907 | 0.61119
5908 | 0.59459
5909 | 0.60719
5910 | 0.64667
5911 | 0.69067
5912 | 0.66891
5913 | 0.66322
5914 | 0.63933
5915 | 0.63366
5916 | 0.61147
5917 | 0.60098
5918 | 0.61428
5919 | 0.61312
5920 | 0.67344
5921 | 0.75795
5922 | 0.84669
5923 | 0.93858
5924 | 0.94453
5925 | 0.90756
5926 | 0.86932
5927 | 0.80179
5928 | 0.72546
5929 | 0.68576
5930 | 0.62622
5931 | 0.59758
5932 | 0.58991
5933 | 0.61752
5934 | 0.70568
5935 | 0.7998
5936 | 0.77336
5937 | 0.70595
5938 | 0.64252
5939 | 0.61083
5940 | 0.58564
5941 | 0.59884
5942 | 0.60929
5943 | 0.62498
5944 | 0.70775
5945 | 0.7976
5946 | 0.87495
5947 | 0.96681
5948 | 0.98966
5949 | 0.9476
5950 | 0.88297
5951 | 0.81041
5952 | 0.72785
5953 | 0.6676
5954 | 0.62378
5955 | 0.59288
5956 | 0.58484
5957 | 0.60929
5958 | 0.69421
5959 | 0.78682
5960 | 0.76163
5961 | 0.69902
5962 | 0.6371
5963 | 0.61228
5964 | 0.59059
5965 | 0.58651
5966 | 0.58617
5967 | 0.6104
5968 | 0.69039
5969 | 0.78065
5970 | 0.86535
5971 | 0.95011
5972 | 0.96554
5973 | 0.92598
5974 | 0.87551
5975 | 0.81068
5976 | 0.7276
5977 | 0.65847
5978 | 0.62571
5979 | 0.59625
5980 | 0.58817
5981 | 0.61324
5982 | 0.70016
5983 | 0.79693
5984 | 0.78378
5985 | 0.75074
5986 | 0.69052
5987 | 0.64544
5988 | 0.6218
5989 | 0.64391
5990 | 0.6621
5991 | 0.67094
5992 | 0.71855
5993 | 0.7951
5994 | 0.8691
5995 | 0.95607
5996 | 0.97685
5997 | 0.94278
5998 | 0.88667
5999 | 0.80986
6000 | 0.73293
6001 | 0.66074
6002 | 0.62455
6003 | 0.59324
6004 | 0.58246
6005 | 0.60875
6006 | 0.6909
6007 | 0.7816
6008 | 0.7571
6009 | 0.70233
6010 | 0.63193
6011 | 0.60486
6012 | 0.57963
6013 | 0.58438
6014 | 0.5845
6015 | 0.62033
6016 | 0.70531
6017 | 0.78922
6018 | 0.84599
6019 | 0.92312
6020 | 0.93687
6021 | 0.89719
6022 | 0.85742
6023 | 0.80728
6024 | 0.73574
6025 | 0.66295
6026 | 0.63561
6027 | 0.60239
6028 | 0.58798
6029 | 0.59174
6030 | 0.62098
6031 | 0.66275
6032 | 0.66309
6033 | 0.64132
6034 | 0.6064
6035 | 0.59131
6036 | 0.54955
6037 | 0.52537
6038 | 0.52368
6039 | 0.54308
6040 | 0.62744
6041 | 0.72392
6042 | 0.81902
6043 | 0.9047
6044 | 0.90855
6045 | 0.8806
6046 | 0.84416
6047 | 0.80905
6048 | 0.74121
6049 | 0.67906
6050 | 0.63476
6051 | 0.60253
6052 | 0.58436
6053 | 0.58578
6054 | 0.60227
6055 | 0.62532
6056 | 0.61073
6057 | 0.60275
6058 | 0.55822
6059 | 0.53933
6060 | 0.52669
6061 | 0.51516
6062 | 0.50655
6063 | 0.5322
6064 | 0.61772
6065 | 0.73831
6066 | 0.82975
6067 | 0.92977
6068 | 0.9361
6069 | 0.91705
6070 | 0.86657
6071 | 0.80265
6072 | 0.71928
6073 | 0.67811
6074 | 0.61195
6075 | 0.58466
6076 | 0.57982
6077 | 0.60699
6078 | 0.69705
6079 | 0.79226
6080 | 0.77762
6081 | 0.74016
6082 | 0.67979
6083 | 0.65416
6084 | 0.66166
6085 | 0.69826
6086 | 0.72942
6087 | 0.73338
6088 | 0.7921
6089 | 0.84449
6090 | 0.89795
6091 | 0.97017
6092 | 0.98199
6093 | 0.93868
6094 | 0.87957
6095 | 0.809
6096 | 0.72182
6097 | 0.65761
6098 | 0.62329
6099 | 0.59444
6100 | 0.58472
6101 | 0.61255
6102 | 0.70161
6103 | 0.79932
6104 | 0.79436
6105 | 0.76184
6106 | 0.71391
6107 | 0.71149
6108 | 0.71116
6109 | 0.7275
6110 | 0.72205
6111 | 0.71416
6112 | 0.79919
6113 | 0.85846
6114 | 0.89306
6115 | 0.96099
6116 | 0.98057
6117 | 0.94084
6118 | 0.87561
6119 | 0.8017
6120 | 0.72033
6121 | 0.66305
6122 | 0.6211
6123 | 0.58939
6124 | 0.58132
6125 | 0.60652
6126 | 0.69314
6127 | 0.78679
6128 | 0.78115
6129 | 0.75733
6130 | 0.74542
6131 | 0.73056
6132 | 0.71243
6133 | 0.71097
6134 | 0.7223
6135 | 0.75081
6136 | 0.79734
6137 | 0.85741
6138 | 0.88999
6139 | 0.95006
6140 | 0.95834
6141 | 0.92024
6142 | 0.8699
6143 | 0.80867
6144 | 0.72181
6145 | 0.65526
6146 | 0.60872
6147 | 0.58102
6148 | 0.5726
6149 | 0.59804
6150 | 0.68296
6151 | 0.77516
6152 | 0.7562
6153 | 0.7009
6154 | 0.65743
6155 | 0.65229
6156 | 0.63849
6157 | 0.63941
6158 | 0.64708
6159 | 0.65385
6160 | 0.70705
6161 | 0.78624
6162 | 0.86154
6163 | 0.92965
6164 | 0.95443
6165 | 0.91535
6166 | 0.86277
6167 | 0.7867
6168 | 0.70977
6169 | 0.64654
6170 | 0.63381
6171 | 0.59905
6172 | 0.59121
6173 | 0.61422
6174 | 0.70065
6175 | 0.79457
6176 | 0.80199
6177 | 0.77443
6178 | 0.71497
6179 | 0.65134
6180 | 0.63624
6181 | 0.6481
6182 | 0.63512
6183 | 0.67236
6184 | 0.74094
6185 | 0.82325
6186 | 0.8754
6187 | 0.93729
6188 | 0.94337
6189 | 0.90263
6190 | 0.86896
6191 | 0.81916
6192 | 0.74518
6193 | 0.66866
6194 | 0.64477
6195 | 0.61148
6196 | 0.59581
6197 | 0.60047
6198 | 0.63167
6199 | 0.67313
6200 | 0.67658
6201 | 0.6683
6202 | 0.63481
6203 | 0.60275
6204 | 0.56027
6205 | 0.5172
6206 | 0.516
6207 | 0.54037
6208 | 0.61601
6209 | 0.73586
6210 | 0.83441
6211 | 0.91822
6212 | 0.91828
6213 | 0.88791
6214 | 0.85735
6215 | 0.82051
6216 | 0.75301
6217 | 0.68714
6218 | 0.63709
6219 | 0.60511
6220 | 0.58759
6221 | 0.58814
6222 | 0.60505
6223 | 0.63251
6224 | 0.62345
6225 | 0.62039
6226 | 0.58534
6227 | 0.54277
6228 | 0.53864
6229 | 0.55752
6230 | 0.54145
6231 | 0.566
6232 | 0.63807
6233 | 0.75697
6234 | 0.84198
6235 | 0.93181
6236 | 0.9371
6237 | 0.91498
6238 | 0.87172
6239 | 0.80407
6240 | 0.72077
6241 | 0.68004
6242 | 0.61712
6243 | 0.5881
6244 | 0.58399
6245 | 0.61064
6246 | 0.70075
6247 | 0.79562
6248 | 0.77964
6249 | 0.7137
6250 | 0.63214
6251 | 0.6074
6252 | 0.57748
6253 | 0.57859
6254 | 0.59448
6255 | 0.61848
6256 | 0.68622
6257 | 0.78431
6258 | 0.87278
6259 | 0.97363
6260 | 0.98444
6261 | 0.93908
6262 | 0.88496
6263 | 0.81484
6264 | 0.72674
6265 | 0.66001
6266 | 0.62286
6267 | 0.59504
6268 | 0.58606
6269 | 0.6116
6270 | 0.70083
6271 | 0.79808
6272 | 0.78175
6273 | 0.736
6274 | 0.67319
6275 | 0.63507
6276 | 0.60768
6277 | 0.60523
6278 | 0.61599
6279 | 0.6421
6280 | 0.70829
6281 | 0.78811
6282 | 0.87275
6283 | 0.95866
6284 | 0.98018
6285 | 0.93899
6286 | 0.87695
6287 | 0.8033
6288 | 0.71974
6289 | 0.66291
6290 | 0.62432
6291 | 0.5933
6292 | 0.58463
6293 | 0.61
6294 | 0.69849
6295 | 0.79223
6296 | 0.78304
6297 | 0.73623
6298 | 0.67256
6299 | 0.63659
6300 | 0.5922
6301 | 0.58006
6302 | 0.59214
6303 | 0.62571
6304 | 0.7159
6305 | 0.81467
6306 | 0.88771
6307 | 0.95489
6308 | 0.96469
6309 | 0.92204
6310 | 0.87451
6311 | 0.81375
6312 | 0.72787
6313 | 0.65855
6314 | 0.62728
6315 | 0.59777
6316 | 0.59145
6317 | 0.61489
6318 | 0.70423
6319 | 0.80025
6320 | 0.78202
6321 | 0.74055
6322 | 0.70091
6323 | 0.67585
6324 | 0.65661
6325 | 0.65367
6326 | 0.65557
6327 | 0.64845
6328 | 0.70734
6329 | 0.81823
6330 | 0.9006
6331 | 0.96145
6332 | 0.97893
6333 | 0.93987
6334 | 0.88415
6335 | 0.8134
6336 | 0.73326
6337 | 0.66206
6338 | 0.62922
6339 | 0.59799
6340 | 0.58666
6341 | 0.61246
6342 | 0.69499
6343 | 0.78961
6344 | 0.79515
6345 | 0.74004
6346 | 0.67021
6347 | 0.63399
6348 | 0.60015
6349 | 0.59219
6350 | 0.59897
6351 | 0.6322
6352 | 0.71509
6353 | 0.79206
6354 | 0.87063
6355 | 0.93129
6356 | 0.9389
6357 | 0.89695
6358 | 0.86089
6359 | 0.81892
6360 | 0.7391
6361 | 0.6647
6362 | 0.64
6363 | 0.60688
6364 | 0.59127
6365 | 0.59498
6366 | 0.62605
6367 | 0.67084
6368 | 0.6691
6369 | 0.64138
6370 | 0.57977
6371 | 0.56945
6372 | 0.53858
6373 | 0.52212
6374 | 0.53058
6375 | 0.5735
6376 | 0.65404
6377 | 0.76382
6378 | 0.84049
6379 | 0.91077
6380 | 0.91211
6381 | 0.88172
6382 | 0.84819
6383 | 0.81368
6384 | 0.74584
6385 | 0.68262
6386 | 0.64152
6387 | 0.61055
6388 | 0.59248
6389 | 0.59356
6390 | 0.61177
6391 | 0.64071
6392 | 0.63165
6393 | 0.61643
6394 | 0.56869
6395 | 0.52744
6396 | 0.50252
6397 | 0.48286
6398 | 0.49083
6399 | 0.52435
6400 | 0.60388
6401 | 0.73948
6402 | 0.84374
6403 | 0.9362
6404 | 0.94202
6405 | 0.92262
6406 | 0.87613
6407 | 0.81635
6408 | 0.72831
6409 | 0.68498
6410 | 0.62634
6411 | 0.60006
6412 | 0.59299
6413 | 0.61933
6414 | 0.7111
6415 | 0.81007
6416 | 0.81128
6417 | 0.75735
6418 | 0.71433
6419 | 0.66721
6420 | 0.63092
6421 | 0.63634
6422 | 0.64467
6423 | 0.67194
6424 | 0.74682
6425 | 0.83321
6426 | 0.89732
6427 | 0.98439
6428 | 0.99646
6429 | 0.95249
6430 | 0.89494
6431 | 0.82949
6432 | 0.74035
6433 | 0.67055
6434 | 0.63283
6435 | 0.60564
6436 | 0.59717
6437 | 0.62344
6438 | 0.71333
6439 | 0.81153
6440 | 0.8046
6441 | 0.75835
6442 | 0.7165
6443 | 0.69571
6444 | 0.68082
6445 | 0.69788
6446 | 0.69235
6447 | 0.71543
6448 | 0.76112
6449 | 0.84461
6450 | 0.91073
6451 | 0.96834
6452 | 0.99054
6453 | 0.95225
6454 | 0.88933
6455 | 0.82007
6456 | 0.73391
6457 | 0.67396
6458 | 0.62328
6459 | 0.59239
6460 | 0.58425
6461 | 0.60768
6462 | 0.69414
6463 | 0.7902
6464 | 0.78591
6465 | 0.74383
6466 | 0.71501
6467 | 0.70897
6468 | 0.67644
6469 | 0.67456
6470 | 0.68385
6471 | 0.73296
6472 | 0.79462
6473 | 0.8613
6474 | 0.90132
6475 | 0.94841
6476 | 0.95829
6477 | 0.91935
6478 | 0.86976
6479 | 0.81055
6480 | 0.72371
6481 | 0.6565
6482 | 0.61609
6483 | 0.58947
6484 | 0.58047
6485 | 0.60655
6486 | 0.69035
6487 | 0.78224
6488 | 0.77308
6489 | 0.72532
6490 | 0.67327
6491 | 0.63869
6492 | 0.61112
6493 | 0.62458
6494 | 0.61419
6495 | 0.62994
6496 | 0.71234
6497 | 0.80883
6498 | 0.87693
6499 | 0.93843
6500 | 0.96296
6501 | 0.92598
6502 | 0.86886
6503 | 0.79407
6504 | 0.71838
6505 | 0.65376
6506 | 0.63069
6507 | 0.5992
6508 | 0.59074
6509 | 0.61218
6510 | 0.69638
6511 | 0.78788
6512 | 0.77852
6513 | 0.73021
6514 | 0.65966
6515 | 0.63116
6516 | 0.60184
6517 | 0.60434
6518 | 0.64206
6519 | 0.68925
6520 | 0.76816
6521 | 0.8376
6522 | 0.88556
6523 | 0.92879
6524 | 0.93873
6525 | 0.90079
6526 | 0.86302
6527 | 0.81682
6528 | 0.74355
6529 | 0.66546
6530 | 0.62957
6531 | 0.59577
6532 | 0.58203
6533 | 0.58436
6534 | 0.61174
6535 | 0.65467
6536 | 0.6532
6537 | 0.62512
6538 | 0.57447
6539 | 0.55176
6540 | 0.51548
6541 | 0.52146
6542 | 0.51583
6543 | 0.5266
6544 | 0.62012
6545 | 0.736
6546 | 0.81764
6547 | 0.88625
6548 | 0.89441
6549 | 0.86828
6550 | 0.83782
6551 | 0.79636
6552 | 0.7331
6553 | 0.67144
6554 | 0.58732
6555 | 0.5556
6556 | 0.53851
6557 | 0.53392
6558 | 0.54736
6559 | 0.56509
6560 | 0.57268
6561 | 0.57325
6562 | 0.53883
6563 | 0.50679
6564 | 0.48048
6565 | 0.45521
6566 | 0.46386
6567 | 0.53696
6568 | 0.62203
6569 | 0.72744
6570 | 0.81509
6571 | 0.90685
6572 | 0.88558
6573 | 0.86553
6574 | 0.82081
6575 | 0.75588
6576 | 0.67359
6577 | 0.62877
6578 | 0.57151
6579 | 0.54442
6580 | 0.53936
6581 | 0.55783
6582 | 0.6434
6583 | 0.73204
6584 | 0.72921
6585 | 0.67758
6586 | 0.62379
6587 | 0.6062
6588 | 0.61837
6589 | 0.60765
6590 | 0.63815
6591 | 0.66135
6592 | 0.7285
6593 | 0.79548
6594 | 0.86768
6595 | 0.94917
6596 | 0.93392
6597 | 0.89335
6598 | 0.83716
6599 | 0.76806
6600 | 0.68207
6601 | 0.61337
6602 | 0.5784
6603 | 0.5497
6604 | 0.54084
6605 | 0.56237
6606 | 0.64477
6607 | 0.7302
6608 | 0.72797
6609 | 0.6813
6610 | 0.64124
6611 | 0.63094
6612 | 0.62395
6613 | 0.62141
6614 | 0.63605
6615 | 0.63996
6616 | 0.70073
6617 | 0.79848
6618 | 0.86974
6619 | 0.93325
6620 | 0.92823
6621 | 0.89221
6622 | 0.83022
6623 | 0.75783
6624 | 0.6748
6625 | 0.61744
6626 | 0.57464
6627 | 0.54436
6628 | 0.53546
6629 | 0.55408
6630 | 0.6335
6631 | 0.72002
6632 | 0.72278
6633 | 0.67759
6634 | 0.63029
6635 | 0.60781
6636 | 0.59239
6637 | 0.58967
6638 | 0.63163
6639 | 0.68058
6640 | 0.77057
6641 | 0.82512
6642 | 0.87511
6643 | 0.92651
6644 | 0.90792
6645 | 0.87085
6646 | 0.82166
6647 | 0.75803
6648 | 0.67365
6649 | 0.60646
6650 | 0.56951
6651 | 0.53971
6652 | 0.53367
6653 | 0.55066
6654 | 0.63146
6655 | 0.71703
6656 | 0.71721
6657 | 0.6686
6658 | 0.64016
6659 | 0.6197
6660 | 0.61249
6661 | 0.608
6662 | 0.61843
6663 | 0.64402
6664 | 0.70465
6665 | 0.78803
6666 | 0.86125
6667 | 0.91905
6668 | 0.91174
6669 | 0.8782
6670 | 0.82343
6671 | 0.74664
6672 | 0.66552
6673 | 0.60327
6674 | 0.57625
6675 | 0.54545
6676 | 0.53613
6677 | 0.55527
6678 | 0.62948
6679 | 0.7141
6680 | 0.71263
6681 | 0.67941
6682 | 0.64612
6683 | 0.61657
6684 | 0.61984
6685 | 0.60482
6686 | 0.60965
6687 | 0.65044
6688 | 0.72471
6689 | 0.78857
6690 | 0.853
6691 | 0.89683
6692 | 0.87947
6693 | 0.843
6694 | 0.80853
6695 | 0.76238
6696 | 0.68423
6697 | 0.61089
6698 | 0.58572
6699 | 0.55255
6700 | 0.53777
6701 | 0.53617
6702 | 0.55938
6703 | 0.59525
6704 | 0.60605
6705 | 0.58101
6706 | 0.55129
6707 | 0.54142
6708 | 0.53021
6709 | 0.51167
6710 | 0.53194
6711 | 0.57119
6712 | 0.65937
6713 | 0.74099
6714 | 0.81154
6715 | 0.87302
6716 | 0.85071
6717 | 0.82434
6718 | 0.79538
6719 | 0.75469
6720 | 0.68586
6721 | 0.62781
6722 | 0.58973
6723 | 0.55844
6724 | 0.54089
6725 | 0.53692
6726 | 0.54897
6727 | 0.56919
6728 | 0.57125
6729 | 0.54979
6730 | 0.50882
6731 | 0.4783
6732 | 0.47122
6733 | 0.47891
6734 | 0.51988
6735 | 0.58711
6736 | 0.67747
6737 | 0.76582
6738 | 0.83859
6739 | 0.90667
6740 | 0.88344
6741 | 0.86553
6742 | 0.82878
6743 | 0.75963
6744 | 0.6739
6745 | 0.63202
6746 | 0.56842
6747 | 0.54118
6748 | 0.53615
6749 | 0.55716
6750 | 0.64221
6751 | 0.7328
6752 | 0.73207
6753 | 0.67484
6754 | 0.60895
6755 | 0.58271
6756 | 0.56838
6757 | 0.5563
6758 | 0.57719
6759 | 0.61692
6760 | 0.70172
6761 | 0.80121
6762 | 0.87963
6763 | 0.94821
6764 | 0.9314
6765 | 0.89075
6766 | 0.83634
6767 | 0.76517
6768 | 0.67565
6769 | 0.61431
6770 | 0.57695
6771 | 0.5486
6772 | 0.539
6773 | 0.5601
6774 | 0.64456
6775 | 0.73365
6776 | 0.73084
6777 | 0.67957
6778 | 0.63301
6779 | 0.60001
6780 | 0.59656
6781 | 0.6019
6782 | 0.61694
6783 | 0.64435
6784 | 0.71036
6785 | 0.80838
6786 | 0.88084
6787 | 0.93542
6788 | 0.92726
6789 | 0.88973
6790 | 0.82813
6791 | 0.75718
6792 | 0.67212
6793 | 0.61692
6794 | 0.57813
6795 | 0.54744
6796 | 0.53922
6797 | 0.55767
6798 | 0.64041
6799 | 0.72807
6800 | 0.7294
6801 | 0.67845
6802 | 0.63167
6803 | 0.6127
6804 | 0.58729
6805 | 0.5926
6806 | 0.62191
6807 | 0.64846
6808 | 0.74393
6809 | 0.82806
6810 | 0.89277
6811 | 0.93594
6812 | 0.91495
6813 | 0.87661
6814 | 0.82744
6815 | 0.76409
6816 | 0.67523
6817 | 0.61144
6818 | 0.576
6819 | 0.54829
6820 | 0.53889
6821 | 0.5597
6822 | 0.641
6823 | 0.73038
6824 | 0.72647
6825 | 0.68458
6826 | 0.65834
6827 | 0.6331
6828 | 0.63198
6829 | 0.65905
6830 | 0.69759
6831 | 0.71265
6832 | 0.76023
6833 | 0.83308
6834 | 0.88724
6835 | 0.93347
6836 | 0.9264
6837 | 0.88749
6838 | 0.83273
6839 | 0.7596
6840 | 0.67511
6841 | 0.61048
6842 | 0.57715
6843 | 0.54466
6844 | 0.53611
6845 | 0.55484
6846 | 0.63361
6847 | 0.71586
6848 | 0.72868
6849 | 0.70396
6850 | 0.6709
6851 | 0.63968
6852 | 0.63529
6853 | 0.65374
6854 | 0.64517
6855 | 0.67232
6856 | 0.72489
6857 | 0.80528
6858 | 0.86293
6859 | 0.90417
6860 | 0.8834
6861 | 0.84391
6862 | 0.80656
6863 | 0.7615
6864 | 0.68324
6865 | 0.60736
6866 | 0.58909
6867 | 0.55388
6868 | 0.53911
6869 | 0.53745
6870 | 0.5622
6871 | 0.59951
6872 | 0.60931
6873 | 0.58939
6874 | 0.56067
6875 | 0.55822
6876 | 0.55364
6877 | 0.53199
6878 | 0.54865
6879 | 0.59801
6880 | 0.68897
6881 | 0.76425
6882 | 0.83291
6883 | 0.88051
6884 | 0.85565
6885 | 0.82806
6886 | 0.79541
6887 | 0.7564
6888 | 0.68793
6889 | 0.62736
6890 | 0.5932
6891 | 0.56087
6892 | 0.54337
6893 | 0.53904
6894 | 0.55302
6895 | 0.57442
6896 | 0.60924
6897 | 0.6389
6898 | 0.60782
6899 | 0.57087
6900 | 0.54533
6901 | 0.53879
6902 | 0.54133
6903 | 0.58818
6904 | 0.68181
6905 | 0.78754
6906 | 0.85107
6907 | 0.91604
6908 | 0.88915
6909 | 0.87017
6910 | 0.83205
6911 | 0.76311
6912 | 0.67742
6913 | 0.63162
6914 | 0.57207
6915 | 0.54108
6916 | 0.53599
6917 | 0.55663
6918 | 0.64187
6919 | 0.73073
6920 | 0.73804
6921 | 0.68741
6922 | 0.63152
6923 | 0.60126
6924 | 0.59699
6925 | 0.60336
6926 | 0.61651
6927 | 0.65571
6928 | 0.73307
6929 | 0.82406
6930 | 0.88874
6931 | 0.95075
6932 | 0.93191
6933 | 0.88869
6934 | 0.83543
6935 | 0.76489
6936 | 0.67516
6937 | 0.61117
6938 | 0.58037
6939 | 0.55129
6940 | 0.54212
6941 | 0.56261
6942 | 0.64688
6943 | 0.73759
6944 | 0.74558
6945 | 0.70315
6946 | 0.67433
6947 | 0.64447
6948 | 0.60958
6949 | 0.61034
6950 | 0.64055
6951 | 0.66101
6952 | 0.74623
6953 | 0.82403
6954 | 0.89536
6955 | 0.94247
6956 | 0.93319
6957 | 0.89251
6958 | 0.83097
6959 | 0.7595
6960 | 0.67442
6961 | 0.61567
6962 | 0.57242
6963 | 0.54017
6964 | 0.53197
6965 | 0.55131
6966 | 0.63188
6967 | 0.71958
6968 | 0.72462
6969 | 0.67669
6970 | 0.64588
6971 | 0.64055
6972 | 0.59938
6973 | 0.58858
6974 | 0.62375
6975 | 0.63654
6976 | 0.70629
6977 | 0.80461
6978 | 0.87463
6979 | 0.92319
6980 | 0.90718
6981 | 0.86821
6982 | 0.82036
6983 | 0.754
6984 | 0.66584
6985 | 0.60327
6986 | 0.55956
6987 | 0.53085
6988 | 0.52441
6989 | 0.54202
6990 | 0.62269
6991 | 0.70782
6992 | 0.70097
6993 | 0.65041
6994 | 0.61414
6995 | 0.60751
6996 | 0.59328
6997 | 0.58739
6998 | 0.60803
6999 | 0.64766
7000 | 0.72168
7001 | 0.79161
7002 | 0.8529
7003 | 0.90597
7004 | 0.90457
7005 | 0.86869
7006 | 0.80992
7007 | 0.7342
7008 | 0.65256
7009 | 0.5899
7010 | 0.57655
7011 | 0.54793
7012 | 0.5385
7013 | 0.5579
7014 | 0.63671
7015 | 0.72362
7016 | 0.74542
7017 | 0.71038
7018 | 0.65564
7019 | 0.62619
7020 | 0.59095
7021 | 0.56688
7022 | 0.59324
7023 | 0.64987
7024 | 0.72511
7025 | 0.81027
7026 | 0.87277
7027 | 0.9121
7028 | 0.89208
7029 | 0.85122
7030 | 0.81326
7031 | 0.76537
7032 | 0.688
7033 | 0.60985
7034 | 0.58435
7035 | 0.55347
7036 | 0.53679
7037 | 0.53528
7038 | 0.5596
7039 | 0.59783
7040 | 0.61291
7041 | 0.58936
7042 | 0.55744
7043 | 0.5293
7044 | 0.50223
7045 | 0.49265
7046 | 0.49421
7047 | 0.54093
7048 | 0.64636
7049 | 0.74531
7050 | 0.83014
7051 | 0.87906
7052 | 0.85528
7053 | 0.82598
7054 | 0.79193
7055 | 0.75172
7056 | 0.68396
7057 | 0.62393
7058 | 0.57659
7059 | 0.54865
7060 | 0.53092
7061 | 0.5268
7062 | 0.53851
7063 | 0.56177
7064 | 0.56764
7065 | 0.55326
7066 | 0.51168
7067 | 0.48757
7068 | 0.46733
7069 | 0.45976
7070 | 0.48291
7071 | 0.53157
7072 | 0.63622
7073 | 0.74361
7074 | 0.83918
7075 | 0.90266
7076 | 0.8796
7077 | 0.85326
7078 | 0.80697
7079 | 0.74014
7080 | 0.65538
7081 | 0.61781
7082 | 0.56219
7083 | 0.53868
7084 | 0.53012
7085 | 0.55098
7086 | 0.63565
7087 | 0.72822
7088 | 0.73235
7089 | 0.6875
7090 | 0.66108
7091 | 0.66433
7092 | 0.6695
7093 | 0.66914
7094 | 0.66872
7095 | 0.68939
7096 | 0.75611
7097 | 0.83089
7098 | 0.89481
7099 | 0.95088
7100 | 0.93114
7101 | 0.88272
7102 | 0.82743
7103 | 0.75387
7104 | 0.66541
7105 | 0.60374
7106 | 0.56831
7107 | 0.54409
7108 | 0.5345
7109 | 0.55545
7110 | 0.63758
7111 | 0.72906
7112 | 0.73535
7113 | 0.69194
7114 | 0.63806
7115 | 0.59811
7116 | 0.60091
7117 | 0.59692
7118 | 0.62528
7119 | 0.6805
7120 | 0.76056
7121 | 0.82664
7122 | 0.88972
7123 | 0.93663
7124 | 0.92803
7125 | 0.88346
7126 | 0.81832
7127 | 0.74444
7128 | 0.65955
7129 | 0.60632
7130 | 0.56367
7131 | 0.5342
7132 | 0.52499
7133 | 0.54394
7134 | 0.62549
7135 | 0.71489
7136 | 0.71705
7137 | 0.6597
7138 | 0.61092
7139 | 0.57193
7140 | 0.57879
7141 | 0.59336
7142 | 0.63946
7143 | 0.65844
7144 | 0.75195
7145 | 0.80957
7146 | 0.87098
7147 | 0.91295
7148 | 0.89905
7149 | 0.86087
7150 | 0.81188
7151 | 0.74348
7152 | 0.65463
7153 | 0.59446
7154 | 0.55844
7155 | 0.53423
7156 | 0.52745
7157 | 0.54712
7158 | 0.62673
7159 | 0.71741
7160 | 0.71083
7161 | 0.662
7162 | 0.61419
7163 | 0.59513
7164 | 0.57121
7165 | 0.582
7166 | 0.61467
7167 | 0.63971
7168 | 0.72217
7169 | 0.80754
7170 | 0.86579
7171 | 0.90475
7172 | 0.90968
7173 | 0.87303
7174 | 0.81591
7175 | 0.73919
7176 | 0.65552
7177 | 0.59276
7178 | 0.55629
7179 | 0.52361
7180 | 0.51909
7181 | 0.53767
7182 | 0.61354
7183 | 0.70087
7184 | 0.7067
7185 | 0.66166
7186 | 0.61102
7187 | 0.58161
7188 | 0.56888
7189 | 0.56117
7190 | 0.58841
7191 | 0.64234
7192 | 0.72705
7193 | 0.7951
7194 | 0.841
7195 | 0.87623
7196 | 0.86816
7197 | 0.82601
7198 | 0.78404
7199 | 0.73419
7200 | 0.65622
7201 | 0.59004
7202 | 0.5743
7203 | 0.54184
7204 | 0.53022
7205 | 0.5266
7206 | 0.55086
7207 | 0.59057
7208 | 0.61438
7209 | 0.59524
7210 | 0.57913
7211 | 0.54107
7212 | 0.50595
7213 | 0.51756
7214 | 0.55137
7215 | 0.6133
7216 | 0.69263
7217 | 0.76564
7218 | 0.8229
7219 | 0.86316
7220 | 0.84404
7221 | 0.81587
7222 | 0.78372
7223 | 0.73819
7224 | 0.66973
7225 | 0.61442
7226 | 0.58374
7227 | 0.5525
7228 | 0.53856
7229 | 0.5336
7230 | 0.54839
7231 | 0.57081
7232 | 0.59395
7233 | 0.60909
7234 | 0.59229
7235 | 0.58374
7236 | 0.57632
7237 | 0.55849
7238 | 0.53922
7239 | 0.58893
7240 | 0.67451
7241 | 0.77559
7242 | 0.84534
7243 | 0.90217
7244 | 0.88497
7245 | 0.85883
7246 | 0.8151
7247 | 0.74683
7248 | 0.66188
7249 | 0.62241
7250 | 0.55803
7251 | 0.5306
7252 | 0.53027
7253 | 0.54851
7254 | 0.63649
7255 | 0.72439
7256 | 0.74098
7257 | 0.68996
7258 | 0.65605
7259 | 0.64583
7260 | 0.62689
7261 | 0.62958
7262 | 0.63904
7263 | 0.66887
7264 | 0.74925
7265 | 0.83023
7266 | 0.87563
7267 | 0.93085
7268 | 0.92242
7269 | 0.87298
7270 | 0.8148
7271 | 0.74384
7272 | 0.65514
7273 | 0.59746
7274 | 0.56734
7275 | 0.53957
7276 | 0.53535
7277 | 0.55633
7278 | 0.6429
7279 | 0.72982
7280 | 0.74874
7281 | 0.72487
7282 | 0.67961
7283 | 0.64117
7284 | 0.59895
7285 | 0.61166
7286 | 0.62518
7287 | 0.65417
7288 | 0.71899
7289 | 0.80406
7290 | 0.88062
7291 | 0.9239
7292 | 0.92549
7293 | 0.88037
7294 | 0.81389
7295 | 0.73893
7296 | 0.65621
7297 | 0.6047
7298 | 0.54631
7299 | 0.51828
7300 | 0.51008
7301 | 0.53562
7302 | 0.62988
7303 | 0.72071
7304 | 0.71958
7305 | 0.65881
7306 | 0.61848
7307 | 0.59829
7308 | 0.57508
7309 | 0.57872
7310 | 0.57986
7311 | 0.62013
7312 | 0.73101
7313 | 0.80315
7314 | 0.86696
7315 | 0.91372
7316 | 0.88268
7317 | 0.83689
7318 | 0.78989
7319 | 0.72947
7320 | 0.64474
7321 | 0.58089
7322 | 0.5436
7323 | 0.51726
7324 | 0.51225
7325 | 0.53959
7326 | 0.63543
7327 | 0.7237
7328 | 0.73908
7329 | 0.67349
7330 | 0.61809
7331 | 0.59109
7332 | 0.55889
7333 | 0.55842
7334 | 0.55537
7335 | 0.59788
7336 | 0.68478
7337 | 0.79222
7338 | 0.8654
7339 | 0.9121
7340 | 0.88867
7341 | 0.8513
7342 | 0.7971
7343 | 0.72689
7344 | 0.64657
7345 | 0.58136
7346 | 0.54959
7347 | 0.51854
7348 | 0.50846
7349 | 0.53854
7350 | 0.63089
7351 | 0.72003
7352 | 0.72213
7353 | 0.68069
7354 | 0.61931
7355 | 0.58837
7356 | 0.5682
7357 | 0.54489
7358 | 0.54868
7359 | 0.61453
7360 | 0.71745
7361 | 0.7925
7362 | 0.85372
7363 | 0.89077
7364 | 0.86559
7365 | 0.82259
7366 | 0.78125
7367 | 0.73408
7368 | 0.65854
7369 | 0.58697
7370 | 0.55698
7371 | 0.52522
7372 | 0.51021
7373 | 0.51818
7374 | 0.55172
7375 | 0.59456
7376 | 0.62029
7377 | 0.59258
7378 | 0.57478
7379 | 0.54564
7380 | 0.51796
7381 | 0.4925
7382 | 0.4838
7383 | 0.53234
7384 | 0.62889
7385 | 0.72613
7386 | 0.80723
7387 | 0.8593
7388 | 0.82811
7389 | 0.79627
7390 | 0.76455
7391 | 0.72369
7392 | 0.65837
7393 | 0.6002
7394 | 0.55446
7395 | 0.52479
7396 | 0.50589
7397 | 0.51158
7398 | 0.53342
7399 | 0.55901
7400 | 0.58503
7401 | 0.5967
7402 | 0.57877
7403 | 0.54353
7404 | 0.51498
7405 | 0.47608
7406 | 0.45325
7407 | 0.50919
7408 | 0.603
7409 | 0.72028
7410 | 0.81604
7411 | 0.88366
7412 | 0.85045
7413 | 0.82381
7414 | 0.78326
7415 | 0.71636
7416 | 0.63459
7417 | 0.59811
7418 | 0.53345
7419 | 0.50796
7420 | 0.50234
7421 | 0.53354
7422 | 0.62681
7423 | 0.7184
7424 | 0.73129
7425 | 0.66922
7426 | 0.60866
7427 | 0.57595
7428 | 0.55436
7429 | 0.54693
7430 | 0.55522
7431 | 0.59329
7432 | 0.67681
7433 | 0.77296
7434 | 0.85568
7435 | 0.92287
7436 | 0.8961
7437 | 0.84512
7438 | 0.79393
7439 | 0.72119
7440 | 0.63635
7441 | 0.57721
7442 | 0.53908
7443 | 0.51182
7444 | 0.5025
7445 | 0.53429
7446 | 0.62775
7447 | 0.71821
7448 | 0.72664
7449 | 0.68406
7450 | 0.65223
7451 | 0.65384
7452 | 0.64031
7453 | 0.64209
7454 | 0.65762
7455 | 0.6808
7456 | 0.72292
7457 | 0.7907
7458 | 0.85722
7459 | 0.90695
7460 | 0.89043
7461 | 0.84388
7462 | 0.78507
7463 | 0.71335
7464 | 0.63052
7465 | 0.57963
7466 | 0.53029
7467 | 0.50104
7468 | 0.4933
7469 | 0.52105
7470 | 0.61084
7471 | 0.69924
7472 | 0.70572
7473 | 0.64551
7474 | 0.5716
7475 | 0.54848
7476 | 0.53221
7477 | 0.53649
7478 | 0.52991
7479 | 0.58675
7480 | 0.68557
7481 | 0.77068
7482 | 0.83974
7483 | 0.8839
7484 | 0.85978
7485 | 0.81268
7486 | 0.76692
7487 | 0.70723
7488 | 0.62327
7489 | 0.56501
7490 | 0.51675
7491 | 0.48873
7492 | 0.48142
7493 | 0.51193
7494 | 0.60238
7495 | 0.68932
7496 | 0.68972
7497 | 0.62085
7498 | 0.56451
7499 | 0.54132
7500 | 0.50535
7501 | 0.51139
7502 | 0.51569
7503 | 0.57815
7504 | 0.66965
7505 | 0.75887
7506 | 0.81592
7507 | 0.86521
7508 | 0.85478
7509 | 0.80505
7510 | 0.76017
7511 | 0.69044
7512 | 0.61277
7513 | 0.55525
7514 | 0.54714
7515 | 0.51147
7516 | 0.48983
7517 | 0.50219
7518 | 0.54051
7519 | 0.5711
7520 | 0.57816
7521 | 0.59514
7522 | 0.5663
7523 | 0.54428
7524 | 0.50425
7525 | 0.4884
7526 | 0.49349
7527 | 0.53275
7528 | 0.6219
7529 | 0.70702
7530 | 0.78211
7531 | 0.81222
7532 | 0.78245
7533 | 0.74879
7534 | 0.7301
7535 | 0.6888
7536 | 0.62273
7537 | 0.58353
7538 | 0.52979
7539 | 0.49778
7540 | 0.48361
7541 | 0.48959
7542 | 0.52255
7543 | 0.55978
7544 | 0.58805
7545 | 0.56148
7546 | 0.53864
7547 | 0.51116
7548 | 0.48436
7549 | 0.49289
7550 | 0.48345
7551 | 0.53867
7552 | 0.61011
7553 | 0.69043
7554 | 0.75871
7555 | 0.81203
7556 | 0.79256
7557 | 0.76118
7558 | 0.73035
7559 | 0.68972
7560 | 0.6249
7561 | 0.57403
7562 | 0.54186
7563 | 0.51218
7564 | 0.49478
7565 | 0.4965
7566 | 0.52047
7567 | 0.54138
7568 | 0.56298
7569 | 0.5513
7570 | 0.50983
7571 | 0.48286
7572 | 0.45484
7573 | 0.43347
7574 | 0.44393
7575 | 0.49411
7576 | 0.58678
7577 | 0.70503
7578 | 0.79169
7579 | 0.86171
7580 | 0.83452
7581 | 0.8076
7582 | 0.77279
7583 | 0.70354
7584 | 0.62148
7585 | 0.58653
7586 | 0.52391
7587 | 0.49859
7588 | 0.4939
7589 | 0.52167
7590 | 0.62015
7591 | 0.70751
7592 | 0.72136
7593 | 0.66229
7594 | 0.60919
7595 | 0.56244
7596 | 0.54036
7597 | 0.55454
7598 | 0.55263
7599 | 0.58901
7600 | 0.67169
7601 | 0.75712
7602 | 0.83916
7603 | 0.90662
7604 | 0.88384
7605 | 0.83348
7606 | 0.78154
7607 | 0.71368
7608 | 0.62734
7609 | 0.56909
7610 | 0.53674
7611 | 0.51115
7612 | 0.50135
7613 | 0.52956
7614 | 0.62769
7615 | 0.71655
7616 | 0.73124
7617 | 0.68026
7618 | 0.6055
7619 | 0.56086
7620 | 0.52916
7621 | 0.54096
7622 | 0.52532
7623 | 0.57309
7624 | 0.68345
7625 | 0.7881
7626 | 0.84792
7627 | 0.89978
7628 | 0.88759
7629 | 0.83977
7630 | 0.78439
7631 | 0.71405
7632 | 0.63108
7633 | 0.57873
7634 | 0.53751
7635 | 0.50967
7636 | 0.50125
7637 | 0.5286
7638 | 0.62275
7639 | 0.71234
7640 | 0.72939
7641 | 0.68271
7642 | 0.62709
7643 | 0.60436
7644 | 0.58723
7645 | 0.5846
7646 | 0.58383
7647 | 0.65754
7648 | 0.73244
7649 | 0.80317
7650 | 0.85902
7651 | 0.90111
7652 | 0.87528
7653 | 0.82882
7654 | 0.78167
7655 | 0.72312
7656 | 0.63968
7657 | 0.57369
7658 | 0.52826
7659 | 0.49988
7660 | 0.49192
7661 | 0.51832
7662 | 0.6145
7663 | 0.70223
7664 | 0.7154
7665 | 0.65567
7666 | 0.61753
7667 | 0.60501
7668 | 0.6043
7669 | 0.6114
7670 | 0.60683
7671 | 0.64149
7672 | 0.71521
7673 | 0.79034
7674 | 0.83727
7675 | 0.88259
7676 | 0.86914
7677 | 0.82546
7678 | 0.76995
7679 | 0.70722
7680 | 0.62823
7681 | 0.56739
7682 | 0.53611
7683 | 0.50418
7684 | 0.49455
7685 | 0.51978
7686 | 0.60913
7687 | 0.69956
7688 | 0.72385
7689 | 0.68294
7690 | 0.63268
7691 | 0.6296
7692 | 0.60079
7693 | 0.61859
7694 | 0.61928
7695 | 0.66777
7696 | 0.72236
7697 | 0.78892
7698 | 0.83218
7699 | 0.86723
7700 | 0.84048
7701 | 0.79785
7702 | 0.76029
7703 | 0.72075
7704 | 0.64642
7705 | 0.5762
7706 | 0.54506
7707 | 0.51232
7708 | 0.49831
7709 | 0.50342
7710 | 0.5377
7711 | 0.58077
7712 | 0.61709
7713 | 0.60614
7714 | 0.56052
7715 | 0.51904
7716 | 0.48343
7717 | 0.47744
7718 | 0.46524
7719 | 0.53633
7720 | 0.64249
7721 | 0.7211
7722 | 0.79519
7723 | 0.8381
7724 | 0.81202
7725 | 0.78279
7726 | 0.75331
7727 | 0.71434
7728 | 0.64871
7729 | 0.59122
7730 | 0.54969
7731 | 0.519
7732 | 0.50236
7733 | 0.50484
7734 | 0.52661
7735 | 0.55576
7736 | 0.58724
7737 | 0.59589
7738 | 0.57263
7739 | 0.53904
7740 | 0.52533
7741 | 0.52017
7742 | 0.51937
7743 | 0.58908
7744 | 0.66068
7745 | 0.75004
7746 | 0.81532
7747 | 0.87423
7748 | 0.84455
7749 | 0.81988
7750 | 0.78408
7751 | 0.71786
7752 | 0.63562
7753 | 0.59631
7754 | 0.53291
7755 | 0.50629
7756 | 0.50193
7757 | 0.52979
7758 | 0.62619
7759 | 0.72264
7760 | 0.75458
7761 | 0.71552
7762 | 0.6474
7763 | 0.65666
7764 | 0.65709
7765 | 0.66625
7766 | 0.65597
7767 | 0.70345
7768 | 0.76012
7769 | 0.81924
7770 | 0.86591
7771 | 0.91787
7772 | 0.89547
7773 | 0.84516
7774 | 0.79549
7775 | 0.72675
7776 | 0.64281
7777 | 0.5793
7778 | 0.53759
7779 | 0.5104
7780 | 0.5023
7781 | 0.53008
7782 | 0.62468
7783 | 0.71874
7784 | 0.74803
7785 | 0.72352
7786 | 0.68449
7787 | 0.67283
7788 | 0.66831
7789 | 0.67786
7790 | 0.64512
7791 | 0.66109
7792 | 0.7339
7793 | 0.8029
7794 | 0.85359
7795 | 0.90021
7796 | 0.88624
7797 | 0.84203
7798 | 0.78568
7799 | 0.71615
7800 | 0.63489
7801 | 0.58132
7802 | 0.53361
7803 | 0.50423
7804 | 0.49623
7805 | 0.52347
7806 | 0.61599
7807 | 0.70672
7808 | 0.73513
7809 | 0.71267
7810 | 0.67942
7811 | 0.64921
7812 | 0.64312
7813 | 0.63211
7814 | 0.62317
7815 | 0.64915
7816 | 0.72667
7817 | 0.80126
7818 | 0.84845
7819 | 0.89178
7820 | 0.86804
7821 | 0.82098
7822 | 0.77972
7823 | 0.71817
7824 | 0.6356
7825 | 0.57234
7826 | 0.52307
7827 | 0.49376
7828 | 0.48542
7829 | 0.51216
7830 | 0.6031
7831 | 0.69431
7832 | 0.71915
7833 | 0.70588
7834 | 0.67582
7835 | 0.63136
7836 | 0.60117
7837 | 0.6044
7838 | 0.61857
7839 | 0.64523
7840 | 0.7084
7841 | 0.77915
7842 | 0.83086
7843 | 0.87312
7844 | 0.86047
7845 | 0.81555
7846 | 0.76609
7847 | 0.69327
7848 | 0.62053
7849 | 0.5634
7850 | 0.54162
7851 | 0.50205
7852 | 0.48198
7853 | 0.49392
7854 | 0.52608
7855 | 0.5568
7856 | 0.58152
7857 | 0.58984
7858 | 0.55845
7859 | 0.54165
7860 | 0.53048
7861 | 0.53977
7862 | 0.55294
7863 | 0.55833
7864 | 0.65125
7865 | 0.71394
7866 | 0.76601
7867 | 0.79542
7868 | 0.77002
7869 | 0.735
7870 | 0.71836
7871 | 0.6795
7872 | 0.61825
7873 | 0.57919
7874 | 0.52941
7875 | 0.49431
7876 | 0.48001
7877 | 0.48623
7878 | 0.51508
7879 | 0.55409
7880 | 0.59411
7881 | 0.5832
7882 | 0.54607
7883 | 0.51597
7884 | 0.49879
7885 | 0.5052
7886 | 0.48526
7887 | 0.52107
7888 | 0.60442
7889 | 0.69419
7890 | 0.75888
7891 | 0.80798
7892 | 0.78311
7893 | 0.75319
7894 | 0.72564
7895 | 0.6873
7896 | 0.6254
7897 | 0.57814
7898 | 0.53476
7899 | 0.50177
7900 | 0.48461
7901 | 0.48794
7902 | 0.50629
7903 | 0.52867
7904 | 0.56657
7905 | 0.58063
7906 | 0.55545
7907 | 0.5115
7908 | 0.50338
7909 | 0.49428
7910 | 0.47172
7911 | 0.53237
7912 | 0.619
7913 | 0.71186
7914 | 0.78225
7915 | 0.84716
7916 | 0.82066
7917 | 0.79539
7918 | 0.75599
7919 | 0.6934
7920 | 0.61519
7921 | 0.58185
7922 | 0.51975
7923 | 0.49117
7924 | 0.48648
7925 | 0.51559
7926 | 0.60964
7927 | 0.69978
7928 | 0.73611
7929 | 0.698
7930 | 0.65885
7931 | 0.64193
7932 | 0.6236
7933 | 0.62472
7934 | 0.62263
7935 | 0.65664
7936 | 0.71349
7937 | 0.78306
7938 | 0.83591
7939 | 0.89356
7940 | 0.87246
7941 | 0.82372
7942 | 0.77052
7943 | 0.70456
7944 | 0.62324
7945 | 0.56814
7946 | 0.52943
7947 | 0.50039
7948 | 0.49187
7949 | 0.52164
7950 | 0.61339
7951 | 0.70192
7952 | 0.73235
7953 | 0.69475
7954 | 0.65725
7955 | 0.63871
7956 | 0.62115
7957 | 0.60281
7958 | 0.58419
7959 | 0.62866
7960 | 0.69788
7961 | 0.77789
7962 | 0.83539
7963 | 0.88379
7964 | 0.87183
7965 | 0.82641
7966 | 0.76958
7967 | 0.70095
7968 | 0.62353
7969 | 0.57543
7970 | 0.52805
7971 | 0.49489
7972 | 0.48695
7973 | 0.51391
7974 | 0.60447
7975 | 0.6926
7976 | 0.72267
7977 | 0.67119
7978 | 0.62419
7979 | 0.59993
7980 | 0.57688
7981 | 0.57976
7982 | 0.59302
7983 | 0.64079
7984 | 0.7252
7985 | 0.78901
7986 | 0.83294
7987 | 0.87564
7988 | 0.85157
7989 | 0.80731
7990 | 0.76197
7991 | 0.70292
7992 | 0.62313
7993 | 0.56648
7994 | 0.52451
7995 | 0.49419
7996 | 0.48547
7997 | 0.51096
7998 | 0.60038
7999 | 0.68707
8000 | 0.72263
8001 | 0.70466
8002 | 0.67964
8003 | 0.65637
8004 | 0.63274
8005 | 0.65047
8006 | 0.66144
8007 | 0.66037
8008 | 0.68462
8009 | 0.76766
8010 | 0.82167
8011 | 0.8657
8012 | 0.85632
8013 | 0.81207
8014 | 0.76159
8015 | 0.69497
8016 | 0.61386
8017 | 0.56274
8018 | 0.53138
8019 | 0.49707
8020 | 0.48174
8021 | 0.50557
8022 | 0.57729
8023 | 0.6526
8024 | 0.67556
8025 | 0.64483
8026 | 0.61269
8027 | 0.58666
8028 | 0.55864
8029 | 0.54409
8030 | 0.55207
8031 | 0.56635
8032 | 0.64021
8033 | 0.70993
8034 | 0.7725
8035 | 0.81824
8036 | 0.80966
8037 | 0.78191
8038 | 0.74538
8039 | 0.71014
8040 | 0.64303
8041 | 0.57009
8042 | 0.537
8043 | 0.49719
8044 | 0.47919
8045 | 0.4832
8046 | 0.50345
8047 | 0.53493
8048 | 0.57838
8049 | 0.57656
8050 | 0.56909
8051 | 0.54694
8052 | 0.50642
8053 | 0.50949
8054 | 0.49296
8055 | 0.51453
8056 | 0.56626
8057 | 0.64537
8058 | 0.72632
8059 | 0.78344
8060 | 0.77519
8061 | 0.76104
8062 | 0.73451
8063 | 0.69811
8064 | 0.63854
8065 | 0.58254
8066 | 0.54056
8067 | 0.50471
8068 | 0.48431
8069 | 0.48596
8070 | 0.4965
8071 | 0.51474
8072 | 0.53926
8073 | 0.54048
8074 | 0.49592
8075 | 0.43143
8076 | 0.40684
8077 | 0.39643
8078 | 0.40903
8079 | 0.47046
8080 | 0.57066
8081 | 0.65279
8082 | 0.74656
8083 | 0.81685
8084 | 0.80342
8085 | 0.78923
8086 | 0.76075
8087 | 0.70231
8088 | 0.62807
8089 | 0.58706
8090 | 0.52358
8091 | 0.4912
8092 | 0.48233
8093 | 0.50773
8094 | 0.58797
8095 | 0.66886
8096 | 0.70192
8097 | 0.66081
8098 | 0.61362
8099 | 0.58922
8100 | 0.57461
8101 | 0.56483
8102 | 0.57638
8103 | 0.60198
8104 | 0.66191
8105 | 0.73208
8106 | 0.79274
8107 | 0.85886
8108 | 0.85035
8109 | 0.81532
8110 | 0.77679
8111 | 0.71164
8112 | 0.63358
8113 | 0.57
8114 | 0.53962
8115 | 0.50658
8116 | 0.49325
8117 | 0.5197
8118 | 0.59922
8119 | 0.67965
8120 | 0.71074
8121 | 0.67353
8122 | 0.60848
8123 | 0.5667
8124 | 0.54346
8125 | 0.53265
8126 | 0.54058
8127 | 0.57295
8128 | 0.63883
8129 | 0.73379
8130 | 0.80773
8131 | 0.85981
8132 | 0.85722
8133 | 0.82633
8134 | 0.78148
8135 | 0.71598
8136 | 0.64075
8137 | 0.5822
8138 | 0.5283
8139 | 0.49302
8140 | 0.47963
8141 | 0.50409
8142 | 0.57956
8143 | 0.65726
8144 | 0.68774
8145 | 0.63906
8146 | 0.5886
8147 | 0.52668
8148 | 0.50701
8149 | 0.50277
8150 | 0.51593
8151 | 0.5593
8152 | 0.64522
8153 | 0.72571
8154 | 0.78901
8155 | 0.83821
8156 | 0.82719
8157 | 0.79591
8158 | 0.76041
8159 | 0.702
8160 | 0.62698
8161 | 0.56532
8162 | 0.52304
8163 | 0.49267
8164 | 0.4803
8165 | 0.50322
8166 | 0.57635
8167 | 0.65122
8168 | 0.68118
8169 | 0.64439
8170 | 0.60282
8171 | 0.55215
8172 | 0.53323
8173 | 0.55407
8174 | 0.55391
8175 | 0.58436
8176 | 0.63783
8177 | 0.7171
8178 | 0.77955
8179 | 0.8297
8180 | 0.83295
8181 | 0.80354
8182 | 0.76384
8183 | 0.69658
8184 | 0.62477
8185 | 0.56116
8186 | 0.53264
8187 | 0.49771
8188 | 0.48572
8189 | 0.50576
8190 | 0.57732
8191 | 0.65177
8192 | 0.68478
8193 | 0.66986
8194 | 0.64601
8195 | 0.6172
8196 | 0.6174
8197 | 0.60212
8198 | 0.62002
8199 | 0.63439
8200 | 0.6788
8201 | 0.72894
8202 | 0.77938
8203 | 0.82019
8204 | 0.81235
8205 | 0.78653
8206 | 0.75184
8207 | 0.70904
8208 | 0.64152
8209 | 0.56452
8210 | 0.54969
8211 | 0.51354
8212 | 0.49155
8213 | 0.49421
8214 | 0.51524
8215 | 0.54892
8216 | 0.59156
8217 | 0.57946
8218 | 0.5645
8219 | 0.52453
8220 | 0.49102
8221 | 0.49694
8222 | 0.49422
8223 | 0.53398
8224 | 0.60301
8225 | 0.68621
8226 | 0.75412
8227 | 0.80598
8228 | 0.78937
8229 | 0.77735
8230 | 0.74806
8231 | 0.71177
8232 | 0.65318
8233 | 0.59298
8234 | 0.55275
8235 | 0.51802
8236 | 0.49567
8237 | 0.4958
8238 | 0.50654
8239 | 0.52679
8240 | 0.5663
8241 | 0.56709
8242 | 0.54173
8243 | 0.49626
8244 | 0.48744
8245 | 0.47742
8246 | 0.47962
8247 | 0.52933
8248 | 0.59663
8249 | 0.68761
8250 | 0.77312
8251 | 0.84031
8252 | 0.82058
8253 | 0.80716
8254 | 0.77369
8255 | 0.71572
8256 | 0.64221
8257 | 0.59717
8258 | 0.53841
8259 | 0.508
8260 | 0.49619
8261 | 0.52038
8262 | 0.60103
8263 | 0.68412
8264 | 0.72009
8265 | 0.67675
8266 | 0.64758
8267 | 0.60621
8268 | 0.58521
8269 | 0.57482
8270 | 0.56385
8271 | 0.59657
8272 | 0.68139
8273 | 0.76694
8274 | 0.82496
8275 | 0.88747
8276 | 0.87177
8277 | 0.8354
8278 | 0.78909
8279 | 0.72855
8280 | 0.65213
8281 | 0.58262
8282 | 0.54103
8283 | 0.51076
8284 | 0.49539
8285 | 0.51989
8286 | 0.59802
8287 | 0.68033
8288 | 0.715
8289 | 0.67776
8290 | 0.63662
8291 | 0.59674
8292 | 0.59201
8293 | 0.60509
8294 | 0.60692
8295 | 0.62198
8296 | 0.67977
8297 | 0.75192
8298 | 0.81424
8299 | 0.86775
8300 | 0.86277
8301 | 0.8321
8302 | 0.77994
8303 | 0.71598
8304 | 0.64224
8305 | 0.5828
8306 | 0.53478
8307 | 0.50133
8308 | 0.48744
8309 | 0.50863
8310 | 0.58427
8311 | 0.66447
8312 | 0.69653
8313 | 0.6575
8314 | 0.60419
8315 | 0.55377
8316 | 0.53391
8317 | 0.53487
8318 | 0.53025
8319 | 0.56112
8320 | 0.63553
8321 | 0.72468
8322 | 0.79962
8323 | 0.85375
8324 | 0.83756
8325 | 0.80728
8326 | 0.76713
8327 | 0.71063
8328 | 0.6341
8329 | 0.56983
8330 | 0.52316
8331 | 0.49283
8332 | 0.48264
8333 | 0.50451
8334 | 0.57695
8335 | 0.65324
8336 | 0.6815
8337 | 0.64043
8338 | 0.61076
8339 | 0.56532
8340 | 0.53248
8341 | 0.52008
8342 | 0.53408
8343 | 0.55459
8344 | 0.62607
8345 | 0.702
8346 | 0.77804
8347 | 0.83401
8348 | 0.83273
8349 | 0.80365
8350 | 0.75815
8351 | 0.69433
8352 | 0.62171
8353 | 0.56003
8354 | 0.53115
8355 | 0.50299
8356 | 0.49022
8357 | 0.51379
8358 | 0.5821
8359 | 0.65878
8360 | 0.69366
8361 | 0.66538
8362 | 0.60853
8363 | 0.56699
8364 | 0.53791
8365 | 0.52392
8366 | 0.51423
8367 | 0.54446
8368 | 0.62299
8369 | 0.70207
8370 | 0.77676
8371 | 0.82679
8372 | 0.81422
8373 | 0.78623
8374 | 0.75369
8375 | 0.71264
8376 | 0.64411
8377 | 0.57269
8378 | 0.55182
8379 | 0.51849
8380 | 0.4993
8381 | 0.49899
8382 | 0.51895
8383 | 0.55213
8384 | 0.59935
8385 | 0.57263
8386 | 0.53491
8387 | 0.48915
8388 | 0.46073
8389 | 0.44661
8390 | 0.4385
8391 | 0.4659
8392 | 0.56807
8393 | 0.66613
8394 | 0.75221
8395 | 0.81214
8396 | 0.79531
8397 | 0.77681
8398 | 0.75128
8399 | 0.71223
8400 | 0.65399
8401 | 0.5941
8402 | 0.54898
8403 | 0.5164
8404 | 0.49465
8405 | 0.49368
8406 | 0.50203
8407 | 0.52112
8408 | 0.56676
8409 | 0.55774
8410 | 0.51426
8411 | 0.47392
8412 | 0.45638
8413 | 0.44978
8414 | 0.43411
8415 | 0.4815
8416 | 0.5561
8417 | 0.6658
8418 | 0.75903
8419 | 0.83313
8420 | 0.81966
8421 | 0.80433
8422 | 0.76999
8423 | 0.7067
8424 | 0.63396
8425 | 0.59284
8426 | 0.53796
8427 | 0.50989
8428 | 0.49941
8429 | 0.52173
8430 | 0.60153
8431 | 0.68448
8432 | 0.72905
8433 | 0.69472
8434 | 0.65448
8435 | 0.63248
8436 | 0.61693
8437 | 0.60942
8438 | 0.61392
8439 | 0.62862
8440 | 0.69805
8441 | 0.76815
8442 | 0.82737
8443 | 0.88995
8444 | 0.87362
8445 | 0.83633
8446 | 0.78933
8447 | 0.72595
8448 | 0.64978
8449 | 0.5821
8450 | 0.54638
8451 | 0.5176
8452 | 0.5047
8453 | 0.52726
8454 | 0.60451
8455 | 0.68602
8456 | 0.73015
8457 | 0.71447
8458 | 0.68207
8459 | 0.62052
8460 | 0.59744
8461 | 0.62556
8462 | 0.66663
8463 | 0.64013
8464 | 0.68864
8465 | 0.76402
8466 | 0.8187
8467 | 0.87795
8468 | 0.87175
8469 | 0.83954
8470 | 0.78848
8471 | 0.7222
8472 | 0.64796
8473 | 0.58836
8474 | 0.53519
8475 | 0.50418
8476 | 0.49181
8477 | 0.51289
8478 | 0.5856
8479 | 0.66458
8480 | 0.70511
8481 | 0.68153
8482 | 0.66124
8483 | 0.63881
8484 | 0.5819
8485 | 0.56975
8486 | 0.58957
8487 | 0.62151
8488 | 0.67754
8489 | 0.74283
8490 | 0.80156
8491 | 0.85411
8492 | 0.8405
8493 | 0.80727
8494 | 0.7705
8495 | 0.71064
8496 | 0.63584
8497 | 0.57157
8498 | 0.52971
8499 | 0.50142
8500 | 0.49075
8501 | 0.51474
8502 | 0.58781
8503 | 0.66402
8504 | 0.69615
8505 | 0.6543
8506 | 0.60908
8507 | 0.56238
8508 | 0.53654
8509 | 0.54932
8510 | 0.54968
8511 | 0.55827
8512 | 0.62098
8513 | 0.70692
8514 | 0.78677
8515 | 0.84631
8516 | 0.84328
8517 | 0.81327
8518 | 0.76846
8519 | 0.70538
8520 | 0.63221
8521 | 0.56697
8522 | 0.52782
8523 | 0.48952
8524 | 0.48413
8525 | 0.50692
8526 | 0.57762
8527 | 0.65001
8528 | 0.68711
8529 | 0.65366
8530 | 0.60222
8531 | 0.56575
8532 | 0.54759
8533 | 0.53478
8534 | 0.53341
8535 | 0.54215
8536 | 0.60821
8537 | 0.68808
8538 | 0.76482
8539 | 0.81315
8540 | 0.8054
8541 | 0.77398
8542 | 0.74011
8543 | 0.70061
8544 | 0.6339
8545 | 0.56388
8546 | 0.53574
8547 | 0.50255
8548 | 0.48697
8549 | 0.48918
8550 | 0.50334
8551 | 0.53351
8552 | 0.57655
8553 | 0.55656
8554 | 0.53234
8555 | 0.48217
8556 | 0.44436
8557 | 0.42412
8558 | 0.40171
8559 | 0.44105
8560 | 0.52658
8561 | 0.62751
8562 | 0.72193
8563 | 0.78744
8564 | 0.77461
8565 | 0.75685
8566 | 0.72803
8567 | 0.69242
8568 | 0.63092
8569 | 0.57754
8570 | 0.54091
8571 | 0.50831
8572 | 0.4897
8573 | 0.48923
8574 | 0.49514
8575 | 0.51215
8576 | 0.55416
8577 | 0.5513
8578 | 0.52054
8579 | 0.47186
8580 | 0.45231
8581 | 0.45135
8582 | 0.43411
8583 | 0.46281
8584 | 0.54499
8585 | 0.64834
8586 | 0.73799
8587 | 0.8216
8588 | 0.81135
8589 | 0.79716
8590 | 0.75862
8591 | 0.69747
8592 | 0.62112
8593 | 0.58229
8594 | 0.54048
8595 | 0.50905
8596 | 0.49096
8597 | 0.50198
8598 | 0.52982
8599 | 0.56299
8600 | 0.59683
8601 | 0.59239
8602 | 0.55322
8603 | 0.52722
8604 | 0.51911
8605 | 0.508
8606 | 0.52663
8607 | 0.52072
8608 | 0.59703
8609 | 0.68196
8610 | 0.76686
8611 | 0.83294
8612 | 0.81461
8613 | 0.78723
8614 | 0.75906
8615 | 0.69233
8616 | 0.62138
8617 | 0.58225
8618 | 0.52165
8619 | 0.49195
8620 | 0.48226
8621 | 0.50765
8622 | 0.57829
8623 | 0.65531
8624 | 0.69199
8625 | 0.67455
8626 | 0.66081
8627 | 0.62124
8628 | 0.59968
8629 | 0.60015
8630 | 0.61451
8631 | 0.62798
8632 | 0.66889
8633 | 0.73145
8634 | 0.7785
8635 | 0.83531
8636 | 0.83898
8637 | 0.81291
8638 | 0.75683
8639 | 0.6883
8640 | 0.61372
8641 | 0.56294
8642 | 0.51536
8643 | 0.48169
8644 | 0.47305
8645 | 0.49557
8646 | 0.56424
8647 | 0.63793
8648 | 0.67383
8649 | 0.62294
8650 | 0.57273
8651 | 0.52835
8652 | 0.52005
8653 | 0.52631
8654 | 0.52516
8655 | 0.54197
8656 | 0.59873
8657 | 0.68538
8658 | 0.76057
8659 | 0.81925
8660 | 0.81296
8661 | 0.78034
8662 | 0.73801
8663 | 0.68066
8664 | 0.60456
8665 | 0.54878
8666 | 0.50905
8667 | 0.47912
8668 | 0.4715
8669 | 0.49536
8670 | 0.56698
8671 | 0.64056
8672 | 0.6713
8673 | 0.63414
8674 | 0.59754
8675 | 0.57662
8676 | 0.56567
8677 | 0.57197
8678 | 0.57949
8679 | 0.57246
8680 | 0.61378
8681 | 0.68241
8682 | 0.75531
8683 | 0.81159
8684 | 0.81668
8685 | 0.78719
8686 | 0.74101
8687 | 0.67549
8688 | 0.60357
8689 | 0.54676
8690 | 0.51588
8691 | 0.48271
8692 | 0.46824
8693 | 0.49775
8694 | 0.56568
8695 | 0.6404
8696 | 0.67338
8697 | 0.64006
8698 | 0.6051
8699 | 0.53169
8700 | 0.49378
8701 | 0.49304
8702 | 0.48043
8703 | 0.5102
8704 | 0.58528
8705 | 0.66588
8706 | 0.73654
8707 | 0.79663
8708 | 0.78864
8709 | 0.76099
8710 | 0.72423
8711 | 0.6852
8712 | 0.61722
8713 | 0.55224
8714 | 0.53031
8715 | 0.49687
8716 | 0.48278
8717 | 0.4875
8718 | 0.50397
8719 | 0.53254
8720 | 0.58412
8721 | 0.57415
8722 | 0.55864
8723 | 0.53036
8724 | 0.49995
8725 | 0.47894
8726 | 0.47082
8727 | 0.49273
8728 | 0.55416
8729 | 0.62658
8730 | 0.71696
8731 | 0.77961
8732 | 0.77225
8733 | 0.75878
8734 | 0.72824
8735 | 0.6869
8736 | 0.62833
8737 | 0.57294
8738 | 0.5237
8739 | 0.49236
8740 | 0.47544
8741 | 0.47693
8742 | 0.48052
8743 | 0.4948
8744 | 0.53445
8745 | 0.52601
8746 | 0.4933
8747 | 0.43052
8748 | 0.39933
8749 | 0.39019
8750 | 0.36948
8751 | 0.41094
8752 | 0.50324
8753 | 0.60889
8754 | 0.70313
8755 | 0.79626
8756 | 0.78964
8757 | 0.77856
8758 | 0.7412
8759 | 0.67553
8760 | 0.60159

## flexible_params
Flexible Params | [6 empty] | Index
param | model_component | period | day | hour_of_day_from | hour_of_day_to | value
max_gen_fraction | Load_reduce | All | All | 0 | 16 | 0
max_gen_fraction | Load_reduce | All | All | 20 | 23 | 0
max_gen_fraction | Load_reduce | All | All | 16 | 20 | 1
max_gen_fraction | PV_Kupono_Battery | All | All | 0 | 7 | 1
max_gen_fraction | PV_Kupono_Battery | All | All | 17 | 23 | 0.71
energy_budget_cap_factor | FFR | None | All | None | None | 0
energy_budget_cap_factor | Hpoff | None | All | None | None | 0.7962
energy_budget_cap_factor | Waiau_3-4 | None | All | None | None | 0.08
can_produce_less_than_energy_budget | Waiau_3-4 | None | None | None | None | 1
under_freq_load_shedding_fraction | None | None | None | None | None | 0.15
total_freq_resp_violation_penalty_per_mw | None | None | None | None | None | 1000000
lf_reserve_timeframe_fraction_of_hour | None | None | None | None | None | 0.5
reg_reserve_timeframe_fraction_of_hour | None | None | None | None | None | 0
erm_shifting_window | None | None | None | None | None | 8760
synchronous_condenser_addition_to_load | Sync_Cond | None | None | None | None | 0.04
synchronous_condenser_addition_to_load | LM6000_2x1CC_Sync_Cond | None | None | None | None | 0.04
synchronous_condenser_addition_to_load | SC_6000CC_New | None | None | None | None | 0.04
allow_synchronous_condenser_mode | LM6000_2x1CC_Sync_Cond | None | None | None | None | TRUE
allow_synchronous_condenser_mode | SC_6000CC_New | None | None | None | None | TRUE
decimals | None | None | None | None | None | 2

## fuels
Fuels |  |  | Index
fuels | tco2_per_mmbtu | can_blend_with_pipeline_biogas
LSFO | 0.083063 | TRUE
Diesel | 0.081807 | TRUE
ULSD_CIP | 0.081807 | TRUE
ULSD_SGS | 0.081807 | TRUE
Biodiesel | 0 | FALSE
60.40_ULSD_SGS.LSFO | 0.082309 | TRUE
Sch_Blend | 0.081461 | TRUE
Free | 0 | FALSE
Coal | 0.097205 | FALSE

## min_cumulative_new_build
Min Cumulative New Build |  |  | Index
resource | period | min_cumulative_build_by_year
Biomass | 2025 | 0
Biomass | 2026 | 0
Biomass | 2027 | 0
Biomass | 2028 | 0
Biomass | 2029 | 0
Biomass | 2030 | 0
Biomass | 2031 | 0
Biomass | 2032 | 0
Biomass | 2033 | 0
Biomass | 2034 | 0
Biomass | 2040 | 0
Biomass | 2045 | 0
Biomass | 2050 | 0
ICE_New | 2025 | 0
ICE_New | 2026 | 0
ICE_New | 2027 | 0
ICE_New | 2028 | 0
ICE_New | 2029 | 0
ICE_New | 2030 | 0
ICE_New | 2031 | 0
ICE_New | 2032 | 0
ICE_New | 2033 | 0
ICE_New | 2034 | 0
ICE_New | 2040 | 0
ICE_New | 2045 | 0
ICE_New | 2050 | 0
LM6000_2x1CC_Sync_Cond | 2025 | 0
LM6000_2x1CC_Sync_Cond | 2026 | 0
LM6000_2x1CC_Sync_Cond | 2027 | 0
LM6000_2x1CC_Sync_Cond | 2028 | 0
LM6000_2x1CC_Sync_Cond | 2029 | 0
LM6000_2x1CC_Sync_Cond | 2030 | 0
LM6000_2x1CC_Sync_Cond | 2031 | 0
LM6000_2x1CC_Sync_Cond | 2032 | 0
LM6000_2x1CC_Sync_Cond | 2033 | 0
LM6000_2x1CC_Sync_Cond | 2034 | 0
LM6000_2x1CC_Sync_Cond | 2040 | 0
LM6000_2x1CC_Sync_Cond | 2045 | 0
LM6000_2x1CC_Sync_Cond | 2050 | 0
Sync_Cond | 2025 | 0
Sync_Cond | 2026 | 0
Sync_Cond | 2027 | 0
Sync_Cond | 2028 | 0
Sync_Cond | 2029 | 0
Sync_Cond | 2030 | 0
Sync_Cond | 2031 | 0
Sync_Cond | 2032 | 0
Sync_Cond | 2033 | 0
Sync_Cond | 2034 | 0
Sync_Cond | 2040 | 0
Sync_Cond | 2045 | 0
Sync_Cond | 2050 | 0
SC_6000CC_New | 2025 | 0
SC_6000CC_New | 2026 | 0
SC_6000CC_New | 2027 | 0
SC_6000CC_New | 2028 | 0
SC_6000CC_New | 2029 | 0
SC_6000CC_New | 2030 | 0
SC_6000CC_New | 2031 | 0
SC_6000CC_New | 2032 | 0
SC_6000CC_New | 2033 | 0
SC_6000CC_New | 2034 | 0
SC_6000CC_New | 2040 | 0
SC_6000CC_New | 2045 | 0
SC_6000CC_New | 2050 | 0
Solar_Grid-Scale_Single-Tracking_New | 2025 | 0
Solar_Grid-Scale_Single-Tracking_New | 2026 | 0
Solar_Grid-Scale_Single-Tracking_New | 2027 | 0
Solar_Grid-Scale_Single-Tracking_New | 2028 | 0
Solar_Grid-Scale_Single-Tracking_New | 2029 | 0
Solar_Grid-Scale_Single-Tracking_New | 2030 | 0
Solar_Grid-Scale_Single-Tracking_New | 2031 | 0
Solar_Grid-Scale_Single-Tracking_New | 2032 | 0
Solar_Grid-Scale_Single-Tracking_New | 2033 | 0
Solar_Grid-Scale_Single-Tracking_New | 2034 | 0
Solar_Grid-Scale_Single-Tracking_New | 2040 | 0
Solar_Grid-Scale_Single-Tracking_New | 2045 | 0
Solar_Grid-Scale_Single-Tracking_New | 2050 | 0
Wind_Onshore_New | 2025 | 0
Wind_Onshore_New | 2026 | 0
Wind_Onshore_New | 2027 | 0
Wind_Onshore_New | 2028 | 0
Wind_Onshore_New | 2029 | 0
Wind_Onshore_New | 2030 | 0
Wind_Onshore_New | 2031 | 0
Wind_Onshore_New | 2032 | 0
Wind_Onshore_New | 2033 | 0
Wind_Onshore_New | 2034 | 0
Wind_Onshore_New | 2040 | 0
Wind_Onshore_New | 2045 | 0
Wind_Onshore_New | 2050 | 0
Wind_Offshore_New | 2025 | 0
Wind_Offshore_New | 2026 | 0
Wind_Offshore_New | 2027 | 0
Wind_Offshore_New | 2028 | 0
Wind_Offshore_New | 2029 | 0
Wind_Offshore_New | 2030 | 0
Wind_Offshore_New | 2031 | 0
Wind_Offshore_New | 2032 | 0
Wind_Offshore_New | 2033 | 0
Wind_Offshore_New | 2034 | 0
Wind_Offshore_New | 2040 | 0
Wind_Offshore_New | 2045 | 0
Wind_Offshore_New | 2050 | 0
PV_Paired_Grid_4hr_New_Supply | 2025 | 0
PV_Paired_Grid_4hr_New_Supply | 2026 | 0
PV_Paired_Grid_4hr_New_Supply | 2027 | 0
PV_Paired_Grid_4hr_New_Supply | 2028 | 0
PV_Paired_Grid_4hr_New_Supply | 2029 | 0
PV_Paired_Grid_4hr_New_Supply | 2030 | 0
PV_Paired_Grid_4hr_New_Supply | 2031 | 0
PV_Paired_Grid_4hr_New_Supply | 2032 | 0
PV_Paired_Grid_4hr_New_Supply | 2033 | 0
PV_Paired_Grid_4hr_New_Supply | 2034 | 0
PV_Paired_Grid_4hr_New_Supply | 2040 | 0
PV_Paired_Grid_4hr_New_Supply | 2045 | 0
PV_Paired_Grid_4hr_New_Supply | 2050 | 0
PV_Paired_Grid_6hr_New_Supply | 2025 | 0
PV_Paired_Grid_6hr_New_Supply | 2026 | 0
PV_Paired_Grid_6hr_New_Supply | 2027 | 0
PV_Paired_Grid_6hr_New_Supply | 2028 | 0
PV_Paired_Grid_6hr_New_Supply | 2029 | 0
PV_Paired_Grid_6hr_New_Supply | 2030 | 0
PV_Paired_Grid_6hr_New_Supply | 2031 | 0
PV_Paired_Grid_6hr_New_Supply | 2032 | 0
PV_Paired_Grid_6hr_New_Supply | 2033 | 0
PV_Paired_Grid_6hr_New_Supply | 2034 | 0
PV_Paired_Grid_6hr_New_Supply | 2040 | 0
PV_Paired_Grid_6hr_New_Supply | 2045 | 0
PV_Paired_Grid_6hr_New_Supply | 2050 | 0
PV_Aggregated_DER_Supply | 2025 | 0
PV_Aggregated_DER_Supply | 2026 | 0
PV_Aggregated_DER_Supply | 2027 | 0
PV_Aggregated_DER_Supply | 2028 | 0
PV_Aggregated_DER_Supply | 2029 | 0
PV_Aggregated_DER_Supply | 2030 | 0
PV_Aggregated_DER_Supply | 2031 | 0
PV_Aggregated_DER_Supply | 2032 | 0
PV_Aggregated_DER_Supply | 2033 | 0
PV_Aggregated_DER_Supply | 2034 | 0
PV_Aggregated_DER_Supply | 2040 | 0
PV_Aggregated_DER_Supply | 2045 | 0
PV_Aggregated_DER_Supply | 2050 | 0
PV_Paired_LowCF_4hr_New_Supply | 2025 | 0
PV_Paired_LowCF_4hr_New_Supply | 2026 | 0
PV_Paired_LowCF_4hr_New_Supply | 2027 | 0
PV_Paired_LowCF_4hr_New_Supply | 2028 | 0
PV_Paired_LowCF_4hr_New_Supply | 2029 | 0
PV_Paired_LowCF_4hr_New_Supply | 2030 | 0
PV_Paired_LowCF_4hr_New_Supply | 2031 | 0
PV_Paired_LowCF_4hr_New_Supply | 2032 | 0
PV_Paired_LowCF_4hr_New_Supply | 2033 | 0
PV_Paired_LowCF_4hr_New_Supply | 2034 | 0
PV_Paired_LowCF_4hr_New_Supply | 2040 | 0
PV_Paired_LowCF_4hr_New_Supply | 2045 | 0
PV_Paired_LowCF_4hr_New_Supply | 2050 | 0
PV_Paired_LowCF_6hr_New_Supply | 2025 | 0
PV_Paired_LowCF_6hr_New_Supply | 2026 | 0
PV_Paired_LowCF_6hr_New_Supply | 2027 | 0
PV_Paired_LowCF_6hr_New_Supply | 2028 | 0
PV_Paired_LowCF_6hr_New_Supply | 2029 | 0
PV_Paired_LowCF_6hr_New_Supply | 2030 | 0
PV_Paired_LowCF_6hr_New_Supply | 2031 | 0
PV_Paired_LowCF_6hr_New_Supply | 2032 | 0
PV_Paired_LowCF_6hr_New_Supply | 2033 | 0
PV_Paired_LowCF_6hr_New_Supply | 2034 | 0
PV_Paired_LowCF_6hr_New_Supply | 2040 | 0
PV_Paired_LowCF_6hr_New_Supply | 2045 | 0
PV_Paired_LowCF_6hr_New_Supply | 2050 | 0
Battery_Grid-Scale_New | 2025 | 0
Battery_Grid-Scale_New | 2026 | 0
Battery_Grid-Scale_New | 2027 | 0
Battery_Grid-Scale_New | 2028 | 0
Battery_Grid-Scale_New | 2029 | 0
Battery_Grid-Scale_New | 2030 | 0
Battery_Grid-Scale_New | 2031 | 0
Battery_Grid-Scale_New | 2032 | 0
Battery_Grid-Scale_New | 2033 | 0
Battery_Grid-Scale_New | 2034 | 0
Battery_Grid-Scale_New | 2040 | 0
Battery_Grid-Scale_New | 2045 | 0
Battery_Grid-Scale_New | 2050 | 0
PV_Paired_Grid_4hr_New_Battery | 2025 | 0
PV_Paired_Grid_4hr_New_Battery | 2026 | 0
PV_Paired_Grid_4hr_New_Battery | 2027 | 0
PV_Paired_Grid_4hr_New_Battery | 2028 | 0
PV_Paired_Grid_4hr_New_Battery | 2029 | 0
PV_Paired_Grid_4hr_New_Battery | 2030 | 0
PV_Paired_Grid_4hr_New_Battery | 2031 | 0
PV_Paired_Grid_4hr_New_Battery | 2032 | 0
PV_Paired_Grid_4hr_New_Battery | 2033 | 0
PV_Paired_Grid_4hr_New_Battery | 2034 | 0
PV_Paired_Grid_4hr_New_Battery | 2040 | 0
PV_Paired_Grid_4hr_New_Battery | 2045 | 0
PV_Paired_Grid_4hr_New_Battery | 2050 | 0
PV_Paired_Grid_6hr_New_Battery | 2025 | 0
PV_Paired_Grid_6hr_New_Battery | 2026 | 0
PV_Paired_Grid_6hr_New_Battery | 2027 | 0
PV_Paired_Grid_6hr_New_Battery | 2028 | 0
PV_Paired_Grid_6hr_New_Battery | 2029 | 0
PV_Paired_Grid_6hr_New_Battery | 2030 | 0
PV_Paired_Grid_6hr_New_Battery | 2031 | 0
PV_Paired_Grid_6hr_New_Battery | 2032 | 0
PV_Paired_Grid_6hr_New_Battery | 2033 | 0
PV_Paired_Grid_6hr_New_Battery | 2034 | 0
PV_Paired_Grid_6hr_New_Battery | 2040 | 0
PV_Paired_Grid_6hr_New_Battery | 2045 | 0
PV_Paired_Grid_6hr_New_Battery | 2050 | 0
PV_Aggregated_DER_Battery | 2025 | 0
PV_Aggregated_DER_Battery | 2026 | 0
PV_Aggregated_DER_Battery | 2027 | 0
PV_Aggregated_DER_Battery | 2028 | 0
PV_Aggregated_DER_Battery | 2029 | 0
PV_Aggregated_DER_Battery | 2030 | 0
PV_Aggregated_DER_Battery | 2031 | 0
PV_Aggregated_DER_Battery | 2032 | 0
PV_Aggregated_DER_Battery | 2033 | 0
PV_Aggregated_DER_Battery | 2034 | 0
PV_Aggregated_DER_Battery | 2040 | 0
PV_Aggregated_DER_Battery | 2045 | 0
PV_Aggregated_DER_Battery | 2050 | 0
PV_Paired_LowCF_4hr_New_Battery | 2025 | 0
PV_Paired_LowCF_4hr_New_Battery | 2026 | 0
PV_Paired_LowCF_4hr_New_Battery | 2027 | 0
PV_Paired_LowCF_4hr_New_Battery | 2028 | 0
PV_Paired_LowCF_4hr_New_Battery | 2029 | 0
PV_Paired_LowCF_4hr_New_Battery | 2030 | 0
PV_Paired_LowCF_4hr_New_Battery | 2031 | 0
PV_Paired_LowCF_4hr_New_Battery | 2032 | 0
PV_Paired_LowCF_4hr_New_Battery | 2033 | 0
PV_Paired_LowCF_4hr_New_Battery | 2034 | 0
PV_Paired_LowCF_4hr_New_Battery | 2040 | 0
PV_Paired_LowCF_4hr_New_Battery | 2045 | 0
PV_Paired_LowCF_4hr_New_Battery | 2050 | 0
PV_Paired_LowCF_6hr_New_Battery | 2025 | 0
PV_Paired_LowCF_6hr_New_Battery | 2026 | 0
PV_Paired_LowCF_6hr_New_Battery | 2027 | 0
PV_Paired_LowCF_6hr_New_Battery | 2028 | 0
PV_Paired_LowCF_6hr_New_Battery | 2029 | 0
PV_Paired_LowCF_6hr_New_Battery | 2030 | 0
PV_Paired_LowCF_6hr_New_Battery | 2031 | 0
PV_Paired_LowCF_6hr_New_Battery | 2032 | 0
PV_Paired_LowCF_6hr_New_Battery | 2033 | 0
PV_Paired_LowCF_6hr_New_Battery | 2034 | 0
PV_Paired_LowCF_6hr_New_Battery | 2040 | 0
PV_Paired_LowCF_6hr_New_Battery | 2045 | 0
PV_Paired_LowCF_6hr_New_Battery | 2050 | 0

## period_discount_factors
Period Discount Factors |  |  | Index
period | discount_factor | years_in_period
2025 | 0.64849 | 1
2026 | 0.61802 | 1
2027 | 0.58898 | 1
2028 | 0.56131 | 1
2029 | 0.53494 | 1
2030 | 0.50981 | 1
2031 | 0.48585 | 1
2032 | 0.46303 | 1
2033 | 0.44127 | 1
2034 | 1.3619 | 3.5
2040 | 1.7709 | 5.5
2045 | 1.2442 | 5
2050 | 3.0651 | 23

## planned_installed_capacities
Planned Installed Capacities |  |  |  |  | Index
resource | period | planned_installed_capacity | min_operational_planned_capacity_mw | planned_capacity_fixed_o_and_m_dollars_per_kw_yr
FFR | 2025 | 26.742 | 0 | 85.8322
FFR | 2026 | 0 | 0 | 0
FFR | 2027 | 0 | 0 | 0
FFR | 2028 | 0 | 0 | 0
FFR | 2029 | 0 | 0 | 0
FFR | 2030 | 0 | 0 | 0
FFR | 2031 | 0 | 0 | 0
FFR | 2032 | 0 | 0 | 0
FFR | 2033 | 0 | 0 | 0
FFR | 2034 | 0 | 0 | 0
FFR | 2040 | 0 | 0 | 0
FFR | 2045 | 0 | 0 | 0
FFR | 2050 | 0 | 0 | 0
Airport_DSG | 2025 | 8 | 0 | 0
Airport_DSG | 2026 | 8 | 0 | 0
Airport_DSG | 2027 | 8 | 0 | 0
Airport_DSG | 2028 | 8 | 0 | 0
Airport_DSG | 2029 | 8 | 0 | 0
Airport_DSG | 2030 | 8 | 0 | 0
Airport_DSG | 2031 | 8 | 0 | 0
Airport_DSG | 2032 | 8 | 0 | 0
Airport_DSG | 2033 | 8 | 0 | 0
Airport_DSG | 2034 | 8 | 0 | 0
Airport_DSG | 2040 | 8 | 0 | 0
Airport_DSG | 2045 | 8 | 0 | 0
Airport_DSG | 2050 | 8 | 0 | 0
Biomass | 2025 | 0 | 0 | 148.1217
Biomass | 2026 | 0 | 0 | 148.1217
Biomass | 2027 | 0 | 0 | 148.1217
Biomass | 2028 | 0 | 0 | 148.1217
Biomass | 2029 | 0 | 0 | 148.1217
Biomass | 2030 | 0 | 0 | 148.1217
Biomass | 2031 | 0 | 0 | 148.1217
Biomass | 2032 | 0 | 0 | 148.1217
Biomass | 2033 | 0 | 0 | 148.1217
Biomass | 2034 | 0 | 0 | 148.1217
Biomass | 2040 | 0 | 0 | 148.1217
Biomass | 2045 | 0 | 0 | 148.1217
Biomass | 2050 | 0 | 0 | 148.1217
CIP_BioD | 2025 | 0 | 0 | 1.3773
CIP_BioD | 2026 | 0 | 0 | 1.3773
CIP_BioD | 2027 | 0 | 0 | 1.3773
CIP_BioD | 2028 | 0 | 0 | 1.3773
CIP_BioD | 2029 | 0 | 0 | 1.3773
CIP_BioD | 2030 | 0 | 0 | 1.3773
CIP_BioD | 2031 | 0 | 0 | 1.3773
CIP_BioD | 2032 | 0 | 0 | 1.3773
CIP_BioD | 2033 | 0 | 0 | 1.3773
CIP_BioD | 2034 | 0 | 0 | 1.3773
CIP_BioD | 2040 | 0 | 0 | 1.3773
CIP_BioD | 2045 | 129 | 0 | 1.3773
CIP_BioD | 2050 | 129 | 0 | 1.3773
Hpoff | 2025 | 68.5 | 0 | 204.9264
Hpoff | 2026 | 68.5 | 0 | 204.9264
Hpoff | 2027 | 68.5 | 0 | 204.9264
Hpoff | 2028 | 68.5 | 0 | 204.9264
Hpoff | 2029 | 68.5 | 0 | 204.9264
Hpoff | 2030 | 68.5 | 0 | 204.9264
Hpoff | 2031 | 68.5 | 0 | 204.9264
Hpoff | 2032 | 68.5 | 0 | 204.9264
Hpoff | 2033 | 68.5 | 0 | 204.9264
Hpoff | 2034 | 68.5 | 0 | 204.9264
Hpoff | 2040 | 68.5 | 0 | 204.9264
Hpoff | 2045 | 68.5 | 0 | 204.9264
Hpoff | 2050 | 68.5 | 0 | 204.9264
Kala1_Biod | 2025 | 0 | 0 | 0
Kala1_Biod | 2026 | 0 | 0 | 0
Kala1_Biod | 2027 | 0 | 0 | 0
Kala1_Biod | 2028 | 0 | 0 | 0
Kala1_Biod | 2029 | 0 | 0 | 0
Kala1_Biod | 2030 | 0 | 0 | 0
Kala1_Biod | 2031 | 0 | 0 | 0
Kala1_Biod | 2032 | 0 | 0 | 0
Kala1_Biod | 2033 | 0 | 0 | 0
Kala1_Biod | 2034 | 0 | 0 | 0
Kala1_Biod | 2040 | 0 | 0 | 0
Kala1_Biod | 2045 | 90 | 0 | 104.7304
Kala1_Biod | 2050 | 90 | 0 | 104.7304
Kala2_Biod | 2025 | 0 | 0 | 0
Kala2_Biod | 2026 | 0 | 0 | 0
Kala2_Biod | 2027 | 0 | 0 | 0
Kala2_Biod | 2028 | 0 | 0 | 0
Kala2_Biod | 2029 | 0 | 0 | 0
Kala2_Biod | 2030 | 0 | 0 | 0
Kala2_Biod | 2031 | 0 | 0 | 0
Kala2_Biod | 2032 | 0 | 0 | 0
Kala2_Biod | 2033 | 0 | 0 | 0
Kala2_Biod | 2034 | 0 | 0 | 0
Kala2_Biod | 2040 | 0 | 0 | 0
Kala2_Biod | 2045 | 118 | 0 | 104.7304
Kala2_Biod | 2050 | 118 | 0 | 104.7304
Schofield | 2025 | 48.84 | 0 | 39.0121
Schofield | 2026 | 48.84 | 0 | 39.0121
Schofield | 2027 | 48.84 | 0 | 39.0121
Schofield | 2028 | 48.84 | 0 | 39.0121
Schofield | 2029 | 48.84 | 0 | 39.0121
Schofield | 2030 | 48.84 | 0 | 39.0121
Schofield | 2031 | 48.84 | 0 | 39.0121
Schofield | 2032 | 48.84 | 0 | 39.0121
Schofield | 2033 | 48.84 | 0 | 39.0121
Schofield | 2034 | 48.84 | 0 | 39.0121
Schofield | 2040 | 48.84 | 0 | 39.0121
Schofield | 2045 | 0 | 0 | 39.0121
Schofield | 2050 | 0 | 0 | 39.0121
Schofield_Biod | 2025 | 0 | 0 | 39.0121
Schofield_Biod | 2026 | 0 | 0 | 39.0121
Schofield_Biod | 2027 | 0 | 0 | 39.0121
Schofield_Biod | 2028 | 0 | 0 | 39.0121
Schofield_Biod | 2029 | 0 | 0 | 39.0121
Schofield_Biod | 2030 | 0 | 0 | 39.0121
Schofield_Biod | 2031 | 0 | 0 | 39.0121
Schofield_Biod | 2032 | 0 | 0 | 39.0121
Schofield_Biod | 2033 | 0 | 0 | 39.0121
Schofield_Biod | 2034 | 0 | 0 | 39.0121
Schofield_Biod | 2040 | 0 | 0 | 39.0121
Schofield_Biod | 2045 | 48.84 | 0 | 39.0121
Schofield_Biod | 2050 | 48.84 | 0 | 39.0121
AES | 2025 | 0 | 0 | 0
AES | 2026 | 0 | 0 | 0
AES | 2027 | 0 | 0 | 0
AES | 2028 | 0 | 0 | 0
AES | 2029 | 0 | 0 | 0
AES | 2030 | 0 | 0 | 0
AES | 2031 | 0 | 0 | 0
AES | 2032 | 0 | 0 | 0
AES | 2033 | 0 | 0 | 0
AES | 2034 | 0 | 0 | 0
AES | 2040 | 0 | 0 | 0
AES | 2045 | 0 | 0 | 0
AES | 2050 | 0 | 0 | 0
CIP_Diesel | 2025 | 129 | 0 | 1.3773
CIP_Diesel | 2026 | 129 | 0 | 1.3773
CIP_Diesel | 2027 | 129 | 0 | 1.3773
CIP_Diesel | 2028 | 129 | 0 | 1.3773
CIP_Diesel | 2029 | 129 | 0 | 1.3773
CIP_Diesel | 2030 | 129 | 0 | 1.3773
CIP_Diesel | 2031 | 129 | 0 | 1.3773
CIP_Diesel | 2032 | 129 | 0 | 1.3773
CIP_Diesel | 2033 | 129 | 0 | 1.3773
CIP_Diesel | 2034 | 129 | 0 | 1.3773
CIP_Diesel | 2040 | 129 | 0 | 1.3773
CIP_Diesel | 2045 | 0 | 0 | 1.3773
CIP_Diesel | 2050 | 0 | 0 | 1.3773
ICE_New | 2025 | 0 | 0 | 39.0121
ICE_New | 2026 | 0 | 0 | 39.0121
ICE_New | 2027 | 0 | 0 | 39.0121
ICE_New | 2028 | 0 | 0 | 39.0121
ICE_New | 2029 | 0 | 0 | 39.0121
ICE_New | 2030 | 0 | 0 | 39.0121
ICE_New | 2031 | 0 | 0 | 39.0121
ICE_New | 2032 | 0 | 0 | 39.0121
ICE_New | 2033 | 0 | 0 | 39.0121
ICE_New | 2034 | 0 | 0 | 39.0121
ICE_New | 2040 | 0 | 0 | 39.0121
ICE_New | 2045 | 0 | 0 | 39.0121
ICE_New | 2050 | 0 | 0 | 39.0121
Kahe_5-6 | 2025 | 269.511 | 0 | 5.3687
Kahe_5-6 | 2026 | 269.511 | 0 | 32.3151
Kahe_5-6 | 2027 | 269.511 | 0 | 20.8371
Kahe_5-6 | 2028 | 269.511 | 0 | 47.7242
Kahe_5-6 | 2029 | 269.511 | 0 | 34.0973
Kahe_5-6 | 2030 | 269.511 | 0 | 32.927
Kahe_5-6 | 2031 | 269.511 | 0 | 31.8041
Kahe_5-6 | 2032 | 269.511 | 0 | 37.7056
Kahe_5-6 | 2033 | 269.511 | 0 | 30.5944
Kahe_5-6 | 2034 | 269.511 | 0 | 32.6743
Kahe_5-6 | 2040 | 269.511 | 0 | 56.9513
Kahe_5-6 | 2045 | 269.511 | 0 | 53.5965
Kahe_5-6 | 2050 | 269.511 | 0 | 37.5796
Kala1 | 2025 | 90 | 0 | 104.7304
Kala1 | 2026 | 90 | 0 | 104.7304
Kala1 | 2027 | 90 | 0 | 104.7304
Kala1 | 2028 | 90 | 0 | 104.7304
Kala1 | 2029 | 90 | 0 | 104.7304
Kala1 | 2030 | 90 | 0 | 104.7304
Kala1 | 2031 | 90 | 0 | 104.7304
Kala1 | 2032 | 90 | 0 | 104.7304
Kala1 | 2033 | 90 | 0 | 104.7304
Kala1 | 2034 | 90 | 0 | 104.7304
Kala1 | 2040 | 90 | 0 | 104.7304
Kala1 | 2045 | 0 | 0 | 0
Kala1 | 2050 | 0 | 0 | 0
Kala2 | 2025 | 118 | 0 | 104.7304
Kala2 | 2026 | 118 | 0 | 104.7304
Kala2 | 2027 | 118 | 0 | 104.7304
Kala2 | 2028 | 118 | 0 | 104.7304
Kala2 | 2029 | 118 | 0 | 104.7304
Kala2 | 2030 | 118 | 0 | 104.7304
Kala2 | 2031 | 118 | 0 | 104.7304
Kala2 | 2032 | 118 | 0 | 104.7304
Kala2 | 2033 | 118 | 0 | 104.7304
Kala2 | 2034 | 118 | 0 | 104.7304
Kala2 | 2040 | 118 | 0 | 104.7304
Kala2 | 2045 | 0 | 0 | 0
Kala2 | 2050 | 0 | 0 | 0
LM6000_2x1CC_Sync_Cond | 2025 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2026 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2027 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2028 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2029 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2030 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2031 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2032 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2033 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2034 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2040 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2045 | 0 | 0 | 14.0684
LM6000_2x1CC_Sync_Cond | 2050 | 0 | 0 | 14.0684
Sync_Cond | 2025 | 0 | 0 | 0
Sync_Cond | 2026 | 0 | 0 | 0
Sync_Cond | 2027 | 0 | 0 | 0
Sync_Cond | 2028 | 0 | 0 | 0
Sync_Cond | 2029 | 0 | 0 | 0
Sync_Cond | 2030 | 0 | 0 | 0
Sync_Cond | 2031 | 0 | 0 | 0
Sync_Cond | 2032 | 0 | 0 | 0
Sync_Cond | 2033 | 0 | 0 | 0
Sync_Cond | 2034 | 0 | 0 | 0
Sync_Cond | 2040 | 0 | 0 | 0
Sync_Cond | 2045 | 0 | 0 | 0
Sync_Cond | 2050 | 0 | 0 | 0
Waiau_3-4 | 2025 | 93.584 | 0 | 39.4768
Waiau_3-4 | 2026 | 93.584 | 0 | 47.5307
Waiau_3-4 | 2027 | 93.584 | 0 | 68.9239
Waiau_3-4 | 2028 | 93.584 | 0 | 39.8809
Waiau_3-4 | 2029 | 93.584 | 0 | 38.5598
Waiau_3-4 | 2030 | 93.584 | 0 | 47.0756
Waiau_3-4 | 2031 | 93.584 | 0 | 48.6896
Waiau_3-4 | 2032 | 93.584 | 0 | 44.3045
Waiau_3-4 | 2033 | 93.584 | 0 | 46.0678
Waiau_3-4 | 2034 | 93.584 | 0 | 48.083
Waiau_3-4 | 2040 | 93.584 | 0 | 38.0491
Waiau_3-4 | 2045 | 93.584 | 0 | 32.2497
Waiau_3-4 | 2050 | 93.584 | 0 | 29.116
Waiau_5-6 | 2025 | 108.059 | 0 | 53.5785
Waiau_5-6 | 2026 | 108.059 | 0 | 46.243
Waiau_5-6 | 2027 | 108.059 | 0 | 44.8271
Waiau_5-6 | 2028 | 108.059 | 0 | 43.4684
Waiau_5-6 | 2029 | 108.059 | 0 | 44.9285
Waiau_5-6 | 2030 | 108.059 | 0 | 63.6516
Waiau_5-6 | 2031 | 108.059 | 0 | 73.9069
Waiau_5-6 | 2032 | 108.059 | 0 | 95.4717
Waiau_5-6 | 2033 | 108.059 | 0 | 74.8867
Waiau_5-6 | 2034 | 108.059 | 0 | 68.8734
Waiau_5-6 | 2040 | 108.059 | 0 | 90.8356
Waiau_5-6 | 2045 | 108.059 | 0 | 53.4446
Waiau_5-6 | 2050 | 108.059 | 0 | 42.1186
Waiau_9-10 | 2025 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2026 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2027 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2028 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2029 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2030 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2031 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2032 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2033 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2034 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2040 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2045 | 102.8 | 0 | 2.0483
Waiau_9-10 | 2050 | 102.8 | 0 | 2.0483
SC_6000CC_New | 2025 | 0 | 0 | 16.2932
SC_6000CC_New | 2026 | 0 | 0 | 16.2932
SC_6000CC_New | 2027 | 0 | 0 | 16.2932
SC_6000CC_New | 2028 | 0 | 0 | 16.2932
SC_6000CC_New | 2029 | 0 | 0 | 16.2932
SC_6000CC_New | 2030 | 0 | 0 | 16.2932
SC_6000CC_New | 2031 | 0 | 0 | 16.2932
SC_6000CC_New | 2032 | 0 | 0 | 16.2932
SC_6000CC_New | 2033 | 0 | 0 | 16.2932
SC_6000CC_New | 2034 | 0 | 0 | 16.2932
SC_6000CC_New | 2040 | 0 | 0 | 16.2932
SC_6000CC_New | 2045 | 0 | 0 | 16.2932
SC_6000CC_New | 2050 | 0 | 0 | 16.2932
K14_W78 | 2025 | 505.549 | 0 | 37.1949
K14_W78 | 2026 | 505.549 | 0 | 40.7877
K14_W78 | 2027 | 505.549 | 0 | 41.7486
K14_W78 | 2028 | 505.549 | 0 | 40.6332
K14_W78 | 2029 | 505.549 | 0 | 63.9498
K14_W78 | 2030 | 505.549 | 0 | 71.797
K14_W78 | 2031 | 505.549 | 0 | 55.7448
K14_W78 | 2032 | 505.549 | 0 | 54.232
K14_W78 | 2033 | 505.549 | 0 | 53.4872
K14_W78 | 2034 | 505.549 | 0 | 77.8178
K14_W78 | 2040 | 505.549 | 0 | 62.8178
K14_W78 | 2045 | 505.549 | 0 | 59.949
K14_W78 | 2050 | 505.549 | 0 | 49.5852
Solar_CBRE | 2025 | 5 | 0 | 296.6378
Solar_CBRE | 2026 | 5 | 0 | 296.6378
Solar_CBRE | 2027 | 5 | 0 | 296.6378
Solar_CBRE | 2028 | 5 | 0 | 296.6378
Solar_CBRE | 2029 | 5 | 0 | 296.6378
Solar_CBRE | 2030 | 5 | 0 | 296.6378
Solar_CBRE | 2031 | 5 | 0 | 296.6378
Solar_CBRE | 2032 | 5 | 0 | 296.6378
Solar_CBRE | 2033 | 5 | 0 | 296.6378
Solar_CBRE | 2034 | 5 | 0 | 296.6378
Solar_CBRE | 2040 | 5 | 0 | 296.6378
Solar_CBRE | 2045 | 5 | 0 | 296.6378
Solar_CBRE | 2050 | 5 | 0 | 296.6378
Solar_Planned | 2025 | 185.431 | 0 | 926.3075
Solar_Planned | 2026 | 185.431 | 0 | 926.3075
Solar_Planned | 2027 | 185.431 | 0 | 926.3075
Solar_Planned | 2028 | 185.431 | 0 | 926.3075
Solar_Planned | 2029 | 185.431 | 0 | 926.3075
Solar_Planned | 2030 | 185.431 | 0 | 926.3075
Solar_Planned | 2031 | 185.431 | 0 | 926.3075
Solar_Planned | 2032 | 184.431 | 0 | 928.4385
Solar_Planned | 2033 | 179.431 | 0 | 940.3734
Solar_Planned | 2034 | 174.431 | 0 | 953.3647
Solar_Planned | 2040 | 174.431 | 0 | 152.8636
Solar_Planned | 2045 | 44.831 | 0 | 582.9089
Solar_Planned | 2050 | 44.831 | 0 | 582.9089
Solar_Grid-Scale_Single-Tracking_New | 2025 | 0 | 0 | 13.1616
Solar_Grid-Scale_Single-Tracking_New | 2026 | 0 | 0 | 12.9405
Solar_Grid-Scale_Single-Tracking_New | 2027 | 0 | 0 | 12.7194
Solar_Grid-Scale_Single-Tracking_New | 2028 | 0 | 0 | 12.5113
Solar_Grid-Scale_Single-Tracking_New | 2029 | 0 | 0 | 12.3032
Solar_Grid-Scale_Single-Tracking_New | 2030 | 0 | 0 | 12.1081
Solar_Grid-Scale_Single-Tracking_New | 2031 | 0 | 0 | 11.926
Solar_Grid-Scale_Single-Tracking_New | 2032 | 0 | 0 | 11.744
Solar_Grid-Scale_Single-Tracking_New | 2033 | 0 | 0 | 11.5749
Solar_Grid-Scale_Single-Tracking_New | 2034 | 0 | 0 | 11.3928
Solar_Grid-Scale_Single-Tracking_New | 2040 | 0 | 0 | 10.4824
Solar_Grid-Scale_Single-Tracking_New | 2045 | 0 | 0 | 9.8842
Solar_Grid-Scale_Single-Tracking_New | 2050 | 0 | 0 | 9.39
Wind_NPM | 2025 | 24 | 0 | 362.2275
Wind_NPM | 2026 | 24 | 0 | 362.2275
Wind_NPM | 2027 | 24 | 0 | 362.2275
Wind_NPM | 2028 | 24 | 0 | 362.2275
Wind_NPM | 2029 | 24 | 0 | 362.2275
Wind_NPM | 2030 | 24 | 0 | 362.2275
Wind_NPM | 2031 | 24 | 0 | 362.2275
Wind_NPM | 2032 | 24 | 0 | 362.2275
Wind_NPM | 2033 | 24 | 0 | 362.2275
Wind_NPM | 2034 | 24 | 0 | 362.2275
Wind_NPM | 2040 | 0 | 0 | 362.2275
Wind_NPM | 2045 | 0 | 0 | 362.2275
Wind_NPM | 2050 | 0 | 0 | 362.2275
Wind_Onshore_Planned | 2025 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2026 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2027 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2028 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2029 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2030 | 99 | 0 | 1040.9751
Wind_Onshore_Planned | 2031 | 69 | 0 | 1060.9151
Wind_Onshore_Planned | 2032 | 69 | 0 | 1060.9151
Wind_Onshore_Planned | 2033 | 69 | 0 | 1060.9151
Wind_Onshore_Planned | 2034 | 69 | 0 | 1060.9151
Wind_Onshore_Planned | 2040 | 0 | 0 | 0
Wind_Onshore_Planned | 2045 | 0 | 0 | 0
Wind_Onshore_Planned | 2050 | 0 | 0 | 0
Wind_Offshore_Planned | 2025 | 0 | 0 | 0
Wind_Offshore_Planned | 2026 | 0 | 0 | 0
Wind_Offshore_Planned | 2027 | 0 | 0 | 0
Wind_Offshore_Planned | 2028 | 0 | 0 | 0
Wind_Offshore_Planned | 2029 | 0 | 0 | 0
Wind_Offshore_Planned | 2030 | 0 | 0 | 0
Wind_Offshore_Planned | 2031 | 0 | 0 | 0
Wind_Offshore_Planned | 2032 | 0 | 0 | 0
Wind_Offshore_Planned | 2033 | 0 | 0 | 0
Wind_Offshore_Planned | 2034 | 0 | 0 | 0
Wind_Offshore_Planned | 2040 | 0 | 0 | 0
Wind_Offshore_Planned | 2045 | 0 | 0 | 0
Wind_Offshore_Planned | 2050 | 0 | 0 | 0
Wind_Onshore_New | 2025 | 0 | 0 | 37.7983
Wind_Onshore_New | 2026 | 0 | 0 | 37.1501
Wind_Onshore_New | 2027 | 0 | 0 | 36.6163
Wind_Onshore_New | 2028 | 0 | 0 | 36.1715
Wind_Onshore_New | 2029 | 0 | 0 | 35.7902
Wind_Onshore_New | 2030 | 0 | 0 | 35.4725
Wind_Onshore_New | 2031 | 0 | 0 | 35.2056
Wind_Onshore_New | 2032 | 0 | 0 | 34.9768
Wind_Onshore_New | 2033 | 0 | 0 | 34.7861
Wind_Onshore_New | 2034 | 0 | 0 | 34.6336
Wind_Onshore_New | 2040 | 0 | 0 | 34.0617
Wind_Onshore_New | 2045 | 0 | 0 | 33.8838
Wind_Onshore_New | 2050 | 0 | 0 | 33.7948
Wind_Offshore_New | 2025 | 0 | 0 | 72.0536
Wind_Offshore_New | 2026 | 0 | 0 | 67.8117
Wind_Offshore_New | 2027 | 0 | 0 | 68.9291
Wind_Offshore_New | 2028 | 0 | 0 | 60.5523
Wind_Offshore_New | 2029 | 0 | 0 | 57.5347
Wind_Offshore_New | 2030 | 0 | 0 | 54.9253
Wind_Offshore_New | 2031 | 0 | 0 | 52.724
Wind_Offshore_New | 2032 | 0 | 0 | 49.4209
Wind_Offshore_New | 2033 | 0 | 0 | 48.0291
Wind_Offshore_New | 2034 | 0 | 0 | 46.6766
Wind_Offshore_New | 2040 | 0 | 0 | 39.3247
Wind_Offshore_New | 2045 | 0 | 0 | 34.0908
Wind_Offshore_New | 2050 | 0 | 0 | 29.5535
Solar_Waianae | 2025 | 27.6 | 0 | 306.5499
Solar_Waianae | 2026 | 27.6 | 0 | 306.5499
Solar_Waianae | 2027 | 27.6 | 0 | 306.5499
Solar_Waianae | 2028 | 27.6 | 0 | 306.5499
Solar_Waianae | 2029 | 27.6 | 0 | 306.5499
Solar_Waianae | 2030 | 27.6 | 0 | 306.5499
Solar_Waianae | 2031 | 27.6 | 0 | 306.5499
Solar_Waianae | 2032 | 27.6 | 0 | 306.5499
Solar_Waianae | 2033 | 27.6 | 0 | 306.5499
Solar_Waianae | 2034 | 27.6 | 0 | 306.5499
Solar_Waianae | 2040 | 0 | 0 | 306.5499
Solar_Waianae | 2045 | 0 | 0 | 306.5499
Solar_Waianae | 2050 | 0 | 0 | 306.5499
Hoohana_Solar_Supply | 2025 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2026 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2027 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2028 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2029 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2030 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2031 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2032 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2033 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2034 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2040 | 52 | 0 | 228.0996
Hoohana_Solar_Supply | 2045 | 0 | 0 | 228.0996
Hoohana_Solar_Supply | 2050 | 0 | 0 | 228.0996
West_Oahu_Solar_Supply | 2025 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2026 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2027 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2028 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2029 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2030 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2031 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2032 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2033 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2034 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2040 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2045 | 12.5 | 0 | 244.1548
West_Oahu_Solar_Supply | 2050 | 0 | 0 | 244.1548
Mililani_Solar_1_Supply | 2025 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2026 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2027 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2028 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2029 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2030 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2031 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2032 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2033 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2034 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2040 | 39 | 0 | 220.6147
Mililani_Solar_1_Supply | 2045 | 0 | 0 | 220.6147
Mililani_Solar_1_Supply | 2050 | 0 | 0 | 220.6147
Waiawa_Solar_Supply | 2025 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2026 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2027 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2028 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2029 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2030 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2031 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2032 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2033 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2034 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2040 | 36 | 0 | 245.5474
Waiawa_Solar_Supply | 2045 | 0 | 0 | 245.5474
Waiawa_Solar_Supply | 2050 | 0 | 0 | 245.5474
PV_Paired_Grid_4hr_New_Supply | 2025 | 0 | 0 | 11.4768
PV_Paired_Grid_4hr_New_Supply | 2026 | 0 | 0 | 11.0573
PV_Paired_Grid_4hr_New_Supply | 2027 | 0 | 0 | 10.6633
PV_Paired_Grid_4hr_New_Supply | 2028 | 0 | 0 | 10.3075
PV_Paired_Grid_4hr_New_Supply | 2029 | 0 | 0 | 9.9897
PV_Paired_Grid_4hr_New_Supply | 2030 | 0 | 0 | 9.7101
PV_Paired_Grid_4hr_New_Supply | 2031 | 0 | 0 | 9.4559
PV_Paired_Grid_4hr_New_Supply | 2032 | 0 | 0 | 9.2399
PV_Paired_Grid_4hr_New_Supply | 2033 | 0 | 0 | 9.0492
PV_Paired_Grid_4hr_New_Supply | 2034 | 0 | 0 | 8.8713
PV_Paired_Grid_4hr_New_Supply | 2040 | 0 | 0 | 8.1468
PV_Paired_Grid_4hr_New_Supply | 2045 | 0 | 0 | 7.7783
PV_Paired_Grid_4hr_New_Supply | 2050 | 0 | 0 | 7.5114
PV_Paired_Grid_6hr_New_Supply | 2025 | 0 | 0 | 11.4768
PV_Paired_Grid_6hr_New_Supply | 2026 | 0 | 0 | 11.0573
PV_Paired_Grid_6hr_New_Supply | 2027 | 0 | 0 | 10.6633
PV_Paired_Grid_6hr_New_Supply | 2028 | 0 | 0 | 10.3075
PV_Paired_Grid_6hr_New_Supply | 2029 | 0 | 0 | 9.9897
PV_Paired_Grid_6hr_New_Supply | 2030 | 0 | 0 | 9.7101
PV_Paired_Grid_6hr_New_Supply | 2031 | 0 | 0 | 9.4559
PV_Paired_Grid_6hr_New_Supply | 2032 | 0 | 0 | 9.2399
PV_Paired_Grid_6hr_New_Supply | 2033 | 0 | 0 | 9.0492
PV_Paired_Grid_6hr_New_Supply | 2034 | 0 | 0 | 8.8713
PV_Paired_Grid_6hr_New_Supply | 2040 | 0 | 0 | 8.1468
PV_Paired_Grid_6hr_New_Supply | 2045 | 0 | 0 | 7.7783
PV_Paired_Grid_6hr_New_Supply | 2050 | 0 | 0 | 7.5114
PV_Kupehau_Supply | 2025 | 60 | 0 | 221.9949
PV_Kupehau_Supply | 2026 | 60 | 0 | 216.944
PV_Kupehau_Supply | 2027 | 60 | 0 | 212.008
PV_Kupehau_Supply | 2028 | 60 | 0 | 207.1844
PV_Kupehau_Supply | 2029 | 60 | 0 | 202.4705
PV_Kupehau_Supply | 2030 | 60 | 0 | 197.8639
PV_Kupehau_Supply | 2031 | 60 | 0 | 193.362
PV_Kupehau_Supply | 2032 | 60 | 0 | 188.9626
PV_Kupehau_Supply | 2033 | 60 | 0 | 184.6633
PV_Kupehau_Supply | 2034 | 60 | 0 | 180.4618
PV_Kupehau_Supply | 2040 | 60 | 0 | 157.1859
PV_Kupehau_Supply | 2045 | 0 | 0 | 140.0997
PV_Kupehau_Supply | 2050 | 0 | 0 | 124.8708
PV_Waiawa_Ph2_Supply | 2025 | 60 | 0 | 82.0677
PV_Waiawa_Ph2_Supply | 2026 | 60 | 0 | 80.2004
PV_Waiawa_Ph2_Supply | 2027 | 60 | 0 | 78.3757
PV_Waiawa_Ph2_Supply | 2028 | 60 | 0 | 76.5925
PV_Waiawa_Ph2_Supply | 2029 | 60 | 0 | 74.8499
PV_Waiawa_Ph2_Supply | 2030 | 60 | 0 | 73.1469
PV_Waiawa_Ph2_Supply | 2031 | 60 | 0 | 71.4826
PV_Waiawa_Ph2_Supply | 2032 | 60 | 0 | 69.8562
PV_Waiawa_Ph2_Supply | 2033 | 60 | 0 | 68.2668
PV_Waiawa_Ph2_Supply | 2034 | 60 | 0 | 66.7136
PV_Waiawa_Ph2_Supply | 2040 | 60 | 0 | 58.1089
PV_Waiawa_Ph2_Supply | 2045 | 0 | 0 | 51.7924
PV_Waiawa_Ph2_Supply | 2050 | 0 | 0 | 46.1626
PV_Mountain_View_Supply | 2025 | 19.5 | 0 | 184.753
PV_Mountain_View_Supply | 2026 | 19.5 | 0 | 180.5494
PV_Mountain_View_Supply | 2027 | 19.5 | 0 | 176.4415
PV_Mountain_View_Supply | 2028 | 19.5 | 0 | 172.4271
PV_Mountain_View_Supply | 2029 | 19.5 | 0 | 168.504
PV_Mountain_View_Supply | 2030 | 19.5 | 0 | 164.6702
PV_Mountain_View_Supply | 2031 | 19.5 | 0 | 160.9236
PV_Mountain_View_Supply | 2032 | 19.5 | 0 | 157.2622
PV_Mountain_View_Supply | 2033 | 19.5 | 0 | 153.6842
PV_Mountain_View_Supply | 2034 | 19.5 | 0 | 150.1875
PV_Mountain_View_Supply | 2040 | 19.5 | 0 | 130.8164
PV_Mountain_View_Supply | 2045 | 19.5 | 0 | 116.5966
PV_Mountain_View_Supply | 2050 | 0 | 0 | 103.9224
PV_Kupono_Supply | 2025 | 0 | 0 | 256.8809
PV_Kupono_Supply | 2026 | 0 | 0 | 251.0363
PV_Kupono_Supply | 2027 | 0 | 0 | 245.3247
PV_Kupono_Supply | 2028 | 0 | 0 | 239.743
PV_Kupono_Supply | 2029 | 0 | 0 | 234.2884
PV_Kupono_Supply | 2030 | 0 | 0 | 228.9578
PV_Kupono_Supply | 2031 | 0 | 0 | 223.7485
PV_Kupono_Supply | 2032 | 0 | 0 | 218.6577
PV_Kupono_Supply | 2033 | 0 | 0 | 213.6828
PV_Kupono_Supply | 2034 | 0 | 0 | 208.8211
PV_Kupono_Supply | 2040 | 0 | 0 | 181.8874
PV_Kupono_Supply | 2045 | 0 | 0 | 162.1161
PV_Kupono_Supply | 2050 | 0 | 0 | 144.494
PV_Barbers_Point_Supply | 2025 | 19 | 0 | 203.558
PV_Barbers_Point_Supply | 2026 | 19 | 0 | 198.9266
PV_Barbers_Point_Supply | 2027 | 19 | 0 | 194.4006
PV_Barbers_Point_Supply | 2028 | 19 | 0 | 189.9776
PV_Barbers_Point_Supply | 2029 | 19 | 0 | 185.6552
PV_Barbers_Point_Supply | 2030 | 19 | 0 | 181.4311
PV_Barbers_Point_Supply | 2031 | 19 | 0 | 177.3032
PV_Barbers_Point_Supply | 2032 | 19 | 0 | 173.2691
PV_Barbers_Point_Supply | 2033 | 19 | 0 | 169.3269
PV_Barbers_Point_Supply | 2034 | 19 | 0 | 165.4743
PV_Barbers_Point_Supply | 2040 | 19 | 0 | 144.1315
PV_Barbers_Point_Supply | 2045 | 19 | 0 | 128.4643
PV_Barbers_Point_Supply | 2050 | 0 | 0 | 114.5002
PV_Mahi_Supply | 2025 | 120 | 0 | 205.1386
PV_Mahi_Supply | 2026 | 120 | 0 | 200.4713
PV_Mahi_Supply | 2027 | 120 | 0 | 195.9101
PV_Mahi_Supply | 2028 | 120 | 0 | 191.4527
PV_Mahi_Supply | 2029 | 120 | 0 | 187.0968
PV_Mahi_Supply | 2030 | 120 | 0 | 182.8399
PV_Mahi_Supply | 2031 | 120 | 0 | 178.6799
PV_Mahi_Supply | 2032 | 120 | 0 | 174.6146
PV_Mahi_Supply | 2033 | 120 | 0 | 170.6417
PV_Mahi_Supply | 2034 | 120 | 0 | 166.7592
PV_Mahi_Supply | 2040 | 120 | 0 | 145.2507
PV_Mahi_Supply | 2045 | 120 | 0 | 129.4618
PV_Mahi_Supply | 2050 | 0 | 0 | 115.3892
PV_Aggregated_DER_Supply | 2025 | 0 | 0 | 15.0736
PV_Aggregated_DER_Supply | 2026 | 0 | 0 | 14.5144
PV_Aggregated_DER_Supply | 2027 | 0 | 0 | 14.006
PV_Aggregated_DER_Supply | 2028 | 0 | 0 | 13.5484
PV_Aggregated_DER_Supply | 2029 | 0 | 0 | 13.1163
PV_Aggregated_DER_Supply | 2030 | 0 | 0 | 12.7477
PV_Aggregated_DER_Supply | 2031 | 0 | 0 | 12.43
PV_Aggregated_DER_Supply | 2032 | 0 | 0 | 12.1377
PV_Aggregated_DER_Supply | 2033 | 0 | 0 | 11.8835
PV_Aggregated_DER_Supply | 2034 | 0 | 0 | 11.6547
PV_Aggregated_DER_Supply | 2040 | 0 | 0 | 10.7015
PV_Aggregated_DER_Supply | 2045 | 0 | 0 | 10.2185
PV_Aggregated_DER_Supply | 2050 | 0 | 0 | 9.8754
PV_Paired_LowCF_4hr_New_Supply | 2025 | 0 | 0 | 11.4768
PV_Paired_LowCF_4hr_New_Supply | 2026 | 0 | 0 | 11.0573
PV_Paired_LowCF_4hr_New_Supply | 2027 | 0 | 0 | 10.6633
PV_Paired_LowCF_4hr_New_Supply | 2028 | 0 | 0 | 10.3075
PV_Paired_LowCF_4hr_New_Supply | 2029 | 0 | 0 | 9.9897
PV_Paired_LowCF_4hr_New_Supply | 2030 | 0 | 0 | 9.7101
PV_Paired_LowCF_4hr_New_Supply | 2031 | 0 | 0 | 9.4559
PV_Paired_LowCF_4hr_New_Supply | 2032 | 0 | 0 | 9.2399
PV_Paired_LowCF_4hr_New_Supply | 2033 | 0 | 0 | 9.0492
PV_Paired_LowCF_4hr_New_Supply | 2034 | 0 | 0 | 8.8713
PV_Paired_LowCF_4hr_New_Supply | 2040 | 0 | 0 | 8.1468
PV_Paired_LowCF_4hr_New_Supply | 2045 | 0 | 0 | 7.7783
PV_Paired_LowCF_4hr_New_Supply | 2050 | 0 | 0 | 7.5114
PV_Paired_LowCF_6hr_New_Supply | 2025 | 0 | 0 | 11.4768
PV_Paired_LowCF_6hr_New_Supply | 2026 | 0 | 0 | 11.0573
PV_Paired_LowCF_6hr_New_Supply | 2027 | 0 | 0 | 10.6633
PV_Paired_LowCF_6hr_New_Supply | 2028 | 0 | 0 | 10.3075
PV_Paired_LowCF_6hr_New_Supply | 2029 | 0 | 0 | 9.9897
PV_Paired_LowCF_6hr_New_Supply | 2030 | 0 | 0 | 9.7101
PV_Paired_LowCF_6hr_New_Supply | 2031 | 0 | 0 | 9.4559
PV_Paired_LowCF_6hr_New_Supply | 2032 | 0 | 0 | 9.2399
PV_Paired_LowCF_6hr_New_Supply | 2033 | 0 | 0 | 9.0492
PV_Paired_LowCF_6hr_New_Supply | 2034 | 0 | 0 | 8.8713
PV_Paired_LowCF_6hr_New_Supply | 2040 | 0 | 0 | 8.1468
PV_Paired_LowCF_6hr_New_Supply | 2045 | 0 | 0 | 7.7783
PV_Paired_LowCF_6hr_New_Supply | 2050 | 0 | 0 | 7.5114
Battery_Grid-Scale_Planned | 2025 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2026 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2027 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2028 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2029 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2030 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2031 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2032 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2033 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2034 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2040 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2045 | 0 | 0 | 0
Battery_Grid-Scale_Planned | 2050 | 0 | 0 | 0
Battery_Grid-Scale_New | 2025 | 0 | 0 | 16.0651
Battery_Grid-Scale_New | 2026 | 0 | 0 | 15.7866
Battery_Grid-Scale_New | 2027 | 0 | 0 | 15.5409
Battery_Grid-Scale_New | 2028 | 0 | 0 | 15.3025
Battery_Grid-Scale_New | 2029 | 0 | 0 | 15.0768
Battery_Grid-Scale_New | 2030 | 0 | 0 | 14.8568
Battery_Grid-Scale_New | 2031 | 0 | 0 | 14.6574
Battery_Grid-Scale_New | 2032 | 0 | 0 | 14.4796
Battery_Grid-Scale_New | 2033 | 0 | 0 | 14.3172
Battery_Grid-Scale_New | 2034 | 0 | 0 | 14.1645
Battery_Grid-Scale_New | 2040 | 0 | 0 | 13.4008
Battery_Grid-Scale_New | 2045 | 0 | 0 | 12.9491
Battery_Grid-Scale_New | 2050 | 0 | 0 | 12.5489
Kapolei_Energy_Storage | 2025 | 135 | 0 | 121.1326
Kapolei_Energy_Storage | 2026 | 135 | 0 | 118.3766
Kapolei_Energy_Storage | 2027 | 135 | 0 | 115.6833
Kapolei_Energy_Storage | 2028 | 135 | 0 | 113.0512
Kapolei_Energy_Storage | 2029 | 135 | 0 | 110.479
Kapolei_Energy_Storage | 2030 | 135 | 0 | 107.9654
Kapolei_Energy_Storage | 2031 | 135 | 0 | 105.509
Kapolei_Energy_Storage | 2032 | 135 | 0 | 103.1084
Kapolei_Energy_Storage | 2033 | 135 | 0 | 100.7625
Kapolei_Energy_Storage | 2034 | 135 | 0 | 98.4699
Kapolei_Energy_Storage | 2040 | 135 | 0 | 85.7693
Kapolei_Energy_Storage | 2045 | 0 | 0 | 76.4461
Kapolei_Energy_Storage | 2050 | 0 | 0 | 68.1364
Load_Build | 2025 | 14.451 | 0 | 51.7449
Load_Build | 2026 | 0 | 0 | 0
Load_Build | 2027 | 0 | 0 | 0
Load_Build | 2028 | 0 | 0 | 0
Load_Build | 2029 | 0 | 0 | 0
Load_Build | 2030 | 0 | 0 | 0
Load_Build | 2031 | 0 | 0 | 0
Load_Build | 2032 | 0 | 0 | 0
Load_Build | 2033 | 0 | 0 | 0
Load_Build | 2034 | 0 | 0 | 0
Load_Build | 2040 | 0 | 0 | 0
Load_Build | 2045 | 0 | 0 | 0
Load_Build | 2050 | 0 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2025 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2026 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2027 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2028 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2029 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2030 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2031 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2032 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2033 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2034 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2040 | 50 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2045 | 0 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2050 | 0 | 0 | 0
Hoohana_Solar_Battery | 2025 | 52 | 0 | 0
Hoohana_Solar_Battery | 2026 | 52 | 0 | 0
Hoohana_Solar_Battery | 2027 | 52 | 0 | 0
Hoohana_Solar_Battery | 2028 | 52 | 0 | 0
Hoohana_Solar_Battery | 2029 | 52 | 0 | 0
Hoohana_Solar_Battery | 2030 | 52 | 0 | 0
Hoohana_Solar_Battery | 2031 | 52 | 0 | 0
Hoohana_Solar_Battery | 2032 | 52 | 0 | 0
Hoohana_Solar_Battery | 2033 | 52 | 0 | 0
Hoohana_Solar_Battery | 2034 | 52 | 0 | 0
Hoohana_Solar_Battery | 2040 | 52 | 0 | 0
Hoohana_Solar_Battery | 2045 | 0 | 0 | 0
Hoohana_Solar_Battery | 2050 | 0 | 0 | 0
West_Oahu_Solar_Battery | 2025 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2026 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2027 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2028 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2029 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2030 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2031 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2032 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2033 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2034 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2040 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2045 | 12.5 | 0 | 0
West_Oahu_Solar_Battery | 2050 | 0 | 0 | 0
Mililani_Solar_1_Battery | 2025 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2026 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2027 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2028 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2029 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2030 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2031 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2032 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2033 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2034 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2040 | 39 | 0 | 0
Mililani_Solar_1_Battery | 2045 | 0 | 0 | 0
Mililani_Solar_1_Battery | 2050 | 0 | 0 | 0
Waiawa_Solar_Battery | 2025 | 36 | 0 | 0
Waiawa_Solar_Battery | 2026 | 36 | 0 | 0
Waiawa_Solar_Battery | 2027 | 36 | 0 | 0
Waiawa_Solar_Battery | 2028 | 36 | 0 | 0
Waiawa_Solar_Battery | 2029 | 36 | 0 | 0
Waiawa_Solar_Battery | 2030 | 36 | 0 | 0
Waiawa_Solar_Battery | 2031 | 36 | 0 | 0
Waiawa_Solar_Battery | 2032 | 36 | 0 | 0
Waiawa_Solar_Battery | 2033 | 36 | 0 | 0
Waiawa_Solar_Battery | 2034 | 36 | 0 | 0
Waiawa_Solar_Battery | 2040 | 36 | 0 | 0
Waiawa_Solar_Battery | 2045 | 0 | 0 | 0
Waiawa_Solar_Battery | 2050 | 0 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2025 | 0 | 0 | 12.8521
PV_Paired_Grid_4hr_New_Battery | 2026 | 0 | 0 | 12.6293
PV_Paired_Grid_4hr_New_Battery | 2027 | 0 | 0 | 12.4327
PV_Paired_Grid_4hr_New_Battery | 2028 | 0 | 0 | 12.242
PV_Paired_Grid_4hr_New_Battery | 2029 | 0 | 0 | 12.0614
PV_Paired_Grid_4hr_New_Battery | 2030 | 0 | 0 | 11.8854
PV_Paired_Grid_4hr_New_Battery | 2031 | 0 | 0 | 11.726
PV_Paired_Grid_4hr_New_Battery | 2032 | 0 | 0 | 11.5837
PV_Paired_Grid_4hr_New_Battery | 2033 | 0 | 0 | 11.4538
PV_Paired_Grid_4hr_New_Battery | 2034 | 0 | 0 | 11.3316
PV_Paired_Grid_4hr_New_Battery | 2040 | 0 | 0 | 10.7206
PV_Paired_Grid_4hr_New_Battery | 2045 | 0 | 0 | 10.3593
PV_Paired_Grid_4hr_New_Battery | 2050 | 0 | 0 | 10.0392
PV_Paired_Grid_6hr_New_Battery | 2025 | 0 | 0 | 12.8521
PV_Paired_Grid_6hr_New_Battery | 2026 | 0 | 0 | 12.6293
PV_Paired_Grid_6hr_New_Battery | 2027 | 0 | 0 | 12.4327
PV_Paired_Grid_6hr_New_Battery | 2028 | 0 | 0 | 12.242
PV_Paired_Grid_6hr_New_Battery | 2029 | 0 | 0 | 12.0614
PV_Paired_Grid_6hr_New_Battery | 2030 | 0 | 0 | 11.8854
PV_Paired_Grid_6hr_New_Battery | 2031 | 0 | 0 | 11.726
PV_Paired_Grid_6hr_New_Battery | 2032 | 0 | 0 | 11.5837
PV_Paired_Grid_6hr_New_Battery | 2033 | 0 | 0 | 11.4538
PV_Paired_Grid_6hr_New_Battery | 2034 | 0 | 0 | 11.3316
PV_Paired_Grid_6hr_New_Battery | 2040 | 0 | 0 | 10.7206
PV_Paired_Grid_6hr_New_Battery | 2045 | 0 | 0 | 10.3593
PV_Paired_Grid_6hr_New_Battery | 2050 | 0 | 0 | 10.0392
PV_Kupehau_Battery | 2025 | 60 | 0 | 0
PV_Kupehau_Battery | 2026 | 60 | 0 | 0
PV_Kupehau_Battery | 2027 | 60 | 0 | 0
PV_Kupehau_Battery | 2028 | 60 | 0 | 0
PV_Kupehau_Battery | 2029 | 60 | 0 | 0
PV_Kupehau_Battery | 2030 | 60 | 0 | 0
PV_Kupehau_Battery | 2031 | 60 | 0 | 0
PV_Kupehau_Battery | 2032 | 60 | 0 | 0
PV_Kupehau_Battery | 2033 | 60 | 0 | 0
PV_Kupehau_Battery | 2034 | 60 | 0 | 0
PV_Kupehau_Battery | 2040 | 60 | 0 | 0
PV_Kupehau_Battery | 2045 | 0 | 0 | 0
PV_Kupehau_Battery | 2050 | 0 | 0 | 0
PV_Waiawa_Ph2_Battery | 2025 | 30 | 0 | 168.4337
PV_Waiawa_Ph2_Battery | 2026 | 30 | 0 | 164.6015
PV_Waiawa_Ph2_Battery | 2027 | 30 | 0 | 160.8564
PV_Waiawa_Ph2_Battery | 2028 | 30 | 0 | 157.1966
PV_Waiawa_Ph2_Battery | 2029 | 30 | 0 | 153.62
PV_Waiawa_Ph2_Battery | 2030 | 30 | 0 | 150.1248
PV_Waiawa_Ph2_Battery | 2031 | 30 | 0 | 146.7092
PV_Waiawa_Ph2_Battery | 2032 | 30 | 0 | 143.3712
PV_Waiawa_Ph2_Battery | 2033 | 30 | 0 | 140.1092
PV_Waiawa_Ph2_Battery | 2034 | 30 | 0 | 136.9214
PV_Waiawa_Ph2_Battery | 2040 | 30 | 0 | 119.2613
PV_Waiawa_Ph2_Battery | 2045 | 0 | 0 | 106.2975
PV_Waiawa_Ph2_Battery | 2050 | 0 | 0 | 94.7429
PV_Mountain_View_Battery | 2025 | 7 | 0 | 0
PV_Mountain_View_Battery | 2026 | 7 | 0 | 0
PV_Mountain_View_Battery | 2027 | 7 | 0 | 0
PV_Mountain_View_Battery | 2028 | 7 | 0 | 0
PV_Mountain_View_Battery | 2029 | 7 | 0 | 0
PV_Mountain_View_Battery | 2030 | 7 | 0 | 0
PV_Mountain_View_Battery | 2031 | 7 | 0 | 0
PV_Mountain_View_Battery | 2032 | 7 | 0 | 0
PV_Mountain_View_Battery | 2033 | 7 | 0 | 0
PV_Mountain_View_Battery | 2034 | 7 | 0 | 0
PV_Mountain_View_Battery | 2040 | 7 | 0 | 0
PV_Mountain_View_Battery | 2045 | 7 | 0 | 0
PV_Mountain_View_Battery | 2050 | 0 | 0 | 0
PV_Kupono_Battery | 2025 | 0 | 0 | 0
PV_Kupono_Battery | 2026 | 0 | 0 | 0
PV_Kupono_Battery | 2027 | 0 | 0 | 0
PV_Kupono_Battery | 2028 | 0 | 0 | 0
PV_Kupono_Battery | 2029 | 0 | 0 | 0
PV_Kupono_Battery | 2030 | 0 | 0 | 0
PV_Kupono_Battery | 2031 | 0 | 0 | 0
PV_Kupono_Battery | 2032 | 0 | 0 | 0
PV_Kupono_Battery | 2033 | 0 | 0 | 0
PV_Kupono_Battery | 2034 | 0 | 0 | 0
PV_Kupono_Battery | 2040 | 0 | 0 | 0
PV_Kupono_Battery | 2045 | 0 | 0 | 0
PV_Kupono_Battery | 2050 | 0 | 0 | 0
PV_Barbers_Point_Battery | 2025 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2026 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2027 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2028 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2029 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2030 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2031 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2032 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2033 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2034 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2040 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2045 | 15 | 0 | 0
PV_Barbers_Point_Battery | 2050 | 0 | 0 | 0
PV_Mahi_Battery | 2025 | 120 | 0 | 0
PV_Mahi_Battery | 2026 | 120 | 0 | 0
PV_Mahi_Battery | 2027 | 120 | 0 | 0
PV_Mahi_Battery | 2028 | 120 | 0 | 0
PV_Mahi_Battery | 2029 | 120 | 0 | 0
PV_Mahi_Battery | 2030 | 120 | 0 | 0
PV_Mahi_Battery | 2031 | 120 | 0 | 0
PV_Mahi_Battery | 2032 | 120 | 0 | 0
PV_Mahi_Battery | 2033 | 120 | 0 | 0
PV_Mahi_Battery | 2034 | 120 | 0 | 0
PV_Mahi_Battery | 2040 | 120 | 0 | 0
PV_Mahi_Battery | 2045 | 120 | 0 | 0
PV_Mahi_Battery | 2050 | 0 | 0 | 0
PV_Aggregated_DER_Battery | 2025 | 0 | 0 | 14.1373
PV_Aggregated_DER_Battery | 2026 | 0 | 0 | 13.8922
PV_Aggregated_DER_Battery | 2027 | 0 | 0 | 13.676
PV_Aggregated_DER_Battery | 2028 | 0 | 0 | 13.4662
PV_Aggregated_DER_Battery | 2029 | 0 | 0 | 13.2676
PV_Aggregated_DER_Battery | 2030 | 0 | 0 | 13.074
PV_Aggregated_DER_Battery | 2031 | 0 | 0 | 12.8985
PV_Aggregated_DER_Battery | 2032 | 0 | 0 | 12.7421
PV_Aggregated_DER_Battery | 2033 | 0 | 0 | 12.5991
PV_Aggregated_DER_Battery | 2034 | 0 | 0 | 12.4648
PV_Aggregated_DER_Battery | 2040 | 0 | 0 | 11.7927
PV_Aggregated_DER_Battery | 2045 | 0 | 0 | 11.3952
PV_Aggregated_DER_Battery | 2050 | 0 | 0 | 11.0431
PV_Paired_LowCF_4hr_New_Battery | 2025 | 0 | 0 | 12.8521
PV_Paired_LowCF_4hr_New_Battery | 2026 | 0 | 0 | 12.6293
PV_Paired_LowCF_4hr_New_Battery | 2027 | 0 | 0 | 12.4327
PV_Paired_LowCF_4hr_New_Battery | 2028 | 0 | 0 | 12.242
PV_Paired_LowCF_4hr_New_Battery | 2029 | 0 | 0 | 12.0614
PV_Paired_LowCF_4hr_New_Battery | 2030 | 0 | 0 | 11.8854
PV_Paired_LowCF_4hr_New_Battery | 2031 | 0 | 0 | 11.726
PV_Paired_LowCF_4hr_New_Battery | 2032 | 0 | 0 | 11.5837
PV_Paired_LowCF_4hr_New_Battery | 2033 | 0 | 0 | 11.4538
PV_Paired_LowCF_4hr_New_Battery | 2034 | 0 | 0 | 11.3316
PV_Paired_LowCF_4hr_New_Battery | 2040 | 0 | 0 | 10.7206
PV_Paired_LowCF_4hr_New_Battery | 2045 | 0 | 0 | 10.3593
PV_Paired_LowCF_4hr_New_Battery | 2050 | 0 | 0 | 10.0392
PV_Paired_LowCF_6hr_New_Battery | 2025 | 0 | 0 | 12.8521
PV_Paired_LowCF_6hr_New_Battery | 2026 | 0 | 0 | 12.6293
PV_Paired_LowCF_6hr_New_Battery | 2027 | 0 | 0 | 12.4327
PV_Paired_LowCF_6hr_New_Battery | 2028 | 0 | 0 | 12.242
PV_Paired_LowCF_6hr_New_Battery | 2029 | 0 | 0 | 12.0614
PV_Paired_LowCF_6hr_New_Battery | 2030 | 0 | 0 | 11.8854
PV_Paired_LowCF_6hr_New_Battery | 2031 | 0 | 0 | 11.726
PV_Paired_LowCF_6hr_New_Battery | 2032 | 0 | 0 | 11.5837
PV_Paired_LowCF_6hr_New_Battery | 2033 | 0 | 0 | 11.4538
PV_Paired_LowCF_6hr_New_Battery | 2034 | 0 | 0 | 11.3316
PV_Paired_LowCF_6hr_New_Battery | 2040 | 0 | 0 | 10.7206
PV_Paired_LowCF_6hr_New_Battery | 2045 | 0 | 0 | 10.3593
PV_Paired_LowCF_6hr_New_Battery | 2050 | 0 | 0 | 10.0392
Load_reduce | 2025 | 19.437 | 0 | 0
Load_reduce | 2026 | 0 | 0 | 0
Load_reduce | 2027 | 0 | 0 | 0
Load_reduce | 2028 | 0 | 0 | 0
Load_reduce | 2029 | 0 | 0 | 0
Load_reduce | 2030 | 0 | 0 | 0
Load_reduce | 2031 | 0 | 0 | 0
Load_reduce | 2032 | 0 | 0 | 0
Load_reduce | 2033 | 0 | 0 | 0
Load_reduce | 2034 | 0 | 0 | 0
Load_reduce | 2040 | 0 | 0 | 0
Load_reduce | 2045 | 0 | 0 | 0
Load_reduce | 2050 | 0 | 0 | 0

## planned_storage_energy_capacity
Planned Storage Energy Capacity |  |  |  | Index
storage_resource | period | planned_storage_energy_capacity_mwh | planned_storage_energy_capacity_fixed_o_and_m_dollars_per_kwh_yr
Battery_Grid-Scale_Planned | 2025 | 0 | 0
Battery_Grid-Scale_Planned | 2026 | 0 | 0
Battery_Grid-Scale_Planned | 2027 | 0 | 0
Battery_Grid-Scale_Planned | 2028 | 0 | 0
Battery_Grid-Scale_Planned | 2029 | 0 | 0
Battery_Grid-Scale_Planned | 2030 | 0 | 0
Battery_Grid-Scale_Planned | 2031 | 0 | 0
Battery_Grid-Scale_Planned | 2032 | 0 | 0
Battery_Grid-Scale_Planned | 2033 | 0 | 0
Battery_Grid-Scale_Planned | 2034 | 0 | 0
Battery_Grid-Scale_Planned | 2040 | 0 | 0
Battery_Grid-Scale_Planned | 2045 | 0 | 0
Battery_Grid-Scale_Planned | 2050 | 0 | 0
Battery_Grid-Scale_New | 2025 | 0 | 0
Battery_Grid-Scale_New | 2026 | 0 | 0
Battery_Grid-Scale_New | 2027 | 0 | 0
Battery_Grid-Scale_New | 2028 | 0 | 0
Battery_Grid-Scale_New | 2029 | 0 | 0
Battery_Grid-Scale_New | 2030 | 0 | 0
Battery_Grid-Scale_New | 2031 | 0 | 0
Battery_Grid-Scale_New | 2032 | 0 | 0
Battery_Grid-Scale_New | 2033 | 0 | 0
Battery_Grid-Scale_New | 2034 | 0 | 0
Battery_Grid-Scale_New | 2040 | 0 | 0
Battery_Grid-Scale_New | 2045 | 0 | 0
Battery_Grid-Scale_New | 2050 | 0 | 0
Kapolei_Energy_Storage | 2025 | 540 | 0
Kapolei_Energy_Storage | 2026 | 540 | 0
Kapolei_Energy_Storage | 2027 | 540 | 0
Kapolei_Energy_Storage | 2028 | 540 | 0
Kapolei_Energy_Storage | 2029 | 540 | 0
Kapolei_Energy_Storage | 2030 | 540 | 0
Kapolei_Energy_Storage | 2031 | 540 | 0
Kapolei_Energy_Storage | 2032 | 540 | 0
Kapolei_Energy_Storage | 2033 | 540 | 0
Kapolei_Energy_Storage | 2034 | 540 | 0
Kapolei_Energy_Storage | 2040 | 540 | 0
Kapolei_Energy_Storage | 2045 | 0 | 0
Kapolei_Energy_Storage | 2050 | 0 | 0
Load_Build | 2025 | 57.8 | 0
Load_Build | 2026 | 57.8 | 0
Load_Build | 2027 | 57.8 | 0
Load_Build | 2028 | 0 | 0
Load_Build | 2029 | 0 | 0
Load_Build | 2030 | 0 | 0
Load_Build | 2031 | 0 | 0
Load_Build | 2032 | 0 | 0
Load_Build | 2033 | 0 | 0
Load_Build | 2034 | 0 | 0
Load_Build | 2040 | 0 | 0
Load_Build | 2045 | 0 | 0
Load_Build | 2050 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2025 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2026 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2027 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2028 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2029 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2030 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2031 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2032 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2033 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2034 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2040 | 25 | 0
Kapolei_Energy_Storage_Contingency | 2045 | 0 | 0
Kapolei_Energy_Storage_Contingency | 2050 | 0 | 0
Hoohana_Solar_Battery | 2025 | 208 | 0
Hoohana_Solar_Battery | 2026 | 208 | 0
Hoohana_Solar_Battery | 2027 | 208 | 0
Hoohana_Solar_Battery | 2028 | 208 | 0
Hoohana_Solar_Battery | 2029 | 208 | 0
Hoohana_Solar_Battery | 2030 | 208 | 0
Hoohana_Solar_Battery | 2031 | 208 | 0
Hoohana_Solar_Battery | 2032 | 208 | 0
Hoohana_Solar_Battery | 2033 | 208 | 0
Hoohana_Solar_Battery | 2034 | 208 | 0
Hoohana_Solar_Battery | 2040 | 208 | 0
Hoohana_Solar_Battery | 2045 | 0 | 0
Hoohana_Solar_Battery | 2050 | 0 | 0
West_Oahu_Solar_Battery | 2025 | 50 | 0
West_Oahu_Solar_Battery | 2026 | 50 | 0
West_Oahu_Solar_Battery | 2027 | 50 | 0
West_Oahu_Solar_Battery | 2028 | 50 | 0
West_Oahu_Solar_Battery | 2029 | 50 | 0
West_Oahu_Solar_Battery | 2030 | 50 | 0
West_Oahu_Solar_Battery | 2031 | 50 | 0
West_Oahu_Solar_Battery | 2032 | 50 | 0
West_Oahu_Solar_Battery | 2033 | 50 | 0
West_Oahu_Solar_Battery | 2034 | 50 | 0
West_Oahu_Solar_Battery | 2040 | 50 | 0
West_Oahu_Solar_Battery | 2045 | 50 | 0
West_Oahu_Solar_Battery | 2050 | 0 | 0
Mililani_Solar_1_Battery | 2025 | 156 | 0
Mililani_Solar_1_Battery | 2026 | 156 | 0
Mililani_Solar_1_Battery | 2027 | 156 | 0
Mililani_Solar_1_Battery | 2028 | 156 | 0
Mililani_Solar_1_Battery | 2029 | 156 | 0
Mililani_Solar_1_Battery | 2030 | 156 | 0
Mililani_Solar_1_Battery | 2031 | 156 | 0
Mililani_Solar_1_Battery | 2032 | 156 | 0
Mililani_Solar_1_Battery | 2033 | 156 | 0
Mililani_Solar_1_Battery | 2034 | 156 | 0
Mililani_Solar_1_Battery | 2040 | 156 | 0
Mililani_Solar_1_Battery | 2045 | 0 | 0
Mililani_Solar_1_Battery | 2050 | 0 | 0
Waiawa_Solar_Battery | 2025 | 144 | 0
Waiawa_Solar_Battery | 2026 | 144 | 0
Waiawa_Solar_Battery | 2027 | 144 | 0
Waiawa_Solar_Battery | 2028 | 144 | 0
Waiawa_Solar_Battery | 2029 | 144 | 0
Waiawa_Solar_Battery | 2030 | 144 | 0
Waiawa_Solar_Battery | 2031 | 144 | 0
Waiawa_Solar_Battery | 2032 | 144 | 0
Waiawa_Solar_Battery | 2033 | 144 | 0
Waiawa_Solar_Battery | 2034 | 144 | 0
Waiawa_Solar_Battery | 2040 | 144 | 0
Waiawa_Solar_Battery | 2045 | 0 | 0
Waiawa_Solar_Battery | 2050 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2025 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2026 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2027 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2028 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2029 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2030 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2031 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2032 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2033 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2034 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2040 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2045 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | 2050 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2025 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2026 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2027 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2028 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2029 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2030 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2031 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2032 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2033 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2034 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2040 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2045 | 0 | 0
PV_Paired_Grid_6hr_New_Battery | 2050 | 0 | 0
PV_Kupehau_Battery | 2025 | 240 | 0
PV_Kupehau_Battery | 2026 | 240 | 0
PV_Kupehau_Battery | 2027 | 240 | 0
PV_Kupehau_Battery | 2028 | 240 | 0
PV_Kupehau_Battery | 2029 | 240 | 0
PV_Kupehau_Battery | 2030 | 240 | 0
PV_Kupehau_Battery | 2031 | 240 | 0
PV_Kupehau_Battery | 2032 | 240 | 0
PV_Kupehau_Battery | 2033 | 240 | 0
PV_Kupehau_Battery | 2034 | 240 | 0
PV_Kupehau_Battery | 2040 | 240 | 0
PV_Kupehau_Battery | 2045 | 0 | 0
PV_Kupehau_Battery | 2050 | 0 | 0
PV_Waiawa_Ph2_Battery | 2025 | 240 | 0
PV_Waiawa_Ph2_Battery | 2026 | 240 | 0
PV_Waiawa_Ph2_Battery | 2027 | 240 | 0
PV_Waiawa_Ph2_Battery | 2028 | 240 | 0
PV_Waiawa_Ph2_Battery | 2029 | 240 | 0
PV_Waiawa_Ph2_Battery | 2030 | 240 | 0
PV_Waiawa_Ph2_Battery | 2031 | 240 | 0
PV_Waiawa_Ph2_Battery | 2032 | 240 | 0
PV_Waiawa_Ph2_Battery | 2033 | 240 | 0
PV_Waiawa_Ph2_Battery | 2034 | 240 | 0
PV_Waiawa_Ph2_Battery | 2040 | 240 | 0
PV_Waiawa_Ph2_Battery | 2045 | 0 | 0
PV_Waiawa_Ph2_Battery | 2050 | 0 | 0
PV_Mountain_View_Battery | 2025 | 35 | 0
PV_Mountain_View_Battery | 2026 | 35 | 0
PV_Mountain_View_Battery | 2027 | 35 | 0
PV_Mountain_View_Battery | 2028 | 35 | 0
PV_Mountain_View_Battery | 2029 | 35 | 0
PV_Mountain_View_Battery | 2030 | 35 | 0
PV_Mountain_View_Battery | 2031 | 35 | 0
PV_Mountain_View_Battery | 2032 | 35 | 0
PV_Mountain_View_Battery | 2033 | 35 | 0
PV_Mountain_View_Battery | 2034 | 35 | 0
PV_Mountain_View_Battery | 2040 | 35 | 0
PV_Mountain_View_Battery | 2045 | 35 | 0
PV_Mountain_View_Battery | 2050 | 0 | 0
PV_Kupono_Battery | 2025 | 0 | 0
PV_Kupono_Battery | 2026 | 0 | 0
PV_Kupono_Battery | 2027 | 0 | 0
PV_Kupono_Battery | 2028 | 0 | 0
PV_Kupono_Battery | 2029 | 0 | 0
PV_Kupono_Battery | 2030 | 0 | 0
PV_Kupono_Battery | 2031 | 0 | 0
PV_Kupono_Battery | 2032 | 0 | 0
PV_Kupono_Battery | 2033 | 0 | 0
PV_Kupono_Battery | 2034 | 0 | 0
PV_Kupono_Battery | 2040 | 0 | 0
PV_Kupono_Battery | 2045 | 0 | 0
PV_Kupono_Battery | 2050 | 0 | 0
PV_Barbers_Point_Battery | 2025 | 60 | 0
PV_Barbers_Point_Battery | 2026 | 60 | 0
PV_Barbers_Point_Battery | 2027 | 60 | 0
PV_Barbers_Point_Battery | 2028 | 60 | 0
PV_Barbers_Point_Battery | 2029 | 60 | 0
PV_Barbers_Point_Battery | 2030 | 60 | 0
PV_Barbers_Point_Battery | 2031 | 60 | 0
PV_Barbers_Point_Battery | 2032 | 60 | 0
PV_Barbers_Point_Battery | 2033 | 60 | 0
PV_Barbers_Point_Battery | 2034 | 60 | 0
PV_Barbers_Point_Battery | 2040 | 60 | 0
PV_Barbers_Point_Battery | 2045 | 60 | 0
PV_Barbers_Point_Battery | 2050 | 0 | 0
PV_Mahi_Battery | 2025 | 480 | 0
PV_Mahi_Battery | 2026 | 480 | 0
PV_Mahi_Battery | 2027 | 480 | 0
PV_Mahi_Battery | 2028 | 480 | 0
PV_Mahi_Battery | 2029 | 480 | 0
PV_Mahi_Battery | 2030 | 480 | 0
PV_Mahi_Battery | 2031 | 480 | 0
PV_Mahi_Battery | 2032 | 480 | 0
PV_Mahi_Battery | 2033 | 480 | 0
PV_Mahi_Battery | 2034 | 480 | 0
PV_Mahi_Battery | 2040 | 480 | 0
PV_Mahi_Battery | 2045 | 480 | 0
PV_Mahi_Battery | 2050 | 0 | 0
PV_Aggregated_DER_Battery | 2025 | 0 | 0
PV_Aggregated_DER_Battery | 2026 | 0 | 0
PV_Aggregated_DER_Battery | 2027 | 0 | 0
PV_Aggregated_DER_Battery | 2028 | 0 | 0
PV_Aggregated_DER_Battery | 2029 | 0 | 0
PV_Aggregated_DER_Battery | 2030 | 0 | 0
PV_Aggregated_DER_Battery | 2031 | 0 | 0
PV_Aggregated_DER_Battery | 2032 | 0 | 0
PV_Aggregated_DER_Battery | 2033 | 0 | 0
PV_Aggregated_DER_Battery | 2034 | 0 | 0
PV_Aggregated_DER_Battery | 2040 | 0 | 0
PV_Aggregated_DER_Battery | 2045 | 0 | 0
PV_Aggregated_DER_Battery | 2050 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2025 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2026 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2027 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2028 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2029 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2030 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2031 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2032 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2033 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2034 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2040 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2045 | 0 | 0
PV_Paired_LowCF_4hr_New_Battery | 2050 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2025 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2026 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2027 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2028 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2029 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2030 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2031 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2032 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2033 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2034 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2040 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2045 | 0 | 0
PV_Paired_LowCF_6hr_New_Battery | 2050 | 0 | 0

## renewable_targets
Renewable Targets | [5 empty] | Index
period | non_modeled_rps_resources_mwh | pipeline_biogas_available_mmbtu_per_year | incremental_pipeline_biogas_cost_per_mmbtu | retail_sales_mwh | RPS_as_fractions_of_retail_sales
2025 | 1144726.3773 | 0 | 999999 | 6519772.8693 | 0.3
2026 | 1174867.7391 | 0 | 999999 | 6598541.9293 | 0.3
2027 | 1205798.9074 | 0 | 999999 | 6610940.013 | 0.3
2028 | 1240167.155 | 0 | 999999 | 6644589.1896 | 0.3
2029 | 1269894.3491 | 0 | 999999 | 6680621.4087 | 0.3
2030 | 1301803.9235 | 0 | 999999 | 6752601.285 | 0.4
2031 | 1332780.7408 | 0 | 999999 | 6786859.8779 | 0.4
2032 | 1366389.8494 | 0 | 999999 | 6823040.8224 | 0.4
2033 | 1391482.4943 | 0 | 999999 | 6877804.9613 | 0.4
2034 | 1418523.1362 | 0 | 999999 | 6921940.1161 | 0.4
2040 | 1567628.1733 | 0 | 999999 | 7431063.6074 | 0.7
2045 | 1663865.1788 | 9999999999 | 26.7149 | 8078630.3508 | 1
2050 | 1737623.5128 | 9999999999 | 26.6437 | 8821585.0348 | 1

## reserve_resources
Reserve Resources | [5 empty] | Index
resource | can_provide_lf_reserves | contributes_to_freq_resp_total | thermal_freq_response_fraction_of_commitment | can_provide_inertia | inertia_response_multiplier_of_commitment
FFR | 0 | 1 | 1 | FALSE | 0
Airport_DSG | 1 | 0 | 0 | FALSE | 0
Biomass | 1 | 0 | 0 | TRUE | 3.4443
CIP_BioD | 1 | 0 | 0 | TRUE | 6.818
Hpoff | 0 | 0 | 0 | TRUE | 3.4025
Kala1_Biod | 1 | 0 | 0 | TRUE | 7.0646
Kala2_Biod | 1 | 0 | 0 | TRUE | 7.0646
Schofield | 1 | 0 | 0 | TRUE | 1.3229
Schofield_Biod | 1 | 0 | 0 | TRUE | 1.3229
AES | 1 | 0 | 0 | TRUE | 3.4124
CIP_Diesel | 1 | 0 | 0 | TRUE | 5.9274
ICE_New | 1 | 0 | 0 | TRUE | 1.3229
Kahe_5-6 | 1 | 0 | 0 | TRUE | 5.1144
Kala1 | 1 | 0 | 0 | TRUE | 7.0646
Kala2 | 1 | 0 | 0 | TRUE | 7.0646
LM6000_2x1CC_Sync_Cond | 1 | 0 | 0 | TRUE | 9.4058
Sync_Cond | 0 | 0 | 0 | TRUE | 3
Waiau_3-4 | 1 | 0 | 0 | TRUE | 5.5421
Waiau_5-6 | 1 | 0 | 0 | TRUE | 4.7836
Waiau_9-10 | 1 | 0 | 0 | TRUE | 8.6942
SC_6000CC_New | 1 | 0 | 0 | TRUE | 8.4476
K14_W78 | 1 | 0 | 0 | TRUE | 4.7845
Battery_Grid-Scale_Planned | 1 | 1 | 1 | FALSE | 0
Battery_Grid-Scale_New | 1 | 1 | 1 | FALSE | 0
Kapolei_Energy_Storage | 1 | 1 | 1 | FALSE | 0
Kapolei_Energy_Storage_Contingency | 1 | 1 | 1 | FALSE | 0
PV_Paired_Grid_4hr_New_Battery | 0 | 1 | 1 | FALSE | 0
PV_Paired_Grid_6hr_New_Battery | 0 | 1 | 1 | FALSE | 0
PV_Kupehau_Battery | 0 | 1 | 1 | FALSE | 0
PV_Waiawa_Ph2_Battery | 0 | 1 | 1 | FALSE | 0
PV_Mountain_View_Battery | 0 | 1 | 1 | FALSE | 0
PV_Kupono_Battery | 0 | 1 | 1 | FALSE | 0
PV_Barbers_Point_Battery | 0 | 1 | 1 | FALSE | 0
PV_Mahi_Battery | 0 | 1 | 1 | FALSE | 0
PV_Aggregated_DER_Battery | 0 | 1 | 1 | FALSE | 0
PV_Paired_LowCF_4hr_New_Battery | 0 | 1 | 1 | FALSE | 0
PV_Paired_LowCF_6hr_New_Battery | 0 | 1 | 1 | FALSE | 0

## resource_storage_paired
Resource Storage Paired |  |  |  | Index
paired_storage_resource | paired_supply_resource | enforce_pairing_ratio | pairing_ratio
Hoohana_Solar_Battery | Hoohana_Solar_Supply | FALSE | 0
West_Oahu_Solar_Battery | West_Oahu_Solar_Supply | FALSE | 0
Mililani_Solar_1_Battery | Mililani_Solar_1_Supply | FALSE | 0
Waiawa_Solar_Battery | Waiawa_Solar_Supply | FALSE | 0
PV_Paired_Grid_4hr_New_Battery | PV_Paired_Grid_4hr_New_Supply | TRUE | 1
PV_Paired_Grid_6hr_New_Battery | PV_Paired_Grid_6hr_New_Supply | TRUE | 1
PV_Kupehau_Battery | PV_Kupehau_Supply | TRUE | 1
PV_Waiawa_Ph2_Battery | PV_Waiawa_Ph2_Supply | FALSE | 0
PV_Mountain_View_Battery | PV_Mountain_View_Supply | FALSE | 0
PV_Kupono_Battery | PV_Kupono_Supply | FALSE | 0
PV_Barbers_Point_Battery | PV_Barbers_Point_Supply | FALSE | 0
PV_Mahi_Battery | PV_Mahi_Supply | FALSE | 0
PV_Aggregated_DER_Battery | PV_Aggregated_DER_Supply | TRUE | 1
PV_Paired_LowCF_4hr_New_Battery | PV_Paired_LowCF_4hr_New_Supply | TRUE | 1
PV_Paired_LowCF_6hr_New_Battery | PV_Paired_LowCF_6hr_New_Supply | TRUE | 1

## resource_variable_renewable
Resource Variable Renewable |  | Index
resource | curtailable
Solar_CBRE | FALSE
Solar_Planned | FALSE
Solar_Grid-Scale_Single-Tracking_New | TRUE
Wind_NPM | FALSE
Wind_Onshore_Planned | FALSE
Wind_Offshore_Planned | TRUE
Wind_Onshore_New | TRUE
Wind_Offshore_New | TRUE
Solar_Waianae | TRUE
Hoohana_Solar_Supply | TRUE
West_Oahu_Solar_Supply | TRUE
Mililani_Solar_1_Supply | TRUE
Waiawa_Solar_Supply | TRUE
PV_Paired_Grid_4hr_New_Supply | TRUE
PV_Paired_Grid_6hr_New_Supply | TRUE
PV_Kupehau_Supply | TRUE
PV_Waiawa_Ph2_Supply | TRUE
PV_Mountain_View_Supply | TRUE
PV_Kupono_Supply | TRUE
PV_Barbers_Point_Supply | TRUE
PV_Mahi_Supply | TRUE
PV_Aggregated_DER_Supply | TRUE
PV_Paired_LowCF_4hr_New_Supply | TRUE
PV_Paired_LowCF_6hr_New_Supply | TRUE

## resources
Resources | [6 empty] | Index
resource | technology | zone | rps_eligible | can_build_new | capacity_limited | can_retire
FFR | FFR | Oahu | 0 | 0 | 0 | 0
Airport_DSG | Airport_DSG | Oahu | 1 | 0 | 0 | 0
Biomass | Biomass | Oahu | 1 | 1 | 1 | 0
CIP_BioD | CIP_BioD | Oahu | 1 | 0 | 0 | 0
Hpoff | Hpoff | Oahu | 1 | 0 | 0 | 0
Kala1_Biod | Kala1_Biod | Oahu | 1 | 0 | 0 | 0
Kala2_Biod | Kala2_Biod | Oahu | 1 | 0 | 0 | 0
Schofield | Schofield | Oahu | 1 | 0 | 0 | 0
Schofield_Biod | Schofield_Biod | Oahu | 1 | 0 | 0 | 0
AES | AES | Oahu | 0 | 0 | 0 | 0
CIP_Diesel | CIP_Diesel | Oahu | 0 | 0 | 0 | 0
ICE_New | ICE_New | Oahu | 0 | 1 | 1 | 0
Kahe_5-6 | Kahe_5-6 | Oahu | 0 | 0 | 0 | 1
Kala1 | Kala1 | Oahu | 0 | 0 | 0 | 0
Kala2 | Kala2 | Oahu | 0 | 0 | 0 | 0
LM6000_2x1CC_Sync_Cond | LM6000_2x1CC_Sync_Cond | Oahu | 0 | 1 | 1 | 0
Sync_Cond | Sync_Cond | Oahu | 0 | 1 | 1 | 0
Waiau_3-4 | Waiau_3-4 | Oahu | 0 | 0 | 0 | 1
Waiau_5-6 | Waiau_5-6 | Oahu | 0 | 0 | 0 | 1
Waiau_9-10 | Waiau_9-10 | Oahu | 0 | 0 | 0 | 0
SC_6000CC_New | SC_6000CC | Oahu | 0 | 1 | 1 | 0
K14_W78 | K14_W78 | Oahu | 0 | 0 | 0 | 1
Solar_CBRE | Solar_CBRE | No_LF_Zone | 1 | 0 | 0 | 0
Solar_Planned | Solar_Existing | No_LF_Zone | 1 | 0 | 0 | 0
Solar_Grid-Scale_Single-Tracking_New | Solar_Grid-Scale_Single-Tracking | Oahu | 1 | 1 | 1 | 0
Wind_NPM | Wind_Onshore | Oahu | 1 | 0 | 0 | 0
Wind_Onshore_Planned | Wind_Existing | Oahu | 1 | 0 | 0 | 0
Wind_Offshore_Planned | Wind_Existing | Oahu | 1 | 0 | 0 | 0
Wind_Onshore_New | Wind_Onshore | Oahu | 1 | 1 | 1 | 0
Wind_Offshore_New | Wind_Offshore | Oahu | 1 | 1 | 1 | 0
Solar_Waianae | Solar_Grid-Scale_Fixed | Oahu | 1 | 0 | 0 | 0
Hoohana_Solar_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
West_Oahu_Solar_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
Mililani_Solar_1_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
Waiawa_Solar_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
PV_Paired_Grid_4hr_New_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 1 | 1 | 0
PV_Paired_Grid_6hr_New_Supply | PV_Paired_Grid_6hr_Supply | Oahu | 1 | 1 | 1 | 0
PV_Kupehau_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
PV_Waiawa_Ph2_Supply | PV_Paired_Grid_8hr_Supply | Waiawa_Ph2 | 1 | 0 | 0 | 0
PV_Mountain_View_Supply | PV_Paired_Grid_4hr_Supply | Mountain_View | 1 | 0 | 0 | 0
PV_Kupono_Supply | PV_Paired_Grid_4hr_Supply | Kupono | 1 | 0 | 0 | 0
PV_Barbers_Point_Supply | PV_Paired_Grid_4hr_Supply | Barbers_Point | 1 | 0 | 0 | 0
PV_Mahi_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 0 | 0 | 0
PV_Aggregated_DER_Supply | PV_Paired_Grid_2hr_Supply | Oahu | 1 | 1 | 1 | 0
PV_Paired_LowCF_4hr_New_Supply | PV_Paired_Grid_4hr_Supply | Oahu | 1 | 1 | 1 | 0
PV_Paired_LowCF_6hr_New_Supply | PV_Paired_Grid_6hr_Supply | Oahu | 1 | 1 | 1 | 0
Battery_Grid-Scale_Planned | Battery_Grid-Scale | Oahu | 0 | 0 | 0 | 0
Battery_Grid-Scale_New | Standalone | Oahu | 0 | 1 | 1 | 0
Kapolei_Energy_Storage | Standalone_4hr | Oahu | 0 | 0 | 0 | 0
Load_Build | Load_Build | Oahu | 0 | 0 | 0 | 0
Kapolei_Energy_Storage_Contingency | Standalone_0.5hr | Oahu | 0 | 0 | 0 | 0
Hoohana_Solar_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
West_Oahu_Solar_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
Mililani_Solar_1_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
Waiawa_Solar_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
PV_Paired_Grid_4hr_New_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 1 | 1 | 0
PV_Paired_Grid_6hr_New_Battery | PV_Paired_Grid_6hr_Battery | Oahu | 0 | 1 | 1 | 0
PV_Kupehau_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
PV_Waiawa_Ph2_Battery | PV_Paired_Grid_8hr_Battery | Waiawa_Ph2 | 0 | 0 | 0 | 0
PV_Mountain_View_Battery | PV_Paired_Grid_4hr_Battery | Mountain_View | 0 | 0 | 0 | 0
PV_Kupono_Battery | PV_Paired_Grid_4hr_Battery | Kupono | 0 | 0 | 0 | 0
PV_Barbers_Point_Battery | PV_Paired_Grid_4hr_Battery | Barbers_Point | 0 | 0 | 0 | 0
PV_Mahi_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 0 | 0 | 0
PV_Aggregated_DER_Battery | PV_Paired_Grid_2hr_Battery | Oahu | 0 | 1 | 1 | 0
PV_Paired_LowCF_4hr_New_Battery | PV_Paired_Grid_4hr_Battery | Oahu | 0 | 1 | 1 | 0
PV_Paired_LowCF_6hr_New_Battery | PV_Paired_Grid_6hr_Battery | Oahu | 0 | 1 | 1 | 0
Load_reduce | Shed_DR | Oahu | 0 | 0 | 0 | 0

## simultaneous_flow_limits
Simulatneous Flow Limits |  |  | Index
simultaneous_flow_group | period | simultaneous_flow_limit_mw
Proxy_constraint | 2025 | 0
Proxy_constraint | 2026 | 0
Proxy_constraint | 2027 | 0
Proxy_constraint | 2028 | 0
Proxy_constraint | 2029 | 0
Proxy_constraint | 2030 | 0
Proxy_constraint | 2031 | 0
Proxy_constraint | 2032 | 0
Proxy_constraint | 2033 | 0
Proxy_constraint | 2034 | 0
Proxy_constraint | 2040 | 0
Proxy_constraint | 2045 | 0
Proxy_constraint | 2050 | 0
Mountain_View_to_OA_constraint | 2025 | 7
Mountain_View_to_OA_constraint | 2026 | 7
Mountain_View_to_OA_constraint | 2027 | 7
Mountain_View_to_OA_constraint | 2028 | 7
Mountain_View_to_OA_constraint | 2029 | 7
Mountain_View_to_OA_constraint | 2030 | 7
Mountain_View_to_OA_constraint | 2031 | 7
Mountain_View_to_OA_constraint | 2032 | 7
Mountain_View_to_OA_constraint | 2033 | 7
Mountain_View_to_OA_constraint | 2034 | 7
Mountain_View_to_OA_constraint | 2040 | 7
Mountain_View_to_OA_constraint | 2045 | 7
Mountain_View_to_OA_constraint | 2050 | 7
Barbers_Point_to_OA_constraint | 2025 | 15
Barbers_Point_to_OA_constraint | 2026 | 15
Barbers_Point_to_OA_constraint | 2027 | 15
Barbers_Point_to_OA_constraint | 2028 | 15
Barbers_Point_to_OA_constraint | 2029 | 15
Barbers_Point_to_OA_constraint | 2030 | 15
Barbers_Point_to_OA_constraint | 2031 | 15
Barbers_Point_to_OA_constraint | 2032 | 15
Barbers_Point_to_OA_constraint | 2033 | 15
Barbers_Point_to_OA_constraint | 2034 | 15
Barbers_Point_to_OA_constraint | 2040 | 15
Barbers_Point_to_OA_constraint | 2045 | 15
Barbers_Point_to_OA_constraint | 2050 | 15
Kaukonahua_to_OA_constraint | 2025 | 6
Kaukonahua_to_OA_constraint | 2026 | 6
Kaukonahua_to_OA_constraint | 2027 | 6
Kaukonahua_to_OA_constraint | 2028 | 6
Kaukonahua_to_OA_constraint | 2029 | 6
Kaukonahua_to_OA_constraint | 2030 | 6
Kaukonahua_to_OA_constraint | 2031 | 6
Kaukonahua_to_OA_constraint | 2032 | 6
Kaukonahua_to_OA_constraint | 2033 | 6
Kaukonahua_to_OA_constraint | 2034 | 6
Kaukonahua_to_OA_constraint | 2040 | 6
Kaukonahua_to_OA_constraint | 2045 | 6
Kaukonahua_to_OA_constraint | 2050 | 6
No_LF_to_OA_constraint | 2025 | 1000
No_LF_to_OA_constraint | 2026 | 1000
No_LF_to_OA_constraint | 2027 | 1000
No_LF_to_OA_constraint | 2028 | 1000
No_LF_to_OA_constraint | 2029 | 1000
No_LF_to_OA_constraint | 2030 | 1000
No_LF_to_OA_constraint | 2031 | 1000
No_LF_to_OA_constraint | 2032 | 1000
No_LF_to_OA_constraint | 2033 | 1000
No_LF_to_OA_constraint | 2034 | 1000
No_LF_to_OA_constraint | 2040 | 1000
No_LF_to_OA_constraint | 2045 | 1000
No_LF_to_OA_constraint | 2050 | 1000
Waiawa_to_OA_constraint | 2025 | 30
Waiawa_to_OA_constraint | 2026 | 30
Waiawa_to_OA_constraint | 2027 | 30
Waiawa_to_OA_constraint | 2028 | 30
Waiawa_to_OA_constraint | 2029 | 30
Waiawa_to_OA_constraint | 2030 | 30
Waiawa_to_OA_constraint | 2031 | 30
Waiawa_to_OA_constraint | 2032 | 30
Waiawa_to_OA_constraint | 2033 | 30
Waiawa_to_OA_constraint | 2034 | 30
Waiawa_to_OA_constraint | 2040 | 30
Waiawa_to_OA_constraint | 2045 | 30
Waiawa_to_OA_constraint | 2050 | 30
Kupono_to_OA_constraint | 2025 | 30
Kupono_to_OA_constraint | 2026 | 30
Kupono_to_OA_constraint | 2027 | 30
Kupono_to_OA_constraint | 2028 | 30
Kupono_to_OA_constraint | 2029 | 30
Kupono_to_OA_constraint | 2030 | 30
Kupono_to_OA_constraint | 2031 | 30
Kupono_to_OA_constraint | 2032 | 30
Kupono_to_OA_constraint | 2033 | 30
Kupono_to_OA_constraint | 2034 | 30
Kupono_to_OA_constraint | 2040 | 30
Kupono_to_OA_constraint | 2045 | 30
Kupono_to_OA_constraint | 2050 | 30

## system_params
System Params | [8 empty] | Index
unserved_energy_penalty | overgen_penalty | upward_reserve_violation_penalty | downward_reserve_violation_penalty | lf_reserve_dispatch_fraction | var_rnw_available_for_reserves | max_var_rnw_reserves | require_overbuild | enforce_ghg_targets | count_storage_losses_as_rps_curtailment | allow_unserved_energy
50000 | 50000 | 10000 | 10000 | 0.5 | 1 | 1 | TRUE | TRUE | TRUE | TRUE

## tech_dispatchable_params
Tech Dispatchable Params | [8 empty] | Index
technology | min_stable_level_fraction | ramp_rate_fraction | min_down_time_hours | min_up_time_hours | unit_size_mw | startup_cost_per_mw | shutdown_cost_per_mw | start_fuel_mmbtu_per_mw
Sync_Cond | 0 | 1 | 1 | 1 | 20 | 0.001 | 0.001 | 0
AES | 0.35 | 0.83333 | 3 | 2 | 180 | 0.001 | 0.001 | 0
Airport_DSG | 0.5 | 12.2359 | 1 | 1 | 8 | 0.001 | 0.001 | 0
Biomass | 0.4 | 7.5 | 1 | 1 | 20 | 0.001 | 0.001 | 9.535
CIP_BioD | 0.31938 | 6.0465 | 1 | 1 | 129 | 0.001 | 0.001 | 0.97674
CIP_Diesel | 0.31938 | 6.0465 | 1 | 1 | 129 | 0.001 | 0.001 | 0.97674
Hpoff | 0.51095 | 1.7518 | 3 | 2 | 68.5 | 0.001 | 0.001 | 0
ICE_New | 0.48649 | 12.2359 | 1 | 1 | 8.14 | 0.001 | 0.001 | 0.15356
Kahe_5-6 | 0.37435 | 1.781 | 1 | 1 | 134.7555 | 297.7535 | 0.001 | 21.2681
Kala1 | 0.72222 | 1.6667 | 3 | 2 | 90 | 0.001 | 0.001 | 0
Kala1_Biod | 0.72222 | 1.6667 | 3 | 2 | 90 | 0.001 | 0.001 | 0
Kala2 | 0.38136 | 1.2712 | 3 | 2 | 118 | 0.001 | 0.001 | 0
Kala2_Biod | 0.38136 | 1.2712 | 3 | 2 | 118 | 0.001 | 0.001 | 0
LM6000_2x1CC_Sync_Cond | 0.19 | 39.2157 | 1 | 1 | 153 | 0.001 | 0.001 | 0
Schofield | 0.48649 | 12.2359 | 1 | 1 | 8.14 | 0.001 | 0.001 | 0.15356
Schofield_Biod | 0.48649 | 12.2359 | 1 | 1 | 8.14 | 0.001 | 0.001 | 0.15356
Waiau_3-4 | 0.50236 | 3.8468 | 3 | 3 | 46.792 | 698.0344 | 0.001 | 7.2021
Waiau_5-6 | 0.43408 | 3.3315 | 3 | 2 | 54.0295 | 604.5295 | 0.001 | 5.1268
Waiau_9-10 | 0.11479 | 4.6693 | 1 | 1 | 51.4 | 593.0611 | 0.001 | 0.67121
SC_6000CC | 0.25 | 54.5455 | 1 | 1 | 55 | 0.001 | 0.001 | 0
K14_W78 | 0.2734 | 3.1173 | 4 | 2 | 84.6161 | 376.1121 | 0.001 | 6.4999

## tech_storage_params
Tech Storage Params |  |  |  |  | Index
storage_technology | charging_efficiency | discharging_efficiency | duration_h | duration_type
Battery_Grid-Scale | 0.94 | 0.94 | 1 | minimum-duration
Load_Build | 1e-06 | 1e-06 | 4 | fixed-duration
Standalone | 0.94 | 0.94 | 1 | minimum-duration
Standalone_0.5hr | 0.94 | 0.94 | 0.5 | fixed-duration
Standalone_4hr | 0.94 | 0.94 | 4 | fixed-duration
PV_Paired_Grid_Battery | 0.94 | 0.94 | 1 | minimum-duration
PV_Paired_Grid_2hr_Battery | 0.94 | 0.94 | 2 | fixed-duration
PV_Paired_Grid_4hr_Battery | 0.94 | 0.94 | 4 | fixed-duration
PV_Paired_Grid_5hr_Battery | 0.94 | 0.94 | 5 | fixed-duration
PV_Paired_Grid_6hr_Battery | 0.94 | 0.94 | 6 | fixed-duration
PV_Paired_Grid_8hr_Battery | 0.94 | 0.94 | 8 | fixed-duration
Solar_CBRE_4Hr_Battery | 0.94 | 0.94 | 4 | fixed-duration

## tech_thermal_params
Tech Thermal Params |  |  |  | Index
technology | fuel | fuel_burn_slope_mmbtu_per_mwh | fuel_burn_intercept_mmbtu_per_hr
Sync_Cond | Free | 0 | 0
AES | Coal | 16.2111 | 200.8912
Airport_DSG | Biodiesel | 10.209 | 0
Biomass | Free | 0 | 0
CIP_BioD | Biodiesel | 9.5566 | 244.2927
CIP_Diesel | Diesel | 9.5566 | 244.2927
Hpoff | Free | 1000 | 0
ICE_New | ULSD_SGS | 7.5385 | 6.6089
Kahe_5-6 | LSFO | 9.9883 | 39.9961
Kala1 | LSFO | 5.8494 | 244.574
Kala1_Biod | Biodiesel | 5.8494 | 244.574
Kala2 | LSFO | 5.9239 | 249.6003
Kala2_Biod | Biodiesel | 5.9239 | 249.6003
LM6000_2x1CC_Sync_Cond | Diesel | 6.6698 | 114.8347
Schofield | Sch_Blend | 7.5626 | 6.3282
Schofield_Biod | Biodiesel | 7.5626 | 6.3282
Waiau_3-4 | LSFO | 11.4821 | 11.3706
Waiau_5-6 | LSFO | 10.749 | 25.3913
Waiau_9-10 | Diesel | 8.7818 | 191.9318
SC_6000CC | Diesel | 7.9151 | 98.3209
K14_W78 | LSFO | 9.529 | 57.2017

## technologies
Technologies | [14 empty] | Index
technology | thermal | dispatchable | must_run | variable | storage | hydro | variable_cost_dollars_per_mwh | firm_capacity | conventional_dr | hydrogen_electrolysis | electric_vehicle | energy_efficiency | flexible_load | synchronous_condenser
Load_Reduction | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Shed_DR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
FFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Battery_Grid-Scale | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load_Build | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Standalone | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Standalone_0.5hr | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Standalone_4hr | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sync_Cond | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1
AES | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Airport_DSG | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Biomass | 1 | 1 | 0 | 0 | 0 | 0 | 62.1949 | 1 | 0 | 0 | 0 | 0 | 0 | 0
CIP_BioD | 1 | 1 | 0 | 0 | 0 | 0 | 37.9155 | 1 | 0 | 0 | 0 | 0 | 0 | 0
CIP_Diesel | 1 | 1 | 0 | 0 | 0 | 0 | 37.9155 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Hpoff | 1 | 1 | 0 | 0 | 0 | 0 | 0.16361 | 1 | 0 | 0 | 0 | 0 | 0 | 0
ICE_New | 1 | 1 | 0 | 0 | 0 | 0 | 29.3422 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Kahe_5-6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.34526 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Kala1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Kala1_Biod | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Kala2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Kala2_Biod | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
LM6000_2x1CC_Sync_Cond | 1 | 1 | 0 | 0 | 0 | 0 | 3.6903 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Schofield | 1 | 1 | 0 | 0 | 0 | 0 | 29.3422 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Schofield_Biod | 1 | 1 | 0 | 0 | 0 | 0 | 29.3422 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Waiau_3-4 | 1 | 1 | 0 | 0 | 0 | 0 | 0.34526 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Waiau_5-6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.34526 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Waiau_9-10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Solar_CBRE | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_DGPV | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_Existing | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_Grid-Scale_Fixed | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_Grid-Scale_Single-Tracking | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Existing | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Onshore | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SC_6000CC | 1 | 1 | 0 | 0 | 0 | 0 | 9.5121 | 1 | 0 | 0 | 0 | 0 | 0 | 0
K14_W78 | 1 | 1 | 0 | 0 | 0 | 0 | 0.34526 | 1 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_2hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_4hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_5hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_6hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_8hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_CBRE_4Hr_Supply | 0 | 0 | 0 | 1 | 0 | 0 | 143.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_2hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_4hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_5hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_6hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV_Paired_Grid_8hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar_CBRE_4Hr_Battery | 0 | 0 | 0 | 0 | 1 | 0 | 143.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## transmission_lines
Transmission Lines |  |  |  |  | Index
transmission_line | transmission_from | transmission_to | min_flow | max_flow
OA_to_PROXY | Oahu | Proxy | 0 | 0
Mountain_View_to_OA | Mountain_View | Oahu | 0 | 7
Barbers_Point_to_OA | Barbers_Point | Oahu | 0 | 15
Kaukonahua_to_OA | Kaukonahua | Oahu | 0 | 6
No_LF_to_OA | No_LF_Zone | Oahu | 0 | 1000
Waiawa_to_OA | Waiawa_Ph2 | Oahu | 0 | 30
Kupono_to_OA | Kupono | Oahu | 0 | 30

## zones
Zones |  |  |  | Index
zone | include_in_rps_target | include_in_load_following | include_in_ghg_target
Oahu | 1 | 1 | 1
Proxy | 0 | 0 | 0
Mountain_View | 1 | 1 | 1
Barbers_Point | 1 | 1 | 1
Kaukonahua | 1 | 1 | 1
Waiawa_Ph2 | 1 | 1 | 1
Kupono | 1 | 1 | 1
No_LF_Zone | 1 | 0 | 1

## Technologies Calc
Technologies tab calculations |  | X1 | X2 | [5 empty] | Y1 | Y2 |  | m | y-int | Index
|  | Cap1 (Min.) | Cap4 (Max.) | A | B | C | AGC Ramp Rates |  |  |  |  | Fuel Burn Slope | Fuel Burn Intercept
Technology Name |  | (Net MW) | (Net MW) | (MMBTU/hr) | (MMBTU/hr-MW) | (MMBTU/hr-MW^2) | (MW/Min.) |  |  |  |  | MMBtu/MWh | MMBtu/unit
Kahe_1-2 |  | 23.2165 | 82.4685 | 72.0582 | 8.7761 | 0.0070072 | 4 |  | 279.5844 | 843.4629 |  | 9.5166 | 58.6419
Kahe_3 |  | 23.075 | 86.112 | 73.2636 | 8.1711 | 0.016704 | 5 |  | 270.706 | 900.758 |  | 9.995 | 40.0724
Kahe_4 |  | 23.135 | 85.352 | 116.5162 | 6.5015 | 0.026363 | 5 |  | 281.0383 | 863.4819 |  | 9.3615 | 64.4603
Kahe_5-6 |  | 50.446 | 134.7555 | 86.5728 | 8.7194 | 0.0068517 | 4 |  | 543.8671 | 1385.9777 |  | 9.9883 | 39.9961
Waiau_3-4 |  | 23.5065 | 46.792 | 43.3364 | 9.4391 | 0.029062 | 3 |  | 281.2741 | 548.6401 |  | 11.4821 | 11.3706
Waiau_5-6 |  | 23.453 | 54.0295 | 35.6669 | 10.1206 | 0.0081092 | 3 |  | 277.4865 | 606.1519 |  | 10.749 | 25.3913
Waiau_7 |  | 23.111 | 82.893 | 101.1916 | 7.4411 | 0.017445 | 4 |  | 282.4809 | 837.8785 |  | 9.2904 | 67.7708
Waiau_8 |  | 23.085 | 86.255 | 78.0588 | 8.2162 | 0.011737 | 4 |  | 273.9839 | 874.0649 |  | 9.4995 | 54.6888
Waiau_9-10 |  | 5.9 | 51.4 | 198.4874 | 7.5432 | 0.021617 | 4 |  | 243.7446 | 643.3176 |  | 8.7818 | 191.9318
CIP |  | 41.2 | 129 | 271.1301 | 8.6971 | 0.0050496 | 13 |  | 638.0233 | 1477.0898 |  | 9.5566 | 244.2927
CIP_BioD |  | 41.2 | 129 | 271.1301 | 8.6971 | 0.0050496 | 13 |  | 638.0233 | 1477.0898 |  | 9.5566 | 244.2927
Hpon |  | 35 | 35 | 0 | 1000 | 0 | 2 |  | 35000 | 35000 |  | 0 | 35000
Hpoff |  | 35 | 68.5 | 0 | 1000 | 0 | 2 |  | 35000 | 68500 |  | 1000 | 0
AES |  | 63 | 180 | 258.7479 | 14.9713 | 0.005102 | 2.5 |  | 1222.1896 | 3118.8867 |  | 16.2111 | 200.8912
Kala1 |  | 65 | 90 | 299.0258 | 4.4067 | 0.009308 | 2.5 |  | 624.7876 | 771.0236 |  | 5.8494 | 244.574
Kala2 |  | 45 | 118 | 299.0258 | 4.4067 | 0.009308 | 2.5 |  | 516.176 | 948.621 |  | 5.9239 | 249.6003
Airport DSG |  | 4 | 8 | 0 | 10.209 | 0 | 1.3 |  | 40.836 | 81.672 |  | 10.209 | 0
Schofield |  | 3.96 | 8.14 | 8.3574 | 6.8009 | 0.062952 | 1.66 |  | 36.2762 | 67.888 |  | 7.5626 | 6.3282
K14_W78 |  | 23.1245 | 84.6161 | 88.2177 | 7.8212 | 0.015851 | 4.4 |  | 277.555 | 863.5084 |  | 9.529 | 57.2017
Technology Name | Fuel Type | Fuel Burn Slope | Fuel Burn Intercept | Pmin (Fraction of Pmax) | Max Ramp Up (Fraction of Pmax/hr) | Min. Down Time | Min. Up Time hours | Unit Nameplate Capacity | Start Cost | Shutdown Cost | Start Fuel
Kahe_1-2 |  | 9.5166 | 58.6419 | 0.28152 | 2.9102 | 4 | 2 | 82.4685 | 792.1188 |  | 6.6692
Kahe_3 |  | 9.995 | 40.0724 | 0.26796 | 3.4838 | 4 | 2 | 86.112 | 709.9871 |  | 6.387
Kahe_4 |  | 9.3615 | 64.4603 | 0.27105 | 3.5149 | 4 | 2 | 85.352 | 716.3091 |  | 6.4439
Kahe_5-6 |  | 9.9883 | 39.9961 | 0.37435 | 1.781 | 1 | 1 | 134.7555 | 595.507 |  | 21.2681
Waiau_3-4 |  | 11.4821 | 11.3706 | 0.50236 | 3.8468 | 3 | 2.5 | 46.792 | 1396.0687 |  | 7.2021
Waiau_5-6 |  | 10.749 | 25.3913 | 0.43408 | 3.3315 | 3 | 2 | 54.0295 | 1209.0589 |  | 5.1268
Waiau_7 |  | 9.2904 | 67.7708 | 0.27881 | 2.8953 | 4 | 2 | 82.893 | 788.0623 |  | 6.6351
Waiau_8 |  | 9.4995 | 54.6888 | 0.26764 | 2.7824 | 4 | 2 | 86.255 | 757.3456 |  | 6.3764
Waiau_9-10 |  | 8.7818 | 191.9318 | 0.11479 | 4.6693 | 1 | 1 | 51.4 | 1270.9114 |  | 0.67121
K14_W78 |  | 9.529 | 57.2017 | 0.27328 | 3.1237 | 4 | 2 | 84.6161 | 752.2242 |  | 6.4999
CIP_Diesel |  | 9.5566 | 244.2927 | 0.31938 | 6.0465 | 1 | 1 | 129
CIP_BioD |  | 9.5566 | 244.2927 | 0.31938 | 0.93023 | 1 | 1 | 129
Airport DSG |  | 10.209 | 0 | 0.5 | 9.75 | 1 | 1 | 8 | 0 | 0 | 0